1703EXT2 | EXTERIOR FINISHES | 1703 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7575
1704EXT2 | EXTERIOR FINISHES | 1704 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1704SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1704 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1706EXT2 | EXTERIOR FINISHES | 1706 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1699EXT2 | EXTERIOR FINISHES | 1699 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1707EXT2 | EXTERIOR FINISHES | 1707 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1902EXT2 | EXTERIOR FINISHES | 1902 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
9962SFT1 | FIRE ALARM SYSTEM UPGRADE | 9962 | This site is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It has given the maintenance staff continuous problems and replacement parts are becoming more difficult to find. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | LOVELOCK CORRECTIONAL CENTER | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 2000000
1705SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1705 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1700EXT2 | EXTERIOR FINISHES | 1700 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the flashing and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37000
3041EXT1 | EXTERIOR FINISHES | 3041 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures, and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEWAGE GRINDER SHELTER | 9962 | Correct | LCC |  | Lovelock | 0 | 160 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
1701EXT2 | EXTERIOR FINISHES | 1701 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18500
1702EXT2 | EXTERIOR FINISHES | 1702 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the flashing and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6375
1706SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1706 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1698INT1 | INTERIOR FINISHES | 1698 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 05-CANTEEN/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 24700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 123500
1695INT2 | INTERIOR FINISHES | 1695 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 153500
1696INT1 | INTERIOR FINISHES | 1696 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 160000
1697INT1 | INTERIOR FINISHES | 1697 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
1695ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1695 | The visiting area has a water fountain which was not operational at the time of the survey and should be scheduled for replacement. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1695ADA3 | ADA RESTROOM / SIGNAGE | 1695 | The restrooms and signage in the visitation area are not fully ADA compliant. This project would provide for proper signage to be installed on the walls adjacent to the restroom and also provide for minor restroom fixture adjustments including relocating the flush valve on the toilet. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2018PLM2 | WATER HEATER REPLACEMENT | 2018 | There are two 100 gallon natural gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2018INT1 | INTERIOR FINISHES | 2018 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
2018PLM1 | WATER SOFTENER SYSTEM INSTALLATION | 2018 | There is no water softening/ treatment systems in the building to serve the mechanical equipment. Water that has not been treated causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softener system including all required connections to plumbing and electrical systems. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1696INT2 | FLOORING REPAIRS | 1696 | The ceramic tile flooring in the Bakery is damaged and is reaching the end of its useful life. There are also numerous places throughout the buildings interior where the tile base is damaged or missing. It is recommended that the flooring and wall base be replaced as needed. This project would provide for removal and disposal of the existing flooring and installation of new 6x6 ceramic tiles and ceramic base in the next 2-3 years. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
2018INT2 | SHOWER FLOOR REPLACEMENT | 2018 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1697PLM1 | TEST VALVE INSTALLATION | 1697 | The water softening system for the laundry room boiler is in Bldg. 5. Testing the water then becomes difficult because the test valve is in the other building. There are strict guidelines for the water supply to the washing machines. This project provides for the installation of a test valve in the Laundry area. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1679INT2 | SHOWER FLOOR REPLACEMENT | 1679 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1691INT2 | SHOWER FLOOR REPLACEMENT | 1691 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1692INT2 | SHOWER FLOOR REPLACEMENT | 1692 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1693INT2 | SHOWER FLOOR REPLACEMENT | 1693 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1695ADA1 | TDD INSTALLATION | 1695 | The visitation area is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in the non-contact visitation area. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Immediate to Two Years | Currently Critical | 1 | 20000
1695PLM1 | WATER HEATER REPLACEMENT | 1695 | There is a 30 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1695EXT3 | WINDOW REPLACEMENT | 1695 | There are two windows in this building that are damaged and should be scheduled for replacement. The seals have broken allowing moisture to accumulate between the panes. This project would provide for the replacement of the windows with new dual pane security rated window systems. Removal and disposal of the existing windows is included in this estimate. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1692EXT1 | ROOF REPLACEMENT | 1692 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1695EXT1 | ROOF REPLACEMENT | 1695 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 460500
1694INT1 | CARPET REPLACEMENT | 1694 | Approximately 2,500 square feet of the building is covered by carpet. It is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
1695INT1 | FLOORING REPLACEMENT | 1695 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base, heavy duty sheet vinyl and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 224000
1696EXT1 | ROOF REPLACEMENT | 1696 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480000
1693EXT1 | ROOF REPLACEMENT | 1693 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1691EXT1 | ROOF REPLACEMENT | 1691 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1679EXT1 | ROOF REPLACEMENT | 1679 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1694EXT1 | ROOF REPLACEMENT | 1694 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 405000
1679EXT2 | EXTERIOR FINISHES | 1679 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1698EXT1 | ROOF REPLACEMENT | 1698 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 05-CANTEEN/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 24700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 370500
2018EXT1 | ROOF REPLACEMENT | 2018 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172500
1697EXT1 | ROOF REPLACEMENT | 1697 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/17/2010. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 405000
1679INT1 | INTERIOR FINISHES | 1679 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1693EXT2 | EXTERIOR FINISHES | 1693 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1694EXT2 | EXTERIOR FINISHES | 1694 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
1695EXT2 | EXTERIOR FINISHES | 1695 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 01-ADMINISTRATION & VISITING | 9962 | Correct | LCC |  | Lovelock | 1993 | 30700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 153500
2018EXT2 | EXTERIOR FINISHES | 2018 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing, and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 5 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1692INT1 | INTERIOR FINISHES | 1692 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1693INT1 | INTERIOR FINISHES | 1693 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 4 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1694INT2 | INTERIOR FINISHES | 1694 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 02-INFIRMARY & EDUCATION | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
1692EXT2 | EXTERIOR FINISHES | 1692 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 3 | 9962 | Correct | LCC |  | Lovelock | 1997 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1691EXT2 | EXTERIOR FINISHES | 1691 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1691INT1 | INTERIOR FINISHES | 1691 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 44500 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
1698EXT2 | EXTERIOR FINISHES | 1698 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 05-CANTEEN/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 24700 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 123500
1696EXT2 | EXTERIOR FINISHES | 1696 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 03-GYM/CULINARY/DINING | 9962 | Correct | LCC |  | Lovelock | 1993 | 32000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 160000
1697EXT2 | EXTERIOR FINISHES | 1697 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry walls, painting the window frames and flashing and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 04-LAUNDRY/PRISON INDUSTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 27000 | 2010-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 135000
0575EXT2 | EXTERIOR DOOR REPLACEMENT | 0575 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the three doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0575PLM1 | WATER HEATER REPLACEMENT | 0575 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1223EXT3 | EXTERIOR DOOR REPLACEMENT | 1223 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | FLAMMABLE STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 480 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1278EXT2 | DEMOLISH STRUCTURE | 1278 | The structure is dilapidated and deteriorating and has reached the end of its useful life. It is approaching 50 years of age and has rodent and insect infestations. This project would provide funding for the demolition and disposal of the building. | STORAGE (Old Water Treatment Plant) | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 323 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 3230
0575ADA1 | ADA RESTROOM UPGRADE | 0575 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
3153PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 3153 | The existing automatic chlorine injection system in the building is older and the State Health Department has recommended an upgrade to the system. Poor production from the system causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing system with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | WATER TREATMENT SHED | 9963 | CNR | Parks |  | Valley of Fire | 0 | 32 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0567EXT1 | COMFORT STATION REPLACEMENT | 0567 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | SEVEN SISTERS COMFORT STATION #2 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2866EXT1 | EXTERIOR FINISHES | 2866 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7020
9963PLM3 | WELL REPLACEMENT | 9963 | According to staff, the existing well is currently about 1,100 feet deep and has a 6" diameter casing that has deteriorated and is bent in several places. It is no longer reliable and should be scheduled for replacement. It is recommended to cap and abandon the existing well, drill a new well and install new casing and pumps as needed. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
0575INT1 | INTERIOR FINISHES | 0575 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1270
0575EXT1 | EXTERIOR FINISHES | 0575 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WEST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1979 | 254 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1270
0572EXT1 | COMFORT STATION REPLACEMENT | 0572 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | GROUP USE AREA COMFORT STATION #7 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 20000
0570EXT1 | COMFORT STATION REPLACEMENT | 0570 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | GROUP USE AREA COMFORT STATION #5 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0566EXT1 | COMFORT STATION REPLACEMENT | 0566 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | ATLATL ROCK COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0565PLM1 | WATER HEATER REPLACEMENT | 0565 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0565ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0565 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 2000
0565EXT2 | ROOF REPAIRS | 0565 | The roof flashing around the plumbing vent and the skylights was not installed properly and all three of the skylights are broken. This project would provide funds for repairing the roof. The estimate includes installing proper flashing at all roof penetrations, replacing the skylights and caulking and painting the flashing. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 4500
3154INT1 | INTERIOR FINISHES | 3154 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WHITE DOME COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 240 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0571EXT1 | COMFORT STATION REPLACEMENT | 0571 | This comfort station was built in 1964. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. | GROUP USE AREA COMFORT STATION #6 | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 288 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1222EXT1 | EXTERIOR FINISHES | 1222 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project should be completed on a cyclical basis based on environmental conditions. | EAST MAP RAMADA | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 900 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 4500
0526INT1 | INTERIOR FINISHES | 0526 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #4 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0526EXT2 | EXTERIOR FINISHES | 0526 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #4 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0555SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0555 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 3000
0555PLM1 | WATER HEATER REPLACEMENT | 0555 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0555INT1 | INTERIOR FINISHES | 0555 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next 3-4 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting and / or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0555EXT1 | EXTERIOR FINISHES | 0555 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0555HVA3 | HEAT PUMP REPLACEMENT | 0555 | The two heat pumps serving the building are older and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful lives. This project would provide for installation of two new heat pumps and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0555HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0555 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9963SIT6 | ASPHALT PAVING REPLACEMENT (MAINTENANCE YARD) | 9963 | The asphalt paving in the maintenance yard area is failing, with significant alligatoring, settling and cracks observed. This project covers the removal and replacement of the existing asphalt in the maintenance yard up to the access road that NDOT maintains. Striping for safety, parking and loading zones is included in this estimate. 24,000 square feet was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
0556EXT1 | EXTERIOR FINISHES | 0556 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the wood trim and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF STORAGE #1 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 648 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 648
0557EXT1 | EXTERIOR FINISHES | 0557 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the wood trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF STORAGE #2 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 420 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
0558PLM1 | WATER HEATER REPLACEMENT | 0558 | There is an 80 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3153EXT1 | EXTERIOR FINISHES | 3153 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WATER TREATMENT SHED | 9963 | CNR | Parks |  | Valley of Fire | 0 | 32 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100
0558EXT2 | EXTERIOR FINISHES | 0558 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33620
0519INT1 | INTERIOR FINISHES | 0519 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #3 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1223INT1 | INTERIOR FINISHES | 1223 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | FLAMMABLE STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 480 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1223EXT1 | EXTERIOR FINISHES | 1223 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | FLAMMABLE STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 480 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
1278INT1 | INTERIOR FINISHES | 1278 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | STORAGE (Old Water Treatment Plant) | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 323 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1615
1278EXT1 | EXTERIOR FINISHES | 1278 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | STORAGE (Old Water Treatment Plant) | 9963 | CNR | Parks |  | Valley of Fire | 1964 | 323 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1615
2224INT1 | INTERIOR FINISHES | 2224 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WEST FEE BOOTH | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2224EXT1 | EXTERIOR FINISHES | 2224 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WEST FEE BOOTH | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2718INT1 | INTERIOR FINISHES | 2718 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WELL/PUMP HOUSE | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2718EXT1 | EXTERIOR FINISHES | 2718 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | WELL/PUMP HOUSE | 9963 | CNR | Parks |  | Valley of Fire | 1998 | 100 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2719EXT1 | EXTERIOR FINISHES | 2719 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | RESIDENCE 3 STORAGE | 9963 | CNR | Parks |  | Valley of Fire | 1995 | 220 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1100
2720EXT1 | EXTERIOR FINISHES | 2720 | It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide funding to protect the exterior of the structures excluding the roof. Included in the cost is sealing and re-pointing the stone to maintain its natural look. It is recommended that the structures be sealed and re-pointed as needed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | CABINS | 9963 | CNR | Parks |  | Valley of Fire | 1935 | 588 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
9963EXT5 | EXTERIOR FINISHES, RAMADAS | 9963 | There are 80 steel shade ramadas and 4 steel carports in different locations throughout the site which add up to a total of 28,890 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 57780
2875ADA1 | ADA PARKING SIGNS | 2875 | The existing ADA signage for the 9 accessible parking spaces do not reflect the most currect maximum fine amount. This project would provide for a new sticker reflecting the most currnet maximum fine information to be installed. | CAMPGROUND EXPANSION RAMADA #5 | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 150 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 1512
0558EXT3 | WINDOW REPLACEMENT | 0558 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 48 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
2898EXT1 | EXTERIOR/ INTERIOR FINISHES | 2898 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CABINS SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2866INT1 | INTERIOR FINISHES | 2866 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #2 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 7020
2867INT1 | INTERIOR FINISHES | 2867 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #5 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7020
2865SFT1 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 2865 | The stair handrails on the exterior steps are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and they do not appear to be structurally capable of resisting loads of 50 plf as prescribed in the building code. The code also requires a guardrail anywhere there is an elevation change that exceeds 30 inches. This project recommends the installation of handrails at the stairs and guardrails around the perimeter of the patio in accordance with IBC Section 1012. | RESIDENCE #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2868EXT1 | EXTERIOR FINISHES | 2868 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE STORAGE SHED #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 100 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 500
2869EXT1 | EXTERIOR FINISHES | 2869 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE STORAGE SHED #2 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 100 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 500
2870EXT1 | EXTERIOR FINISHES | 2870 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND EXPANSION COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 525 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2625
2870INT1 | INTERIOR FINISHES | 2870 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPGROUND EXPANSION COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 525 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2625
2870PLM1 | WATER HEATER REPLACEMENT | 2870 | There is an 80 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CAMPGROUND EXPANSION COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 525 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2000
2893EXT1 | EXTERIOR/ INTERIOR FINISHES | 2893 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MOUSE'S TANK SST COMFORT STATION #2 | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
0555EXT2 | EXTERIOR DOOR REPLACEMENT | 0555 | The 4 exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2894ELE1 | EXTERIOR/ INTERIOR FINISHES | 2894 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MOUSE'S TANK SST COMFORT STATION #1 | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2895EXT1 | EXTERIOR/ INTERIOR FINISHES | 2895 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RAINBOW VISTA SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 78 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 390
0526PLM1 | WATER HEATER REPLACEMENT | 0526 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #4 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2897EXT1 | EXTERIOR/ INTERIOR FINISHES | 2897 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOOP B UPPER SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
0519EXT2 | EXTERIOR FINISHES | 0519 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #3 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2899EXT1 | EXTERIOR/ INTERIOR FINISHES | 2899 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EAST ENTRANCE SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
3151EXT1 | EXTERIOR FINISHES | 3151 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VOF ADMINISTRATION BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 2009 | 1184 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 5920
3151INT1 | INTERIOR FINISHES | 3151 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VOF ADMINISTRATION BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 2009 | 1184 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 5920
3152EXT1 | EXTERIOR FINISHES | 3152 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITORS CENTER COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2009 | 450 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 2250
3154EXT1 | EXTERIOR FINISHES | 3154 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WHITE DOME COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 240 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2865EXT1 | EXTERIOR FINISHES | 2865 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7020
3154ADA1 | ADA RESTROOM REMODEL | 3154 | The comfort station does not have an ADA accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | WHITE DOME COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1974 | 240 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 7000
9963PLM4 | WATER TANK REPLACEMENT | 9963 | There are a total of 6 water storage tanks at the site. Four of them are older underground steel tanks including 2 - 5,000 gallon tanks near the maintenance yard and 2 - 1,600 gallon above ground tanks at the Group Use Area. The average life span of a water storage tank is forty to fifty years. These tank were installed in 1964. With the passage of time the tanks have deteriorated and should be scheduled for replacement in the next 3-4 years. This project would provide for new water storage tanks to be installed including connections to existing utilities. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
9963ADA2 | ARCH ROCK CAMPGROUND ADA UPGRADES | 9963 | The designated ADA accessible campsite at the Arch Rock campground does not meet current accessibility guidelines. Required features of an accessible campsite may include a 20'-0" wide drive aisle for RV/ tent trailer sites and accessible amenities on an accessible route to existing restroom including the grill, picnic table, fire ring and water & electric utilities. This project provides for upgrading one existing campsite at Arch Rock to accessible campsites. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 10000
9963ADA3 | ADA ACCESSIBLE PARKING | 9963 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel at 6 Comfort Stations across the site are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk at the Atlatl, West Entrance, Mouse's Tank #1 & #2, Rainbow Vista and East Entrance Comfort Stations. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
9963SIT7 | FUEL TANK REPLACEMENT | 9963 | The above ground fuel storage tank and distribution system was installed in 1996. Staff noted that it has had leaks, the pumps have been repaired several times and the totalizer is inaccurate. The tank and delivery system has reached the end of its useful life and should be scheduled for replacement. This project recommends replacing the 2,000 gallon capacity storage tank and the associated pumping system. The estimate includes removal and disposal of the existing equipment. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
0519PLM1 | WATER HEATER REPLACEMENT | 0519 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF RESIDENCE #3 | 9963 | CNR | Parks |  | Valley of Fire | 1992 | 1400 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2865INT1 | INTERIOR FINISHES | 2865 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #1 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 7020
2896EXT1 | EXTERIOR/ INTERIOR FINISHES | 2896 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOOP B LOWER SST COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 2007 | 180 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 900
2867EXT1 | EXTERIOR FINISHES | 2867 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #5 | 9963 | CNR | Parks |  | Valley of Fire | 2008 | 1404 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 7020
0555ENR1 | LIGHTING UPGRADE | 0555 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, storage closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/20/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
9963PLM1 | REPLACE UNDERGROUND WATER PIPE, ROAD | 9963 | The Valley of Fire State Park is served by wells for domestic water use. The piping that serves the "loop road" is of an older thin walled blue plastic. The pipe requires frequent service and repair due to the age and condition of the system. This project recommends replacing the existing water main with a new, Schedule 80 plastic pipe system. The park is operational year round, so it will be necessary to trench, lay the pipe, backfill and make connections concurrent with ongoing park activities. Two (2) miles of piping was used for this estimate including trenching and backfill. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 316800
9963PLM2 | REPLACE UNDERGROUND WATER PIPE, VISITORS CENTER | 9963 | The Valley of Fire State Park is served by wells for domestic water use. A portion of the piping between the main well house and the Visitors Center at the north end of the park is of an older 4" ductile iron. The pipe requires frequent service and repair due to the age and condition of the system. This project recommends replacing the existing main with a new, Schedule 80 plastic pipe system. The park is operational year round, so it will be necessary to trench, lay the pipe, backfill and make connections concurrent with ongoing park activities. 1-1/2 miles of pipe was used for this estimate including trenching and backfill. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 237600
9963EXT4 | ATLATL ROCK SITE UPGRADES | 9963 | There is an exterior stair system that provides access to the Atlatl Rock petroglyphs site. The paint on the stairs and guardrails is peeling, and some metal is exposed to the elements. The Lexan panel at the top of the stairs has become cloudy and has many scratches due to wind and sand as well as vandalism. This project provides for cleaning and prep of the stringers, guardrails and other structural elements, and the application of an epoxy-based paint and replacing the Lexan panel with a more durable product. This work should be performed off season, to minimize interruption of access to the site. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9963ENV4 | COMPOSTING TOILET MODIFICATIONS | 9963 | The Valley of Fire State Park has two Clivus composting comfort stations. These are 'dry' restroom facilities with a holding tank located under the building. This system, working via microbial action, breaks down the wastes. This type of system does not work well at its remote location. They are very labor intensive. Due to their intermittent use and desert location, the composting mass has been drying out, which interrupts the decomposition process and makes the materials difficult to remove. To remedy this, staff has to manually haul water and sawdust to the comfort station and then mix it with the waste. This project recommends the installation of a moistening system, available from the manufacturer, which introduces a few gallons of water into the tank to keep the composting process operational year round. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 04/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/16/2012. | VALLEY OF FIRE STATE PARK | 9963 | CNR | Parks |  | Valley of Fire | 1935 |  | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0554INT3 | FRP REPLACEMENT | 0554 | The fiberglass reinforced panels (FRP) in the showers are aged and reaching the end of their useful life. It is recommended to schedule the FRP for replacement. This project would provide for removal and disposal of the FRP and installation of new FRP. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0554ADA1 | ADA RESTROOM UPGRADE | 0554 | The building does not have a fully compliant accessible restroom or shower stall. The existing restrooms do not fully meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms to provide ADA compliant restrooms and showers. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 30000
0554INT2 | INTERIOR FINISHES | 0554 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
0554ADA3 | ADA SIGNAGE | 0554 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 1500
0554ENR1 | LIGHTING UPGRADE | 0554 | The existing interior and exterior lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts and compact florescent lights (CFL's) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3024
0554PLM1 | WATER HEATER REPLACEMENT | 0554 | There is a 50 gallon electric water heater in the building that was installed in 2007. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 1500
0555INT2 | RESTROOM REMODEL | 0555 | The restroom in the building is in need of a remodel. It is showing signs of wear and tear and should be remodeled. This project would provide for a complete remodel of the restroom including fixtures, hardware, flooring, exhaust fan and wall finishes. | VOF MAINTENANCE SHOP | 9963 | CNR | Parks |  | Valley of Fire | 1972 | 6000 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0554ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0554 | This restroom contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Immediate to Two Years | Currently Critical | 1 | 2000
0554EXT2 | EXTERIOR FINISHES | 0554 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal eaves and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND A SHOWER BUILDING | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 864 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
0558INT2 | INTERIOR FINISHES | 0558 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VALLEY OF FIRE VISITORS CENTER | 9963 | CNR | Parks |  | Valley of Fire | 1968 | 6724 | 2018-05-23 | Four to Ten Years | Long-Term Needs | 3 | 33620
0565EXT1 | EXTERIOR FINISHES | 0565 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3915
0565INT1 | INTERIOR FINISHES | 0565 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SMALL CAMPGROUND A COMFORT STATION | 9963 | CNR | Parks |  | Valley of Fire | 1975 | 783 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3915
0556EXT2 | ROOF REPLACEMENT | 0556 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | VOF STORAGE #1 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 648 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7776
0557EXT2 | ROOF REPLACEMENT | 0557 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new rolled asphalt roof and new underlayments. This estimate includes removal and disposal of the old roofing. | VOF STORAGE #2 | 9963 | CNR | Parks |  | Valley of Fire | 1966 | 420 | 2018-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5040
3032EXT1 | EXTERIOR FINISHES | 3032 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MUSEUM CARPORT | 9964 | CultAffr | M&H | Museums | Overton | 0 | 1000 | 2014-01-20 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0974INT1 | INTERIOR FINISHES | 0974 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY STORAGE BUILDING | 9964 | CultAffr | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
9964SIT1 | SLURRY SEAL ASPHALT PAVING | 9964 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 41,156 square feet of asphalt area was used to generate this estimate. This project was completed in 2014 but should scheduled every 5 or so years as stated above. This project or a portion thereof was previously recommended in the FCA report dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM SITE | 9964 | CultAffr | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 30867
0267INT1 | INTERIOR FINISHES | 0267 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs are included due to the historic nature of the building and for treating complicated areas such as the wood framing members on the ceiling. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 168255
0267INT2 | FLOORING REPLACEMENT | 0267 | The flooring in the museum includes (VCT) vinyl composite tile, carpet, painted concrete, and local sandstone. The floor finishes are damaged and reaching the end of their useful life. This project would provide for removal and disposal of the existing VCT and Carpet flooring and installation of new 12x12 VCT with a 6" base, heavy duty commercial grade carpet and refinishing the painted concrete in the next two to three years. Most of this work is in the old residence and museum display area of the building. The sandstone should remain as is. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136000
0973EXT1 | EXTERIOR FINISHES | 0973 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM WORKSHOP | 9964 | CultAffr | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 2900
0267PLM1 | SINK REPAIRS - WORKROOM | 0267 | The sink in the workroom does not drain properly and has been taken out of service. It is believed that the drain line was capped during the last addition on the east side of the building and was not re-attached after construction. This project would provide for a licensed plumber to repair the drain line by saw-cutting the concrete floor to determine the failure and installing a new drain line to bring the sink back into service. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0267ADA2 | ASSISTED LISTENING SYSTEM INSTALLATION | 0267 | The Lost City Museum is designed to be a self-guided experience. Many of the exhibits and displays would benefit from a further explanation or clarification, but staffing and budget limitations impact those efforts. This project recommends the installation of a public address type system with a listening system that would activate when the visitor approaches the display or activates a switch. This would greatly enhance the experience and provide compliance with ADA requirements for assistive listening devices for the hearing and visually impaired. Prices quoted are for an infrared system. A radio frequency system may prove more appropriate for this application, and both should be evaluated. This project does include costs for developing the material and recording media for the exhibits. These efforts could serve as a test program for similar programs at other museums and sites of interest state-wide. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 48000
9964SEC1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9964 | The site has minimal site lighting in the parking lots and between the buildings which is a security and safety concern. This project would provide for the installation of 16 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM SITE | 9964 | CultAffr | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104000
0267INT3 | OFFICE RESTROOM REMODEL | 0267 | A portion of the original adobe building is used as offices for the staff. There are two restrooms in this area, both are in poor condition and due for a remodel. There have been ongoing problems with the plumbing, and one of the showers is inoperative. This project recommends replacing the finishes, fixtures, cabinets, toilets, tubs/ showers and exhaust fans in both restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9964ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 9964 | The Picnic Area contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM SITE | 9964 | CultAffr | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 4000
0974EXT1 | EXTERIOR FINISHES | 0974 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY STORAGE BUILDING | 9964 | CultAffr | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 2900
0267ADA1 | ADA SIGNAGE | 0267 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that the restroom signs are moved off of the doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 03/21/2002 and 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 5000
0267ENR3 | WINDOW REPLACEMENT | 0267 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replication of 17 units including wooden frames to maintain the historic character of the building. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25500
0856ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 0856 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete route of travel to the Outdoor Exhibit is necessary to comply with ADA accessibility requirements. This project would provide for installing a concrete walkway to the exhibit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 350 square feet of 4" thick concrete was used for this estimate. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY OUTDOOR EXHIBIT | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 740 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 8750
0973INT1 | INTERIOR FINISHES | 0973 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM WORKSHOP | 9964 | CultAffr | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
0974INT2 | CEILING INSTALLATION | 0974 | The ceiling in the building was intended to be finished with gypsum board. The gypsum board was purchased but never installed and the interior space has remained as an open framed ceiling. At the time of the survey, the roof insulation was falling down through the rafters and in other places the rafters were being used for storing materials. This project would provide for the purchase and installation of gypsum board on the ceiling and insulation attachments to secure the insulation to the roof decking. | LOST CITY STORAGE BUILDING | 9964 | CultAffr | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
9964SIT3 | RETAINING WALL INSTALLATION | 9964 | On the south side of the site along the main entrance driveway, the dirt bank is eroding considerably. The runoff from the parking lot is exacerbating the problem. This project recommends installing a retaining wall along the driveway in order to prevent further erosion. The estimate is based on a 100 foot long reinforced concrete retaining wall. | LOST CITY MUSEUM SITE | 9964 | CultAffr | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0974EXT3 | EXTERIOR SIDING REPLACEMENT | 0974 | The building has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY STORAGE BUILDING | 9964 | CultAffr | M&H | Museums | Overton | 1991 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
0973SFT1 | FIRE PROTECTION EQUIPMENT INSTALLATION | 0973 | The building does not have smoke detectors or a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in Group F occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them and for the purchase and installation of smoke detectors in accordance with these codes. | LOST CITY MUSEUM WORKSHOP | 9964 | CultAffr | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 1500
0973ENR2 | HVAC REPLACEMENT | 0973 | The existing HVAC system consists of a wall mounted heat pump and a small wall mounted air conditioner. These units were not operating at the time of the survey. This project would provide for replacing the existing equipment with an exterior ground mounted packaged unit. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LOST CITY MUSEUM WORKSHOP | 9964 | CultAffr | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0267ELE3 | EXHIBIT LIGHTING UPGRADE | 0267 | The existing lighting fixtures in the artifact cabinets are older and costly to maintain. Replacement bulbs are as much as $75.00 each and the Museum's budget cannot support this costly system. This project will upgrade fixtures to a fiber optic system with lower cost replacement bulbs. Any electrical wiring upgrades are not included in this estimate. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9964SIT4 | SIGNAGE REPLACEMENT | 9964 | The Museum has three large signs indentifying the site and providing basic parking directions. The signs are older, difficult to read and in poor locations for visibility. It is recommended to commission and install new signs for the site. This project provides for the replacement of three identification and directional signs for the site. | LOST CITY MUSEUM SITE | 9964 | CultAffr | M&H | Museums | Overton | 1935 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0267EXT6 | EXTERIOR DOOR REPAIRS | 0267 | Two of the exterior metal man doors are difficult to operate and due for repairs. The door hardware including the panic bars, hinges and closers are worn from general wear and tear and do not operate smoothly. This project would provide for the purchase and installation of new emergency panic hardware, hinges and closers to be installed on the doors and removing the existing hardware. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0973EXT5 | WINDOW REPLACEMENT | 0973 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. | LOST CITY MUSEUM WORKSHOP | 9964 | CultAffr | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0267SFT3 | FIRE SUPPRESSION SYSTEM SUPPRESSION | 0267 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire suppression system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 314076
0267PLM2 | WATER HEATER REPLACEMENT | 0267 | There are two electric water heaters in the building. A 19 gallon water heater for the public restrooms and a 40 gallon water heater for the staff restrooms. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0973EXT4 | EXTERIOR DOOR REPLACEMENT | 0973 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | LOST CITY MUSEUM WORKSHOP | 9964 | CultAffr | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0856EXT3 | EXTERIOR FINISHES | 0856 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the structures. Included in the cost is basic adobe maintenance by the staff as well as funds for adobe specialists to come out once a year. These costs should be sufficient to allow the specialists to spend five days per year at the museum over the next four years. This project should be scheduled on a cyclical basis to maintain the integrity of the outdoor exhibit. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY OUTDOOR EXHIBIT | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 740 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0857EXT3 | EXTERIOR FINISHES | 0857 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is repairing the cracks and applying a new layer of adobe coating over the masonry. It is recommended that the building be repaired in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY PUMP HOUSE | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 64 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
0858EXT2 | EXTERIOR FINISHES | 0858 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for repairing the adobe coating, sealing and staining the wood beams and refurbishing the ocatillo roofing. It is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY MUSEUM RAMADA | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 130 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 650
0973EXT3 | EXTERIOR SIDING REPLACEMENT | 0973 | The shop has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion thereof was previously recommended in the FCA report dated 11/04/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | LOST CITY MUSEUM WORKSHOP | 9964 | CultAffr | M&H | Museums | Overton | 1989 | 580 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 5800
0268EXT2 | EXTERIOR FINISHES | 0268 | This unique structure consists of wood poles and beams covered with reeds and finally packed with soil. It is largely underground and accessed from a hole in the ground with a ladder going down into the Pit House. This type of structure deteriorates over time and requires refurbishment every couple of years. This project provides for removing the soil and reeds, replacing any poles or beams as needed and rebuilding the roof structure. It is recommended that the Pit House be refurbished in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY MUSEUM PIT HOUSE | 9964 | CultAffr | M&H | Museums | Overton |  | 400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0267EXT5 | EXTERIOR FINISHES | 0267 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and painting the stucco, patching the adobe and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes be treated in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the facility, this project is subject to review and approval from the State Historical Preservation Office. | LOST CITY MUSEUM | 9964 | CultAffr | M&H | Museums | Overton | 1935 | 22434 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 112170
0660EXT1 | EXTERIOR FINISHES | 0660 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0660ENR1 | WINDOW REPLACEMENT | 0660 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0660EXT3 | OVERHEAD DOOR REPLACEMENT | 0660 | There are two 10'x14' and one 10'x12' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0660ENR2 | HVAC EQUIPMENT REPLACEMENT | 0660 | The HVAC system was installed in 1988 and is original to the building. It consists of two propane-fired furnaces and four wall mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0640EXT1 | EXTERIOR FINISHES | 0640 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1875
0640EXT2 | EXTERIOR DOOR REPLACEMENT | 0640 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0640EXT3 | WINDOW REPLACEMENT | 0640 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
0915INT1 | INTERIOR FINISHES | 0915 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OIL STORAGE SHED | 9965 | Wildlife |  |  | Overton | 2000 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0915ENR1 | LIGHTING UPGRADE | 0915 | The existing sodium halide pole light on the exterior of the building is broken and is not energy efficient. This project will upgrade the fixture to a more energy efficient high-pressure sodium or LED lamp. These types of lights will provide better illumination and save energy. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OIL STORAGE SHED | 9965 | Wildlife |  |  | Overton | 2000 | 100 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 2500
2221EXT1 | EXTERIOR/ INTERIOR FINISHES | 2221 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. Additional costs are included for patching and repairing the damage caused by a recent impact. It is recommended that the building be repaired, sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CXT ADA COMFORT STATION | 9965 | Wildlife |  |  | Overton | 2001 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0918ADA1 | ADA PARKING SPACE | 0918 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CHECK STATION (FEE BOOTH) | 9965 | Wildlife |  |  | Overton | 2000 | 120 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 2500
0918INT1 | INTERIOR FINISHES | 0918 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CHECK STATION (FEE BOOTH) | 9965 | Wildlife |  |  | Overton | 2000 | 120 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
2213EXT1 | EXTERIOR/ INTERIOR FINISHES | 2213 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CXT COMFORT STATION | 9965 | Wildlife |  |  | Overton | 2001 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2221ADA1 | ADA SIGNAGE & STRIPING | 2221 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | CXT ADA COMFORT STATION | 9965 | Wildlife |  |  | Overton | 2001 | 100 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 1000
3030INT1 | INTERIOR FINISHES | 3030 | The interior finishes are in fair condition. It is recommended to paint the interior walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
3030EXT1 | EXTERIOR FINISHES | 3030 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, staining the wood siding and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
9965SIT4 | DIVERSION DAM REPAIRS | 9965 | There is a diversion dam on the north side of the site that was built in the 1940's and is due for major repairs or replacement. There is no catwalk above the dam to do repairs and maintenance from and several of the mechanical parts are worn and broken. One of the locks is not functioning correctly and is currently held in place with a block of wood. The gates are worn and the concrete is deteriorating. This project would provide for refurbishing the entire dam structure to ensure that the wildlife management area has the hydraulic controls that are necessary. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9965SIT3 | CARPORT STRUCTURE INSTALLATION | 9965 | There is a need for a carport structure in the maintenance area. The trucks and agricultural equipment are exposed to the sun causing preventable damage and maintenance costs. This project would provide a steel carport 24' x 100' to be constructed on the east side of the yard. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0916EXT1 | EXTERIOR FINISHES | 0916 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | GRANARY | 9965 | Wildlife |  |  | Overton | 1940 | 314 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 942
0915EXT1 | EXTERIOR FINISHES | 0915 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the door and metal trim and caulking and sealing the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OIL STORAGE SHED | 9965 | Wildlife |  |  | Overton | 2000 | 100 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
9965EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9965 | There are 7 steel shade ramadas throughout the site which are either 120 s.f., 240 s.f. or 576 s.f. for a total of 1,416 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2832
0660ELE1 | ELECTRICAL UPGRADE | 0660 | This building was constructed before the high demand for electrical services were needed for computers and vehicle repair equipment. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/29/2014. | WMA MAINTENANCE SHOP | 9965 | Wildlife |  |  | Overton | 1988 | 2400 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
3030EXT3 | EXTERIOR DOOR REPLACEMENT | 3030 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3030EXT2 | ROOF REPLACEMENT | 3030 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Several shingles had blown off and many others were partially detached and failing. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | EMPLOYEE STORAGE - FIELD SHOP | 9965 | Wildlife |  |  | Overton | 0 | 1440 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 17280
0918EXT3 | EXTERIOR FINISHES | 0918 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CHECK STATION (FEE BOOTH) | 9965 | Wildlife |  |  | Overton | 2000 | 120 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 600
0641EXT2 | DEMOLISH STRUCTURE | 0641 | The structure is over 70 years of age and is a safety hazard. The structural system has failed and the building should no longer be in use in any way. The main structural posts have detached from their footings, bolts are missing from the structural attachments, and the roof system has failed. This project would provide funding for the demolition and disposal of the building. | EQUIPMENT STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 2600 | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 26000
0640EXT4 | ROOF REPLACEMENT | 0640 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | EMPLOYEE STORAGE | 9965 | Wildlife |  |  | Overton | 1940 | 375 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0639PLM1 | WATER HEATER REPLACEMENT | 0639 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WMA SUPERVISOR'S RESIDENCE | 9965 | Wildlife |  |  | Overton | 1966 | 1600 | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0639INT4 | INTERIOR FINISHES | 0639 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WMA SUPERVISOR'S RESIDENCE | 9965 | Wildlife |  |  | Overton | 1966 | 1600 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 8000
0639EXT4 | EXTERIOR FINISHES | 0639 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | WMA SUPERVISOR'S RESIDENCE | 9965 | Wildlife |  |  | Overton | 1966 | 1600 | 2014-01-29 | Four to Ten Years | Long-Term Needs | 3 | 8000
9965SIT7 | TREE TRIMMING | 9965 | There are many large cottonwood trees on the site that have not been trimmed recently. They have grown to the extent that they are a safety hazard due to dead branches falling or the entire tree falling in areas where visitors frequent. This project would trim, prune or remove the trees to ensure the safety of visitors and maintain the health of the trees. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9965SIT5 | FENCE REPLACEMENT | 9965 | The majority of the fencing around the maintenance yard has failed and is due for replacement. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with two 14' wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9965SIT6 | CXT RESTROOM INSTALLATION | 9965 | The restroom building on the site has been demolished leaving no restroom facilities for the maintenance staff. This project would provide for the purchase and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to the Maintenance Shop. | OVERTON WMA SITE | 9965 | Wildlife |  |  | Overton | 1967 |  | 2014-01-29 | Immediate to Two Years | Currently Critical | 1 | 20000
0638EXT1 | EXTERIOR FINISHES | 0638 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, staining the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
0283EXT3 | OVERHEAD DOOR REPLACEMENT | 0283 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0283PLM2 | PLUMBING REPLACEMENT | 0283 | The plumbing and waste system is older and in poor condition. There is a floor drain in the Work Room that is backed up and is no longer functional. Most of the system is original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines in the building to a point 5 feet outside of the building. This estimate includes removal and disposal of the existing system as required. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
0283ADA2 | ADA UPGRADES | 0283 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are several areas pertaining to building access and restrooms that need to be altered to ensure that the facility is compliant. ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for the purchase and installation of ADA signage, including directional signage from the parking to the accessible building entrances, route of travel inside the building and restrooms. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed on the entry door and ADA restroom door to meet these requirements. This building contains a counter which does not meet current code. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0283SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0283 | The Nursery Office does not have a fire sprinkler system. The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 31500
0283SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0283 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2012 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 18000
0637EXT1 | EXTERIOR FINISHES | 0637 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0637EXT2 | OVERHEAD DOOR REPLACEMENT | 0637 | There is an 8'x8' manually operated overhead coiling door on the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and the replacement with a new manually operated overhead coiling door. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0637HVA1 | HVAC INSTALLATION | 0637 | The building does not have a central cooling or heating system and is uncomfortably warm in the summer and cold in the winter. It is recommended to install an evaporative cooler and propane fired heater in the building to ensure a comfortable work environment. This project would provide for the purchase and installation of new equipment, including all required connections to existing utilities. It is recommended that this project coincide with the Insulate Building project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 10000
0638EXT2 | OVERHEAD DOOR INSTALLATION | 0638 | The building has an exterior opening large enough for vehicles to enter through. Since the seed refrigerator is housed here, vehicles come in and out often and are also stored here. It is recommended to install an overhead door at the opening to protect the vehicles and other equipment inside. This project would provide for the purchase and installation of the door including the door frame and hardware. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2196EXT1 | REBUILD STRUCTURE | 2196 | The structure is over 30 years old and houses brand new equipment including the well pump and expansion tanks. There is no solid floor and the walls and roof are damaged and severely deteriorated. There is evidence of water damage on the interior walls indicating a failed building envelope. As such, the equipment is basically exposed to the elements and will deteriorate prematurely. This project would provide for demolishing the existing structure and rebuilding a new one around the equipment. The new structure will have a poured concrete foundation, wood framing and an asphalt composition roof. Design fees are not included in this estimate. | NURSERY PUMP HOUSE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 48 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 10000
3046EXT2 | EXTERIOR DOOR REPLACEMENT | 3046 | The two exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the doors with new wood doors, storm doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
3046ENR1 | WINDOW REPLACEMENT | 3046 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
3046EXT1 | EXTERIOR FINISHES | 3046 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, painting the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0637SIT1 | CONCRETE APRON INSTALLATION | 0637 | The vehicle garage door does not have a concrete apron in front of it. There are some pavers in place, but these will not last very long with the large vehicles and tractors that drive over them daily. This project would provide for the installation of a 10'x20', 4" thick concrete slab-on-grade apron at the vehicle garage door. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2701EXT1 | ROOF REPLACEMENT | 2701 | The Custom Shade Cloth roof on the Nursery Shade Structure was in poor condition at the time of the survey. It is recommended that the Nursery Shade Structure be re-roofed in the next 4-5 years with a new Custom Shade Cloth. This estimate includes removal and disposal of the old Custom Shade Cloth roofing. | NURSERY SHADE STRUCTURE | 9966 | CNR | Forestry |  | Floyd Lamb | 2006 | 20000 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 30000
3045EXT1 | EXTERIOR FINISHES | 3045 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
3753EXT1 | EXTERIOR FINISHES | 3753 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1960
3753EXT2 | ROOF REPLACEMENT | 3753 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next year with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 2352
3753ELE1 | WIRING CLEANUP | 3753 | The wiring in the residence shed is disorganized and not in proper electrical boxes. This creates a safety issue when conducting repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3046INT2 | INTERIOR FINISHES | 3046 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 16000
3046PLM1 | WATER HEATER REPLACEMENT | 3046 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
3046SFT2 | SMOKE ALARM INSTALLATION | 3046 | International Residential Code (IRC) 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3046INT3 | INTERIOR REMODEL | 3046 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement at the time. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
3046HVA1 | HVAC EQUIPMENT REPLACEMENT | 3046 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA compliant and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3046INT4 | FLOORING REPLACEMENT | 3046 | The plywood subfloor under the furnace and water heater is damaged and reaching the end of its useful life. This project would provide for a licensed contractor to evaluate the floor joists, and determine if they are structurally sound. The costs will cover repair or replacement (if necessary) and the installation of new plywood. Removal and disposal of materials has been included in the estimate. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 10000
0637ENR1 | INSULATE BUILDING | 0637 | The building is not insulated and is not energy efficient. Due to this, the building has extreme temperature fluctuations and is not a comfortable work environment. This project will install (R19) batt insulation in the walls and (R38) batt insulation in the ceiling with an impermeable vinyl surface to help moderate temperature fluctuations. It is recommended that this project coincide with the HVAC Installation project. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 21600
9966SIT1 | SITE BOLLARDS | 9966 | There is an above ground propane tank on the site that does not have bollards in place for protection. Per International Fire Code 2012 Section 312 Vehicle Impact Protection, there needs to be steel posts installed, not less than 4 inches in diameter and filled with concrete around the propane tank. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from the propane tank. This project would provide funding for eight new bollards to be located around the propane tank. | LAS VEGAS STATE TREE NURSERY | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
3753EXT3 | REPAIR/ REPLACE FASCIA AND SOFFITS | 3753 | The fascia and the soffits surrounding the building are weather beaten, peeling, and are showing signs of considerable wear. This project would provide funding to repair and/or replace the fascia and soffits. Repairs include: replacing sections or entirely where needed, sanding, scraping, priming and paint. This project should coincide with the Roof Replacement project. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
0637EXT3 | ROOF REPLACEMENT | 0637 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 21600
0638INT2 | WINDOW REPLACEMENT | 0638 | The windows are original, single pane construction in metal frames. These older windows are drafty and damaged. This project recommends replacing the windows with new dual pane, vinyl framed units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 4500
3753EXT4 | SITE DRAINAGE UPGRADES | 3753 | The grade does not slope away effectively from the building. Water has pooled against the foundation and over time, this can cause damage to the foundation and siding. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales should be installed, as needed. | NURSERY RESIDENCE SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 196 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3046ELE1 | GFCI OUTLETS | 3046 | The existing receptacles in the kitchen, bathroom and on the outside of the structure, are standard duplex receptacles. The 2011 National Electrical Code (NEC) 210.8 requires these locations to have Ground Fault Circuit Interrupters (GFCI) for protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
3045ENR1 | LIGHTING UPGRADE | 3045 | The interior light in the building has an old light fixture and is not energy efficient. This project would provide for the replacement of the interior light fixture and bulb with a new light fixture and LED bulb. An occupancy sensor will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350
3044HVA1 | EVAPORATIVE COOLER REPLACEMENT | 3044 | A wet wall evaporative cooler system is installed on the side of this building. It is severely scaled and the damper and motor are not functioning properly. The system has reached the end of its useful and expected life. This project would provide for a new wet wall evaporative cooler system to be installed, and includes all required connections to utilities. The estimate includes removal and disposal of the old cooler. | NURSERY GREENHOUSE #4 | 9966 | CNR | Forestry |  | Floyd Lamb | 2006 | 2480 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0638EXT3 | ROOF REPLACEMENT | 0638 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes the removal and disposal of the old roofing. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13125
0637EXT4 | SITE DRAINAGE UPGRADES | 0637 | The grade does not slope away effectively from the building. Water has pooled against the foundation and over time, this can cause damage to the foundation and siding. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales should be installed, as needed. It is recommended that the grading be completed within 2-3 years. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0637ELE1 | WIRING CLEANUP | 0637 | The wiring is disorganized and not in proper electrical boxes. This creates a safety issue when making repairs or upgrades and is not up to National Electrical Code (NEC) 2011. This project would provide for cleanup and labeling of the wiring. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0637SFT1 | EXTERIOR LANDING INSTALLATION | 0637 | Section 1008.1 of the 2012 International Building Code (IBC) describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | NURSERY SHOP/ STORAGE #1 | 9966 | CNR | Forestry |  | Floyd Lamb | 1985 | 1440 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 2500
0283SIT1 | SITE DRAINAGE UPGRADES | 0283 | The grade does not slope away effectively from the building. Water has pooled against the foundation and over time, this can cause damage to the foundation and siding. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales should be installed, as needed. It is recommended that the grading be completed within 2-3 years. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0283EXT5 | CONCRETE APRON REPLACEMENT | 0283 | Outside of the Shop Area, the exterior concrete apron has extensive cracking and is due for replacement. This project would provide for the installation of a new 120 square foot 4" thick concrete slab-on-grade apron. Removal and disposal of the existing concrete is included in this estimate. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0283ADA3 | BREAK ROOM REMODEL | 0283 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish to cover the door, frame and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0283EXT7 | GUTTER REPLACEMENT | 0283 | The existing rain gutters and down spouts on the Nursery Office have numerous joints that have multiple leaks. The leaks have been repaired multiple times, but continue to leak. The leaking rain gutters and down spouts will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented rain gutters and down spouts with seamless rain gutters and new down spouts. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
0283EXT4 | TRIM OR REMOVE TREES | 0283 | The building has several trees which are growing up against the structure. The trees move in windy conditions and rub the roof, which can cause premature failure of the roof system and void roof warranties. The root systems are causing shifting and heaving of sidewalks, creating unsafe conditions. There are also several large trees in need of trimming. Lack of maintenance can become a safety issue. This project recommends that these issues be addressed before additional damage is done. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0638ENR1 | LIGHTING UPGRADE | 0638 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project would upgrade the lighting fixtures to the higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and the addition of new tombstones, if needed. Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NURSERY STORAGE #2 | 9966 | CNR | Forestry |  | Floyd Lamb | 1980 | 875 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
3045EXT2 | ROOF REPLACEMENT | 3045 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Four to Ten Years | Long-Term Needs | 3 | 600
0616EXT2 | ROOF REPLACEMENT | 0616 | The Custom Shade Cloth roof on the Nursery Lath House was in poor condition at the time of the survey. It is recommended that the Nursery Lath House be re-roofed in the next 3-4 years with a new Custom Shade Cloth. This estimate includes removal and disposal of the old Custom Shade Cloth roofing. | NURSERY LATH HOUSE | 9966 | CNR | Forestry |  | Floyd Lamb | 2008 | 15000 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0283EXT6 | ROOF REPLACEMENT | 0283 | The corrugated metal roof on this building is in poor condition. It is over 40 years old and signs of leaking were observed at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33750
3046ENV1 | PEST CONTROL | 3046 | There are numerous rodent droppings throughout this building and a dead rabbit is located at the crawl space entrance. Due to the potential risk of disease, this project would provide for the treatment and cleanup of all rodent droppings, removal of the dead rabbit, and sealing the home so no other animals can crawl under the house. This work should be conducted by a licensed pest control business. | NURSERY RESIDENCE (VACANT) | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 1600 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9966ADA4 | ADA SIDEWALK REPLACEMENT | 9966 | The concrete sidewalks around the site are in need of replacement. The sidewalks have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 4,000 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAS VEGAS STATE TREE NURSERY | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 60000
9966ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 9966 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a new concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | LAS VEGAS STATE TREE NURSERY | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 30000
3045PLM1 | FERTILIZER INJECTOR REPLACEMENT | 3045 | The building has fertilizer injectors on the domestic water system. The fertilizer injectors have built-up water calcium deposits, are problematic and intermittently work. This project recommends the removal and disposal of the current fertilizer injectors and the installation of new fertilizer injectors and provides for all necessary connections to the existing utilities. | NURSERY FERTILIZATION SHED | 9966 | CNR | Forestry |  | Floyd Lamb | 1981 | 40 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0283HVA3 | HVAC UPGRADE | 0283 | There is not a central HVAC system in the building. The office areas are cooled by window mounted AC units and have no heat. These units are problematic and require frequent replacement. The lack of heat has resulted in frozen pipes and drainage problems. There is a ceiling mounted heater in the garage that is not operational. This project would provide for the purchase and installation of a packaged HVAC unit, ducting and associated controls for the office areas and a ceiling mounted heater and evaporative cooler for the Shop Area. This project includes removal and disposal of the existing units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
9966PLM1 | BACKFLOW PREVENTION | 9966 | State Health Law (NAC 445A.67185) and the Uniform Plumbing Code (UPC Section 603) require backflow prevention on water service connections. This is to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs also include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | LAS VEGAS STATE TREE NURSERY | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 |  | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 35000
2195EXT1 | PANEL REPLACEMENT | 2195 | The corrugated fiberglass panels covering the building are original to the building and should be scheduled for replacement. Many of the panels are damaged from general wear and tear and have needed maintenance often. This project would provide for removal and disposal of the existing panels and replacement with polycarbonate panels. The estimate is based on 1,200 linear feet of 4'-0" wide panels at $17 per linear foot. This project or a portion thereof was previously recommended in the FCA reports dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY GREENHOUSE #3 | 9966 | CNR | Forestry |  | Floyd Lamb | 1983 | 2480 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20400
0283PLM1 | WATER HEATER REPLACEMENT | 0283 | There is a 40 gallon electric water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was installed in 2004. It is recommended that a new water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0283INT2 | FLOORING REPLACEMENT | 0283 | The Vinyl Composite Tile (VCT) in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" cove base in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0283EXT1 | EXTERIOR FINISHES | 0283 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0283INT3 | INTERIOR FINISHES | 0283 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project does not cover the garage in the rear of the building, it will be addressed in the Shop Area Remodel project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0283INT4 | SHOP AREA REMODEL | 0283 | The Shop Area at the rear of the building has gypsum board covering the walls. This is not an appropriate wall covering for the garage because it does not hold up to the heavy water usage. Buckets, hand tools and plant containers are washed here daily and water makes contact with the walls. The existing gypsum board is severely damaged and in some places has been removed and covered with plywood. This project would remove and dispose of the gypsum board and replace it with a type X gypsum board and FRP. The damaged ceiling gypsum board is also included in this project. It is recommended that the roof leaks be repaired prior to implementing this project. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12150
0283ENR2 | WINDOW REPLACEMENT | 0283 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0283EXT2 | EXTERIOR DOOR REPLACEMENT | 0283 | The three exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the existing doors, frames and hardware with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY OFFICE | 9966 | CNR | Forestry |  | Floyd Lamb | 1975 | 2250 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2195HVA1 | HVAC EQUIPMENT REPLACEMENT | 2195 | The greenhouse is currently cooled via a modified evaporative cooling system and is heated by a propane heater. These units are not energy efficient and have reached the end of their expected and useful life. This project recommends replacing the equipment in the next 2-3 years. The estimate includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 01/30/2002 and 05/12/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/10/2016. | NURSERY GREENHOUSE #3 | 9966 | CNR | Forestry |  | Floyd Lamb | 1983 | 2480 | 2016-05-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
9967SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9967 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 415,000 square feet of asphalt area was used to generate this estimate. | THREE LAKES VALLEY CONSERVATION CAMP | 9967 | Correct | TLVCC |  | Indian Springs |  |  | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 249000
3089INT1 | INTERIOR FINISHES | 3089 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT A2 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
3090EXT1 | EXTERIOR FINISHES | 3090 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE SERVICES B | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 23866 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 119330
3093INT1 | INTERIOR FINISHES | 3093 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF OFFICE/SHOP E | 9967 | Correct | Forestry |  | Indian Springs | 2010 | 14685 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 73425
3092EXT1 | EXTERIOR FINISHES | 3092 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE PROGRAMS D | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 10838 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 54190
3092INT1 | INTERIOR FINISHES | 3092 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INMATE PROGRAMS D | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 10838 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 54190
3091EXT1 | EXTERIOR FINISHES | 3091 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOC/NDF ADMINISTRATION C | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 16386 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81930
3091INT1 | INTERIOR FINISHES | 3091 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDOC/NDF ADMINISTRATION C | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 16386 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81930
3093EXT1 | EXTERIOR FINISHES | 3093 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF OFFICE/SHOP E | 9967 | Correct | Forestry |  | Indian Springs | 2010 | 14685 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 73425
3089EXT1 | EXTERIOR FINISHES | 3089 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT A2 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
3088EXT1 | EXTERIOR FINISHES | 3088 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT A1 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
3088INT1 | INTERIOR FINISHES | 3088 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT A1 | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 26767 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 133835
3090INT1 | INTERIOR FINISHES | 3090 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INMATE SERVICES B | 9967 | Correct | TLVCC |  | Indian Springs | 2010 | 23866 | 2013-05-01 | Four to Ten Years | Long-Term Needs | 3 | 119330
0966EXT1 | EXTERIOR FINISHES | 0966 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Four to Ten Years | Long-Term Needs | 3 | 25000
0966SFT2 | FIRE ALARM SYSTEM UPGRADE | 0966 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907.2.6.3 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0966EXT2 | REPLACE EXTERIOR DOORS | 0966 | The five existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of five new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. The main entrance door hall have ADA accessible hardware including lever action door handles and threshold. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0966PLM2 | REMODEL BARRACKS RESTROOM | 0966 | The restroom in the barracks section of the building is in general disrepair and is due for a complete remodel. This project provides for new sinks, toilets, partitions, plumbing fixtures, cabinets and all interior finishes for the restroom. Minor plumbing and room redesign may be required and is included in this estimate. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Immediate to Two Years | Currently Critical | 1 | 80000
0966SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0966 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0966ENR1 | LIGHTING UPGRADE | 0966 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0966HVA1 | REPLACE EVAPORATIVE COOLERS | 0966 | A number of evaporative coolers have been installed throughout the building. They are in fair condition and it is recommended that these units be replaced in two to four years as they are reaching the end of their expected life. Six (6) units were used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0966INT1 | INTERIOR FINISHES | 0966 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | BARRACKS/ADMINISTRATION | 9968 | Correct | TLVCC |  | Indian Springs | 1990 | 6112 | 2007-04-05 | Four to Ten Years | Long-Term Needs | 3 | 25000
9969ADA1 | ADA PARKING STRIPING AND SIGN | 9969 | The accessible parking area striping is fading, and is becoming difficult to identify. The area also does not have a sign designating the parking space as accessible. CABO/ANSI A117.1 - 1992 Section 4.6.2 states, "...accessible parking spaces shall be identified by a sign showing the international symbol of accessibility..." The area should be re-striped and complying signage installed. | THREE LAKES VALLEY NDF CON. CAMP SITE | 9969 | CNR | Forestry |  | Indian Springs |  |  | 2001-12-01 | Immediate to Two Years | Currently Critical | 1 | 791.2824
0864SFT1 | FIRE ALARM SYSTEM UPGRADE | 0864 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12047.6658
0864SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0864 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11475.8824
0864ADA1 | ADA REMODEL | 0864 | The office is open to the public, and the building does not fully comply with the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with CABO/ANSI A117.1-1992 Sections 4.15 - 4.20 and 1997 UBC Chapter 11. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Immediate to Two Years | Currently Critical | 1 | 10762.2477
0864INT1 | INTERIOR FINISHES | 0864 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Four to Ten Years | Long-Term Needs | 3 | 15256.4185
9969SIT1 | REPAIR AND RESEAL ASPHALT PARKING AREAS | 9969 | The existing paving is in good condition. Climate and constant use will accelerate deterioration. For proper maintenance it is recommended the entire parking area and driveway be resealed and re-striped. This type of maintenance will extend the life of the asphalt. | THREE LAKES VALLEY NDF CON. CAMP SITE | 9969 | CNR | Forestry |  | Indian Springs |  |  | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3089.9999
0864ELE1 | LIGHTING UPGRADE | 0864 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. | NDF OFFICE/SHOPS | 9969 | CNR | Forestry |  | Indian Springs | 1988 | 7050 | 2001-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13690.4624
0156ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0156 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 4000
0159ENR2 | WINDOW REPLACEMENT | 0159 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136800
0158ENR2 | WINDOW REPLACEMENT | 0158 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136800
0158EXT5 | EXTERIOR DOOR REPLACEMENT | 0158 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next 5-6 years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 24000
0157ENR2 | WINDOW REPLACEMENT | 0157 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136800
0156EXT3 | ROOF REPLACEMENT | 0156 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 514944
0155ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0155 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 4000
0156PLM2 | WATER HEATER REPLACEMENT | 0156 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0162ENR2 | WINDOW REPLACEMENT | 0162 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136800
0156ADA1 | ADA RESTROOM UPGRADE | 0156 | There are 10 small restrooms , 2 large restrooms and Locker Rooms for the staff. The Locker Rooms have recently been remodeled and are ADA compliant, but none of the other restrooms meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of each restroom is necessary. This project would provide funding for remodeling the 2 large restrooms into ADA compliant restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 50000
0156EXT4 | DOOR REPLACEMENT | 0156 | The existing exterior and interior metal doors and frames are original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 197 new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. Additional costs have been added to the estimate due to the nature of the facility and the more complex locking mechanisms that are required in this secured building. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 591000
0156ENR2 | WINDOW REPLACEMENT | 0156 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 53 units. Removal and disposal of the existing windows is included in this estimate. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53000
0155INT2 | JANITORS CLOSET REPAIRS | 0155 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0163EXT4 | ROOF REPLACEMENT | 0163 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205524
0155EXT3 | ROOF REPLACEMENT | 0155 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118740
0164EXT3 | ROOF REPLACEMENT | 0164 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 237888
0155EXT2 | INVESTIGATE/ REPAIR WATERPROOFING | 0155 | The grade on the southeast side of the building has built up over time to the extent that it is higher than the grade originally designed. The result is that the waterproofing membrane is below grade and there are reports of water seeping into the interior of the building. This project recommends excavating the excess dirt to the grade originally designed and inspecting and repairing the waterproof membrane. The estimated depth of excavation is about two feet. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 8500
0155SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0155 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 138530
0162EXT4 | ROOF REPLACEMENT | 0162 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205524
0161EXT4 | ROOF REPLACEMENT | 0161 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205524
0158EXT4 | ROOF REPLACEMENT | 0158 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205524
0160ENR2 | WINDOW REPLACEMENT | 0160 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136800
0165EXT3 | ROOF REPLACEMENT | 0165 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 915708
0161ENR2 | WINDOW REPLACEMENT | 0161 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136800
2706INT2 | INTERIOR DRAINAGE REPAIRS | 2706 | The building has a drainage problem inside where the slope of the floor does not carry water towards the floor drain. The water accumulates in several areas inside the building and pools up against the exterior walls. This is causing damage to the CMU walls and concrete foundation from the water leaching into the concrete. This project would provide for either installing additional floor drains or pouring a new concrete floor with proper slopes. | SDCC PUMP HOUSE 2 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2706HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2706 | An evaporative cooler is installed on the roof of this building. It is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | SDCC PUMP HOUSE 2 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2788PLM1 | WATER HEATER REPLACEMENT | 2788 | There are two 125 gallon gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | SDCC DORM HOUSING UNIT #12 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0164INT3 | INTERIOR FINISHES | 0164 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 99120
0163ENR2 | WINDOW REPLACEMENT | 0163 | The existing windows in this building are of single pane wire mesh construction. These older windows are drafty and not energy efficient. Some of the windows and louver mechanisms are broken. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136800
0155ADA3 | BREAK ROOM REMODEL | 0155 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 15000
0157EXT4 | ROOF REPLACEMENT | 0157 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205524
3097INT1 | INTERIOR FINISHES | 3097 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC POWER/GENERATOR BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 4004 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 20020
0155ADA5 | ADA SIGNAGE | 0155 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 900
2707HVA1 | AIR CONDITIONER REPLACEMENT | 2707 | A small air conditioner is installed on the side of this building. It is original to the building and has reached the end of it's useful and expected life. This project would provide for a new air conditioner to be installed including all required connections to utilities. The estimate includes removal and disposal of the old unit. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2787EXT1 | EXTERIOR FINISHES | 2787 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC DORM HOUSING UNIT #11 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
2787INT1 | INTERIOR FINISHES | 2787 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC DORM HOUSING UNIT #11 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
2788EXT1 | EXTERIOR FINISHES | 2788 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC DORM HOUSING UNIT #12 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
0162HVA2 | EXHAUST FAN REPLACEMENT | 0162 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 9000
3160EXT1 | EXTERIOR FINISHES | 3160 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC CARD SORTING BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 2000 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0163SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0163 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 239778
3097EXT1 | EXTERIOR FINISHES | 3097 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC POWER/GENERATOR BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 4004 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 20020
3096INT1 | INTERIOR FINISHES | 3096 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC INFIRMARY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 11724 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 58620
3096EXT1 | EXTERIOR FINISHES | 3096 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC INFIRMARY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 11724 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 58620
3095INT1 | INTERIOR FINISHES | 3095 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC CULINARY/DINING/CHAPEL/LAUNDRY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 44049 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 220245
3095EXT1 | EXTERIOR FINISHES | 3095 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC CULINARY/DINING/CHAPEL/LAUNDRY | 9970 | Correct | SDCC |  | Indian Springs | 2010 | 44049 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 220245
2710HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2710 | A small evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | SDCC P. I. SANDBLASTING SHED 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2788INT1 | INTERIOR FINISHES | 2788 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC DORM HOUSING UNIT #12 | 9970 | Correct | SDCC |  | Indian Springs | 2008 | 23780 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
9970SIT4 | SITE DRAINAGE UPGRADES | 9970 | Recent heavy rains exposed drainage problems around the site. The grade does not slope away from the buildings effectively which allowed water to infiltrate several of the housing units. This project would create positive flow away from the buildings by regrading, paving and/ or installing additional drainage swales as needed. | SOUTHERN DESERT CORRECTIONAL CENTER | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0155ADA2 | ADA RESTROOM UPGRADE | 0155 | The existing Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0155ADA1 | ADA DOOR HARDWARE REPLACEMENT | 0155 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 22500
0155ENR2 | WINDOW REPLACEMENT | 0155 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 35 units. Removal and disposal of the existing windows is included in this estimate. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
9970ENV1 | PIGEON ABATEMENT | 9970 | The site and buildings have been inhabited by pigeons. The birds introduce a potential risk of disease, cause maintenance problems with the mechanical systems and cost labor time for general clean-up. This project provides for removal and disposal of pigeon debris, eggs and carcasses from the site and buildings by a licensed pest control business. | SOUTHERN DESERT CORRECTIONAL CENTER | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
9970ELE1 | MAIN ELECTRICAL SYSTEM REPLACEMENT | 9970 | The electrical system has many components that are more than 30 years old including switchgear and wiring. This worn equipment has resulted in many maintenance issues which have left the facility without power multiple times. Loss of power is a major safety concern for the staff and inmates. This project provides for the replacement of the switchgear, transformers, underground feeder system around the entire site and other components as needed. The cost includes removal and disposal of the existing equipment. | SOUTHERN DESERT CORRECTIONAL CENTER | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500000
0161HVA2 | EXHAUST FAN REPLACEMENT | 0161 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 9000
9970ENR1 | HIGH MAST LIGHTING UPGRADE | 9970 | There are 22 high mast security light poles throughout the facility that have 10 security lamps each. The wiring, poles and light fixtures are more than 30 years old. Maintenance staff reported that the wind causes the wires to collide inside the poles damaging the housing and insulation which has resulted in shorts during high wind or rain. The underground feeder lines and vaults are also deteriorated due to normal wear and aging. Loss of lighting is a major safety concern for the staff and inmates after dark. It is recommended to install LED bulbs for energy and labor savings. This project provides for the replacement of the feeders, heads, lamps, ballasts, lowering mechanisms, circuit components and vaults for the high mast light poles. The cost includes removal and disposal of the existing equipment. | SOUTHERN DESERT CORRECTIONAL CENTER | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 1500000
2706SFT1 | WATER TREATMENT SYSTEM ADDITION | 2706 | The chlorine water treatment system is located inside the building. The system should be in a separate ventilated room for safety. Currently the system creates a safety hazard due to being located in the same room as the electrical panels, lighting and mechanical equipment. This project would provide for building a small addition onto the building to safely store the chlorine water treatment system. | SDCC PUMP HOUSE 2 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 50000
9970ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9970 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. 7 concrete parking spaces, passenger loading areas and a path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for 7 total accessible parking spaces, of which at least 2 shall be van accessible spaces and an accessible concrete walkway from each space to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 3,000 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | SOUTHERN DESERT CORRECTIONAL CENTER | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 75000
0163SEC2 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0163 | Housing Unit 7 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275000
0159EXT4 | ROOF REPLACEMENT | 0159 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205524
0160EXT4 | ROOF REPLACEMENT | 0160 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205524
0171ELE1 | ELECTRICAL UPGRADE | 0171 | The electrical equipment in the tower is original to the building and due for replacement. The electrical panels, transformer, light switches and receptacles are showing signs of extreme wear. It is recommended the entire system be upgraded to ensure reliable operation and the safety of the occupants. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0163HVA2 | EXHAUST FAN REPLACEMENT | 0163 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units should be installed. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 9000
9970ENR2 | ENERGY MANAGEMENT SYSTEM UPGRADE | 9970 | The existing energy management system is older and is not connected to all of the equipment. In a facility of this type, it is imperative that the conditioned spaces and lighting are properly controlled at all times. This project would provide for the removal and disposal of the existing energy management system and replacement with new equipment including all required connections to utilities and equipment. | SOUTHERN DESERT CORRECTIONAL CENTER | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
2553SFT1 | RECOMMISSION BUILDING SYSTEMS | 2553 | The fire suppression system, fire alarm system and electricity have been turned off in the building, however the building is currently used to store boxes of playing cards on pallets. During the survey, inmates were bringing the pallets of cards into and out of the building. This poses a safety risk because since the life safety systems are turned off there should be no occupants in the building at any time. This project would provide for recommissioning the building systems before any activities are resumed inside the building. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC | PI | Indian Springs | 2004 | 20000 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 15000
0173EXT4 | WINDOW REPLACEMENT | 0173 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9970SIT3 | SLURRY SEAL ASPHALT PAVING | 9970 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and paving around the old Culinary and Laundry building. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 265,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SOUTHERN DESERT CORRECTIONAL CENTER | 9970 | Correct | SDCC |  | Indian Springs | 1980 |  | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 198750
0163SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0163 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0170SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0170 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 750
0170HVA1 | HVAC UNIT REPLACEMENTS | 0170 | The existing wall-mounted HVAC units are more than 25 years old, not energy efficient and have reached the end of their expected life. This project would provide for the installation of two new energy efficient wall mounted HVAC units including connections to existing utilities. Removal and disposal of the old units are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0171SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0171 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 750
0166SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0166 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 228536
0172SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0172 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 750
0166PLM1 | WATER HEATER REPLACEMENT | 0166 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0172HVA1 | HVAC UNIT REPLACEMENTS | 0172 | The existing wall-mounted HVAC units are more than 25 years old, not energy efficient and have reached the end of their expected life. This project would provide for the installation of two new energy efficient wall mounted HVAC units including connections to existing utilities. Removal and disposal of the old units are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0173SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0173 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 750
0173HVA1 | HVAC UNIT REPLACEMENTS | 0173 | The existing wall-mounted HVAC units are more than 25 years old, not energy efficient and have reached the end of their expected life. This project would provide for the installation of two new energy efficient wall mounted HVAC units including connections to existing utilities. Removal and disposal of the old units are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0365SFT1 | FIRE SUPPRESSION / ALARM SYSTEM INSTALLATION | 0365 | Pursuant to the 2012 International Building Code Section 903.2.5.1, an automatic sprinkler system shall be installed in Group H occupancies. The building in this report is currently classified as an H occupancy due to the operation and storage of welding equipment and supplies. This project would provide for a fire sprinkler system including backflow prevention to be installed. Installation of a fire alarm system is also included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC WELDING SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 400 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0172EXT4 | WINDOW REPLACEMENT | 0172 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2183HVA1 | HVAC REPLACEMENT | 2183 | An air conditioning unit is installed on the roof of this building. It is original to the building and has reached the end of it's useful and expected life. This project would provide for a new air conditioner to be installed including all required connections to utilities. The estimate includes removal and disposal of the old unit. | SDCC GLASS SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0164ADA1 | ADA RESTROOM UPGRADE | 0164 | The unisex restroom and the inmate restroom have been upgraded for ADA accessibility compliance, but they are not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, and the accessories are not all within reach ranges. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 6500
0171EXT3 | EXTERIOR SIDING REPLACEMENT | 0171 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding including priming and painting. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0166INT2 | FIRE RATED CEILING ASSEMBLY REPAIRS | 0166 | The gypsum board ceiling in the Billiard's Room and the Coffee Shop are damaged in several areas. It appears that this is a one hour fire rated ceiling assembly and needs to repaired immediately. This project would provide for repairs to the ceiling with a fire rated gypsum board assembly. Taping, texture and paint are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 2500
0166SFT4 | ELECTRICAL SYSTEM UPGRADE | 0166 | This building was constructed before the high demand for new types of electrical devices were needed. The existing system has numerous electrical devices daisy chained together using extension cords and surge protectors. This is a safety issue that needs to be addressed. It is recommended that the portion of the system serving the Law Library, Coffee Shop and Offices be upgraded to meet the evolving demands of the building. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 180000
0168EXT2 | OVERHEAD DOOR REPLACEMENT | 0168 | There are two 12'x15' overhead coiling doors and five 12'x10' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0168EXT3 | EXTERIOR DOOR REPLACEMENT | 0168 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of ten new hollow metal doors, frames and hardware. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 10 new exterior doors. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0168PLM1 | RESTROOM WASTELINE REPLACEMENT | 0168 | The sanitary sewer waste line running from the warehouse restroom under the building has collapsed resulting in closure of the restroom. This project provides for removal of the existing piping and installation of a new line. Investigation on the cause of the collapse, saw cutting of the concrete and excavation are included in this estimate. An allowance of 20 lineal feet was used. Repairs to the restroom are addressed in the RESTROOM/ SHOWER REPLACEMENT project which should be done in conjunction with this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0168EXT4 | EXTERIOR STUCCO FINISH REPAIRS | 0168 | The exterior walls have a stucco finish. Some of the areas have cracked and the stucco and underlying block have been damaged. Some damage was caused by forklifts and large delivery trucks. This project would provide for the repair of the damaged areas and repainting with an elastomeric paint. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0165HVA3 | EVAPORATIVE COOLER REPLACEMENT | 0165 | The 14 roof top evaporative cooling units were installed in 1989. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 14 new evaporative coolers and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0173ELE1 | ELECTRICAL UPGRADE | 0173 | The electrical equipment in the tower is original to the building and due for replacement. The electrical panels, transformer, light switches and receptacles are showing signs of extreme wear. It is recommended the entire system be upgraded to ensure reliable operation and the safety of the occupants. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0173INT3 | REPAIR DAMAGED CEILING | 0173 | The gypsum board ceiling is severely damaged from a plumbing leak below the toilet and sink. This project would provide for the removal of the damaged gypsum board ceiling and installation of new 5/8" type X gypsum board. This estimate includes tape, texture and paint. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 1000
0172EXT3 | EXTERIOR SIDING REPLACEMENT | 0172 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding including priming and painting. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0173EXT3 | EXTERIOR SIDING REPLACEMENT | 0173 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding including priming and painting. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0171PLM1 | RESTROOM FIXTURE REPLACEMENT | 0171 | The water closet and sink in the tower are original to the building and in overall poor condition. This project would provide for replacing the fixtures. The removal and disposal of the existing fixtures is included in this estimate. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0172PLM1 | RESTROOM FIXTURE REPLACEMENT | 0172 | The water closet and sink in the tower are original to the building and in overall poor condition. This project would provide for replacing the fixtures. The removal and disposal of the existing fixtures is included in this estimate. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0173PLM1 | RESTROOM FIXTURE REPLACEMENT | 0173 | The water closet and sink in the tower are original to the building and in overall poor condition. This project would provide for replacing the fixtures. The removal and disposal of the existing fixtures is included in this estimate. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0171EXT4 | WINDOW REPLACEMENT | 0171 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0172ELE1 | ELECTRICAL UPGRADE | 0172 | The electrical equipment in the tower is original to the building and due for replacement. The electrical panels, transformer, light switches and receptacles are showing signs of extreme wear. It is recommended the entire system be upgraded to ensure reliable operation and the safety of the occupants. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0158SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0158 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 239778
2183EXT3 | EXTERIOR DOOR REPLACEMENT | 2183 | The exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | SDCC GLASS SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2183EXT4 | OVERHEAD DOOR REPLACEMENT | 2183 | There is a 16'x14' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | SDCC GLASS SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0161SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0161 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 239778
0160HVA2 | EXHAUST FAN REPLACEMENT | 0160 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 9000
0159HVA2 | EXHAUST FAN REPLACEMENT | 0159 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 9000
0171HVA1 | HVAC UNIT REPLACEMENTS | 0171 | The existing wall-mounted HVAC units are more than 25 years old, not energy efficient and have reached the end of their expected life. This project would provide for the installation of two new energy efficient wall mounted HVAC units including connections to existing utilities. Removal and disposal of the old units are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2183EXT2 | EXTERIOR FINISHES | 2183 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC GLASS SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 4000
0158HVA2 | EXHAUST FAN REPLACEMENT | 0158 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 9000
0160SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0160 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 239778
2710INT1 | INTERIOR FINISHES | 2710 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC P. I. SANDBLASTING SHED 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0166EXT2 | ROOF REPLACEMENT | 0166 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 195888
0169SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0169 | There are no exit signs or emergency egress lights in the guard tower. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 750
0169INT3 | FLOORING INSTALLATION | 0169 | The VCT (vinyl composite tile) flooring in the tower has been removed and the concrete is exposed. It is recommended to install new VCT flooring. This project would provide for installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2183ENR1 | WINDOW REPLACEMENT | 2183 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | SDCC GLASS SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0168PLM2 | RESTROOM/ SHOWER REPLACEMENT | 0168 | There is a restroom and shower in the building that are damaged from abuse and neglect and the waste line has collapsed. This project would provide for the restroom and shower to be repaired back to operational condition. This estimate includes replacement of all of the fixtures and finishes. This project must be done in conjunction with the RESTROOM WASTELINE REPAIR project. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0159SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0159 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 239778
0165INT7 | FLOORING REPLACEMENT | 0165 | The VCT (vinyl composite tile), painted concrete and ceramic tile in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base, painting or sealing the concrete as needed and replacing the ceramic tile in the next 2-3 years. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
2181EXT2 | EXTERIOR FINISHES | 2181 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC PI LUNCH ROOM | 9970 | Correct | SDCC |  | Indian Springs |  | 600 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 3000
0165SFT4 | EGRESS DOOR HARDWARE UPGRADE | 0165 | One of the exterior egress doors on the building was locked shut from the inside with deadbolt hardware. IBC 2012 section 1008.1.9.4 prohibits manually operated flush bolts or surface bolts on egress doors. This project would provide for the purchase and installation of emergency panic hardware to be installed on the door and removing the deadbolt locking hardware. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 2000
0165EXT2 | EXTERIOR DOOR REPLACEMENT | 0165 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of five new hollow metal doors, frames and hardware. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 16 exterior doors, not including the Laundry/ Culinary side of the building. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 64000
0165EXT4 | OVERHEAD DOOR REPLACEMENT | 0165 | There are eight 12'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0169PLM2 | RESTROOM FIXTURE REPLACEMENT | 0169 | The water closet and sink in the tower are original to the building and in overall poor condition. This project would provide for replacing the fixtures. The removal and disposal of the existing fixtures is included in this estimate. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0165INT6 | INTERIOR DOOR REPLACEMENT | 0165 | The existing interior doors in the Industrial/ Vocational side of the building are original to the building and are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new metal doors. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 44 interior doors, not including the Laundry/ Culinary side of the building. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 88000
0164ENR2 | WINDOW REPLACEMENT | 0164 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 98 units. Removal and disposal of the existing windows is included in this estimate. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 117600
2180EXT2 | EXTERIOR DOOR REPLACEMENT | 2180 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | SDCC PI QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0169EXT3 | WINDOW REPLACEMENT | 0169 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
2180HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2180 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | SDCC PI QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0160INT1 | INTERIOR FINISHES | 0160 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85635
0162PLM2 | TOILET AND LAVATORY REPLACEMENT | 0162 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 561000
0162SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0162 | Housing Unit 6 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275000
0159SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0159 | Housing Unit 3 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275000
0160SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0160 | Housing Unit 4 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275000
0161SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0161 | Housing Unit 5 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275000
0161SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0161 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0156SEC1 | VISITOR CENTER SECURITY UPGRADES | 0156 | The visitor center serves as the primary access for friends and families visiting inmates at Indian Springs. The potential for the introduction of contraband into the prison via visitors remains a problem, and this project addresses general security and related issues in this portion of the building. Included in the alterations are the installation of fixed covers for the restroom lavatory drains and replacing hollow stall components with solid materials. In the no-contact visitors room, there are line of sight issues for the correction officers, and the phone systems are outdated and in need of replacement. This project will include the installation of a full-view window in this area, a new correctional type phone system, and the installation of outlets and communications equipment for deaf and hearing impaired inmates and visitors. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 65000
0157SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0157 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0168HVA1 | REFRIGERATION CONDENSING UNIT REPLACEMENTS | 0168 | The refrigeration system is served by three rooftop condensing units. Based on lifecycle analysis and condition, these units should be scheduled for replacement in the next 1-2 years. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 15000
0157SEC2 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0157 | Housing Unit 1 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275000
0163SEC1 | EXTERIOR DOOR REPLACEMENT | 0163 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0162SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0162 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0162SEC2 | EXTERIOR DOOR REPLACEMENT | 0162 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0161PLM1 | TOILET AND LAVATORY REPLACEMENT | 0161 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 561000
0161SEC2 | EXTERIOR DOOR REPLACEMENT | 0161 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0160PLM2 | TOILET AND LAVATORY REPLACEMENT | 0160 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 561000
0160SEC2 | EXTERIOR DOOR REPLACEMENT | 0160 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0159PLM1 | TOILET AND LAVATORY REPLACEMENT | 0159 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 561000
0159SEC2 | EXTERIOR DOOR REPLACEMENT | 0159 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0158PLM2 | TOILET AND LAVATORY REPLACEMENT | 0158 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 561000
0163PLM1 | TOILET AND LAVATORY REPLACEMENT | 0163 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 561000
0173EXT2 | EXTERIOR FINISHES | 0173 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0157SEC1 | EXTERIOR DOOR REPLACEMENT | 0157 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. It was noted that maintenance problems are occurring often. Because of security concerns and the condition of the doors, it is recommended they be replaced in the next two years. This project includes doors, frames, hardware, painting and disposal of the old doors. A total of 6 solid metal security-grade doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0156INT1 | INTERIOR FINISHES | 0156 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 214560
0170INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0170 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for removal and disposal of the VCT and plywood and installation of new plywood subfloor and new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0170EXT1 | ROOF REPLACEMENT | 0170 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0171INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0171 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for removal and disposal of the VCT and plywood and installation of new plywood subfloor and new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0171EXT1 | ROOF REPLACEMENT | 0171 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0172INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0172 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for removal and disposal of the VCT and plywood and installation of new plywood subfloor and new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1482EXT1 | EXTERIOR FINISHES | 1482 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
0158SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0158 | Housing Unit 2 was constructed in 1981. The cell door locks and mechanisms are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and mechanisms. A total of 102 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275000
0365EXT1 | EXTERIOR FINISHES | 0365 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC WELDING SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 400 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
0168EXT1 | EXTERIOR FINISHES | 0168 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105610
0172EXT2 | EXTERIOR FINISHES | 0172 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0171EXT2 | EXTERIOR FINISHES | 0171 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0159INT1 | INTERIOR FINISHES | 0159 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85635
0169EXT2 | EXTERIOR FINISHES | 0169 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0167EXT1 | EXTERIOR FINISHES | 0167 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PUMP HOUSE 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 624 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3120
0159SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0159 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0158SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0158 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0160SEC3 | SECURITY GLAZING UPGRADE AT CENTRAL CONTROL | 0160 | The central control area in the housing unit is encased in an expanded metal lath and plexiglass. This arrangement protects the correctional officers, but causes line of sight issues, blind spots and is damaged from abuse. The plexiglass is scratched and hazy making it difficult to see through. This project recommends replacing the expanded metal lath and plexiglass with a high-impact resistant glazing product, new frames and reinforcement to support the new glazing systems. A total of 6 glazing panels was used for this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0624EXT1 | EXTERIOR FINISHES | 0624 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC WATER TANK | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 2551 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25510
0166INT3 | INTERIOR FINISHES | 0166 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 81620
0170PLM1 | RESTROOM FIXTURE REPLACEMENT | 0170 | The water closet and sink in the tower are original to the building and in overall poor condition. This project would provide for replacing the fixtures. The removal and disposal of the existing fixtures is included in this estimate. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0157INT1 | INTERIOR FINISHES | 0157 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85635
0162INT1 | INTERIOR FINISHES | 0162 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85635
0161INT1 | INTERIOR FINISHES | 0161 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85635
0168HVA3 | WATER TREATMENT SYSTEM INSTALLATION | 0168 | The existing cooling towers are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the cooling towers. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 25000
0157PLM1 | TOILET AND LAVATORY REPLACEMENT | 0157 | The existing toilets and lavatories in each of the 102 inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing toilets and lavatories with a stainless steel combination toilet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 561000
0170EXT3 | EXTERIOR SIDING REPLACEMENT | 0170 | The tower has a painted T1-11 siding that is due for replacement. The existing siding is in poor condition and is missing some trim pieces. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding including priming and painting. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0166ADA2 | ADA RESTROOM REPLACEMENT | 0166 | The building does not have an accessible restroom. The existing restrooms on the upper level and lower level do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom on each level. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 30000
0158INT1 | INTERIOR FINISHES | 0158 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85635
0166INT4 | INTERIOR DOOR REPLACEMENT | 0166 | The existing interior doors in the building are original to the building and are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new metal doors. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 22 interior doors. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44000
0166INT5 | FLOORING REPLACEMENT | 0166 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The wood gymnasium flooring is addressed in a separate project. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84708
0166INT6 | GYMNASIUM FLOOR REPLACEMENT | 0166 | The existing wood flooring in the gymnasium is reaching the end of its useful life. This project would provide for the removal of the existing flooring and installation of a new wood floor. A 25/32" thick maple on a sleeper system was used for this estimate. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 103680
0166PLM2 | ROOFTOP RESTROOM INSTALLATION | 0166 | There is a guard station on the roof which is not equipped with a code compliant restroom. Guards are required to spend continuous hours at the station with no opportunity to use the restrooms inside the Gymnasium building. This project would provide for installing a restroom on the roof equipped with code compliant fixtures, finishes, hot and cold water service and a proper sewer connection. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 50000
0167INT1 | INTERIOR FINISHES | 0167 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | SDCC PUMP HOUSE 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 624 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3120
0168SFT2 | STORAGE RACK SEISMIC BRACING | 0168 | This project would provide for the installation of seismic bracing for the steel storage racks in the Warehouse. Section 15.5.3 of ASCE 7 describes the provisions required for seismic bracing of steel storage racks including connections to the floor, connections between back to back racks and protections for lower portions of posts from forklifts or other equipment. This project would provide for installing seismic bracing as required. The assessment and design of seismic bracing requirements by a licensed structural or civil engineer are not included in the estimate. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 35000
0166ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0166 | This building contains water fountains on each floor that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 8000
0170EXT2 | EXTERIOR FINISHES | 0170 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0170EXT4 | WINDOW REPLACEMENT | 0170 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0168INT1 | REFRIGERATION UNIT REPAIRS | 0168 | The central stores warehouse includes three coolers and a freezer that are designed for walk-in and pallet jack operations. The doors, floors and walls have been damaged over the years by fork-lifts and other equipment. Several of the seals for the units have been compromised. This projects recommends new doors, gaskets and frames and general repair to walls and floors to address damage. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CENTRAL PLANT/WAREHOUSE | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 21122 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0166SEC1 | EXTERIOR DOOR REPLACEMENT | 0166 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of five new hollow metal doors, frames and hardware. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 6 new exterior doors. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0173EXT1 | ROOF REPLACEMENT | 0173 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0173INT1 | FLOORING AND SUBFLOORING REPLACEMENT | 0173 | The VCT (vinyl composite tile) flooring and subfloor are damaged and reaching the end of their useful life. It is recommended to replace the VCT flooring and plywood subfloor. This project would provide for removal and disposal of the VCT and plywood and installation of new plywood subfloor and new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0172EXT1 | ROOF REPLACEMENT | 0172 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0160SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0160 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. Not needed in I-3 occupancies. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5871.6889
0163INT1 | INTERIOR FINISHES | 0163 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85635
0159SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0159 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. Not needed in I-3 occupancies. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5871.6889
0170ELE1 | ELECTRICAL UPGRADE | 0170 | The electrical equipment in the tower is original to the building and due for replacement. The electrical panels, transformer, light switches and receptacles are showing signs of extreme wear. It is recommended the entire system be upgraded to ensure reliable operation and the safety of the occupants. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2184EXT1 | EXTERIOR FINISHES | 2184 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC AUTOMOTIVE SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 1200 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2709INT1 | INTERIOR FINISHES | 2709 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC P. I. PAINT BOOTH | 9970 | Correct | SDCC |  | Indian Springs |  | 704 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3520
0164EXT2 | EXTERIOR FINISHES | 0164 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken stucco areas, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC EDUCATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 19824 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 138768
2706EXT1 | EXTERIOR FINISHES | 2706 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PUMP HOUSE 2 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2180EXT1 | EXTERIOR FINISHES | 2180 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PI QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2553EXT1 | EXTERIOR FINISHES | 2553 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the wall panels and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC | PI | Indian Springs | 2004 | 20000 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2707EXT1 | EXTERIOR FINISHES | 2707 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
0158EXT3 | EXTERIOR FINISHES | 0158 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119889
0166EXT1 | EXTERIOR FINISHES | 0166 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GYM/RECREATION BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 16324 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 81620
0163EXT3 | EXTERIOR FINISHES | 0163 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 7 | 9970 | Correct | SDCC |  | Indian Springs | 1981 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119889
0162EXT3 | EXTERIOR FINISHES | 0162 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119889
0161EXT3 | EXTERIOR FINISHES | 0161 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119889
2708EXT1 | EXTERIOR FINISHES | 2708 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC K GATE GUARD SHACK | 9970 | Correct | SDCC |  | Indian Springs |  | 48 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 240
0159EXT3 | EXTERIOR FINISHES | 0159 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119889
0165EXT1 | EXTERIOR FINISHES | 0165 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 381545
0157EXT3 | EXTERIOR FINISHES | 0157 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119889
0156EXT1 | EXTERIOR FINISHES | 0156 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 12/01/2001 and 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC CONTROL/VISITATION | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 47498 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 214560
0155INT1 | INTERIOR FINISHES | 0155 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49475
0155EXT1 | EXTERIOR FINISHES | 0155 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC ADMINISTRATION A | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 9895 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49475
0160EXT3 | EXTERIOR FINISHES | 0160 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing the broken fluted blocks, power washing, priming and painting the stucco, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 119889
2707INT1 | INTERIOR FINISHES | 2707 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC TOWER 1 SALLY PORT | 9970 | Correct | SDCC |  | Indian Springs |  | 144 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
2181INT1 | INTERIOR FINISHES | 2181 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PI LUNCH ROOM | 9970 | Correct | SDCC |  | Indian Springs |  | 600 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2183INT1 | INTERIOR FINISHES | 2183 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GLASS SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Four to Ten Years | Long-Term Needs | 3 | 4000
2184INT1 | INTERIOR FINISHES | 2184 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC AUTOMOTIVE SHOP | 9970 | Correct | SDCC |  | Indian Springs |  | 1200 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1482INT1 | INTERIOR FINISHES | 1482 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUN POST 1 AT GYM BUILDING | 9970 | Correct | SDCC |  | Indian Springs | 1987 | 80 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
2709EXT1 | EXTERIOR FINISHES | 2709 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC P. I. PAINT BOOTH | 9970 | Correct | SDCC |  | Indian Springs |  | 704 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 704
0162SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0162 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 6 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 239778
2553INT1 | INTERIOR FINISHES | 2553 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be checked for tears and leaks at least once in the next 2-3 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PRISON INDUSTRIES SPRUNG BLDG | 9970 | Correct | SDCC | PI | Indian Springs | 2004 | 20000 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2180INT1 | INTERIOR FINISHES | 2180 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PI QUONSET HUT | 9970 | Correct | SDCC |  | Indian Springs | 2001 | 1000 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0167SFT1 | FIRE ALARM SYSTEM UPGRADE | 0167 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements during the next remodel or addition to ensure the safety of the occupants. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PUMP HOUSE 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 624 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 2496
0157SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0157 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 239778
0173INT2 | INTERIOR FINISHES | 0173 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 5 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 1200
0172INT2 | INTERIOR FINISHES | 0172 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 4 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 1200
0171INT2 | INTERIOR FINISHES | 0171 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 3 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 1200
0170INT2 | INTERIOR FINISHES | 0170 | The interior finishes are in poor condition. It is recommended that the interior walls and ceiling be repaired and painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. Additional costs have been added for repairing large areas of damaged drywall. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 2 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 120 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 1200
2708INT1 | INTERIOR FINISHES | 2708 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC K GATE GUARD SHACK | 9970 | Correct | SDCC |  | Indian Springs |  | 48 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 240
0157HVA2 | EXHAUST FAN REPLACEMENT | 0157 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units are recommended. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC HOUSING UNIT 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 17127 | 2013-04-30 | Immediate to Two Years | Currently Critical | 1 | 9000
0169INT2 | INTERIOR FINISHES | 0169 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC GUARD TOWER 1 | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 200 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0165INT2 | INTERIOR FINISHES | 0165 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC INDUSTRIAL/CULINARY/P.I. | 9970 | Correct | SDCC |  | Indian Springs | 1980 | 76309 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 381545
2710EXT1 | EXTERIOR FINISHES | 2710 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC P. I. SANDBLASTING SHED 1 | 9970 | Correct | SDCC |  | Indian Springs |  | 120 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
2706INT1 | INTERIOR FINISHES | 2706 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2013. | SDCC PUMP HOUSE 2 | 9970 | Correct | SDCC |  | Indian Springs |  | 800 | 2013-04-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1481SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1481 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 16000
1481HVA1 | HVAC EQUIPMENT REPLACEMENT | 1481 | There are 4 rooftop packaged HVAC units that are original to the building and are not energy efficient. The packaged HVAC units have been cannibalized, the heat pump systems have been removed, the air conditioning has been converted to R-22 and the heating has been converted to electric heat strip. The packaged HVAC units have reached the end of their expected and useful life. This project would provide for the installation of three new 20 ton and one new 4 ton packaged HVAC units. Also included in this estimate is new curb adapters, roofing modifications, 100 feet of new condensate line, crane and rigging removal and installation and all required connections to utilities. Additional features to include direct drive, economizer and Direct Digital Controls (DDC). This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007 and 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 260000
1481ELE1 | ELECTRICAL UPGRADE | 1481 | This building was constructed before the high demand for electrical services were needed for security systems, computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. The electrical panels and receptacles are at their limit. There are also problems with rusting conduits particularly underground conduits. As failures have happened, new conduits have been installed on the interior walls and some are not properly connected. It is recommended the entire system be upgraded to meet the evolving needs of the building and provide safe electrical distribution. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 800000
1481PLM2 | PLUMBING REPLACEMENT | 1481 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted and failing especially underground. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 800000
1481PLM3 | WATER HEATER REPLACEMENT | 1481 | There is one 80 gallon and two 119 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that three new propane fired water heaters be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Four to Ten Years | Long-Term Needs | 3 | 15000
1481PLM4 | WATER TREATMENT SYSTEM REPLACEMENT | 1481 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. The water comes directly into the water treatment system without going into a Pressure Reducing Valve (PRV) first, which causes abnormal wear and tear on the water treatment system. Failure of the water softening/ treatment system causes additional wear and tear on the domestic water supply lines, water heaters and plumbing fixtures. This project would provide for the installation of a PRV (to be installed prior to the water softener/ treatment system) and the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program to include an updated chemical control system, service and employee training to be provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 25000
1481SEC3 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 1481 | Housing Unit 8 was constructed in 1988. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 200 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001, 04/03/2007 and 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 1600000
1481EXT3 | WINDOW REPLACEMENT | 1481 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. This project or a portion thereof was previously recommended in the FCA report dated 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480000
1481PLM1 | JANITORS CLOSET REPAIRS | 1481 | The mop sink in the Janitors Closet has several cracks in the concrete and is leaking. This could lead to mold growth if not addressed. This project would provide for a new fiberglass mop sink and fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007 and 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 1800
1481SFT7 | SPRINKLER HEAD REPLACEMENT | 1481 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to them and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with tamper-resistant sprinkler heads. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 40000
1481INT3 | RESTROOM REMODEL | 1481 | The restroom in the control room is original to the building and in overall poor condition. The finishes, fixtures, toilet and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1481ADA2 | ADA SHOWER UPGRADE | 1481 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 75000
1481INT2 | SHOWER REPAIRS | 1481 | There are seventeen showers in the building that are showing signs of failure. The walls and fixtures should be scheduled for repairs. The walls are constructed of gypsum board covered by fiberglass reinforced panels (FRP). The gypsum board is failing in the wet environment and should be replaced with a cementitious backerboard. This project would provide for removing the gypsum board and replacing it with a more appropriate wall board, such as Hardiboard, covered with new FRP and new fixtures. Removal and disposal of the existing materials is included in the estimate. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 127500
1481SFT8 | SMOKE DETECTOR MAINTENANCE | 1481 | The smoke detectors in the building should be tested and vacuumed annually or per the manufacturer's instructions. It is recommended to clean the smoke detectors and the mechanical chases where they are located in to ensure they remain in full operational condition. This project should be done after a major remodel or construction project in the building and before the inmates are returned to the cells saving time and cost. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 10000
1481SIT1 | SITE DRAINAGE UPGRADES | 1481 | The grade does not slope away effectively from the building. Water has pooled against the foundation and over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
1481SIT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 1481 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention, an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 9000
1481ADA4 | TDD INSTALLATION | 1481 | The Housing Unit is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 60000
1481SFT5 | PANIC HARDWARE IN ELECTRICAL ROOMS | 1481 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed in 1988. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 1-2 years. The estimate is based on one door that requires panic hardware. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 3000
1481PLM5 | ISOLATION VALVE INSTALLATION | 1481 | There are no isolation valves for the individual wings of the building's water lines. There is a main shut off valve for the entire building. By installing isolation valves to the individual wings of the building, this will allow the maintenance staff to do repairs and maintenance to the plumbing without shutting down the entire building. More importantly, a leak in the building can be shut down quickly minimizing damage in an emergency. This estimate provides for 3 ball valves to be installed at each wing of the building. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1481EXT6 | ROOF DRAIN DOWNSPOUT INSTALLATION | 1481 | The rain gutters are in need of full length downspouts and extensions. The downspouts currently terminate within inches of the rain gutter with no continuous drainage away from the building. This is causing the water to run down the building and pool next to the foundation and damage the foundation and stucco walls. This project would provide for full length downspouts to grade and extensions to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 8704
1481EXT5 | ROOF REPAIRS | 1481 | The curb and ductwork flashings and sealants around the roof penetrations and in the rain gutters are due for repair. The sealants are dried out and cracking and the flashings are coming loose. Birds on the roof are pecking at the sealants, causing them to prematurely breakdown and to leak. This project would provide funds for repairing the roof. The estimate includes repairing the curb and ductwork flashings, removing the existing sealants and applying new sealants. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 15000
1481EXT4 | ROOF REPLACEMENT | 1481 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires on 05/20/2017. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt onto the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 05/20/2002. It is recommended that this building be re-roofed in the next 4-5 years. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Four to Ten Years | Long-Term Needs | 3 | 229548
1481ELE2 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 1481 | The electrical panel in the building does not have proper floor space clearance. The 2012 IFC Section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." The electrical room is in the shape of a triangle and the electrical panel is located in one of the corners of the room. This project would move the electrical panel in the electrical room to provide adequate working space per IFC. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 5000
1481SFT4 | EXTERIOR LANDING INSTALLATION | 1481 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1481ENR1 | LIGHTING UPGRADE | 1481 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 256000
1481SFT6 | FIRE RATED ELECTRICAL ROOM | 1481 | NFPA 13 requires a fire sprinkler in electrical rooms or if the electrical room complies within NFPA Section 5-13.11, which allows an exception to installing fire sprinklers in an electrical room, the electrical room shall meet all of the following requirements: the electrical room is dedicated to electrical equipment only; only dry-type electrical equipment is used; equipment is installed in a 2-hour fire rated enclosure including the floor and deck above and includes protection for penetrations; no combustible storage is permitted to be stored in the electrical room; any openings (doors) in the room must be properly fire rated at 90-minutes and must be self-closing and positive latching; any ventilation ductwork which penetrates the 2-hour barrier must be equipped with the appropriate fire dampers, and all penetrations must be properly fire stopped. This project would provide a 2 hour separation or a fire sprinkler to be installed in the electrical room per NFPA. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 5000
1481ADA3 | ADA TABLE UPGRADE | 1481 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 3000
1481SEC2 | VIDEO SECURITY SYSTEM UPGRADE | 1481 | The video security system is outdated and some of the cameras do not function consistently. This project addresses replacement of the cameras and controls in the building with all digital equipment as well as sufficient storage capacity. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001, 04/03/2007 and 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 250000
1481EXT2 | EXTERIOR FINISHES | 1481 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas of stucco, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/03/2007 and 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 320000
1481INT1 | INTERIOR FINISHES | 1481 | It is recommended that the interior walls and ceilings be painted at least once in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001, 04/03/2007 and 4/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Immediate to Two Years | Currently Critical | 1 | 320000
1481SEC1 | EXTERIOR DOOR REPLACEMENT | 1481 | The existing exterior metal doors and frames appear to be original to the building. They are damaged and showing signs of wear and deterioration from constant use and inmate abuse. The window in one of the doors is broken. This project would provide for the removal and replacement of nine new metal door assemblies including frames, locks, hardware and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001, 04/03/2007 and 04/30/2013. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/13/2016. | SDCC HOUSING UNIT 8 | 9970 | Correct | SDCC |  | Indian Springs | 1988 | 32000 | 2016-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0741ADA1 | ADA RESTROOM UPGRADE | 0741 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0737ENR1 | WINDOW REPLACEMENT | 0737 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0737ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0737 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0737SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0737 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 64134
0737SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0737 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2291
0737SFT6 | SAFETY CABINETS | 0737 | The storage areas contains many different paints, stains and other hazardous products on open shelves. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 10000
0739EXT2 | EXTERIOR FINISHES | 0739 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13550
0739SFT1 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0739 | The interior stair handrails in the building are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports in accordance with the 2006 IBC Chapter 10, Section 1012. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2500
0737EXT5 | EXTERIOR FINISHES | 0737 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 22905
0741ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 0741 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0741SFT2 | INTERIOR STAIRWAY REPLACEMENT | 0741 | The stairway between the first floor and the second floor does not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The rise and run are inconsistent and there are no handrails. This project would provide funding to remove and replace the stairway and handrail. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0741ENR1 | EVAPORATIVE COOLER REPLACEMENT | 0741 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0741PLM1 | WATER HEATER REPLACEMENT | 0741 | There are two 30 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0747INT2 | FLOORING REPLACEMENT | 0747 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9624
0739INT1 | INTERIOR FINISHES | 0739 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13550
0736INT2 | RESTROOM REMODEL | 0736 | The four restrooms in the building are more than 20 years old and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of three of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0735SFT2 | SMOKE ALARM INSTALLATION | 0735 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 1000
0735SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0735 | The building is a R-1 occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 29428
0734SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0734 | The building is a R-1 occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 22820
0734SFT5 | FIRE ALARM SYSTEM INSTALLATION | 0734 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 6520
2161EXT1 | EXTERIOR FINISHES | 2161 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #094 PUMP HOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 183 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 915
0735SFT4 | FIRE ALARM SYSTEM INSTALLATION | 0735 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 8408
0735SFT5 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0735 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 5255
0737INT3 | RESTROOM REMODEL | 0737 | The restroom in the building has older fixtures and finishes and is due for a complete remodel. The drain from the urinal had an active leak at the time of the survey. This project would provide for a complete remodel of the restroom fixtures, plumbing, hardware, floor and wall finishes. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0736ADA1 | ADA RESTROOM UPGRADE | 0736 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom for one of the units in the triplex. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0737INT2 | INTERIOR FINISHES | 0737 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 22905
0734ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 0734 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the building entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 10000
0736ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 0736 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the building entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0736ELE1 | ELECTRICAL UPGRADE | 0736 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97240
0736SFT3 | SMOKE ALARM INSTALLATION | 0736 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 3200
0736SFT4 | FIRE ALARM SYSTEM INSTALLATION | 0736 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 19448
0736SFT5 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0736 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 12155
0746INT3 | RESTROOM REMODEL | 0746 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0735ELE1 | ELECTRICAL UPGRADE | 0735 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42040
0745INT5 | KITCHEN REMODEL | 0745 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0744INT3 | RESTROOM REMODEL | 0744 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9971SIT10 | SIDEWALK REPLACEMENT | 9971 | Some of the sidewalks serving the buildings and recreation areas on this site are deteriorated and failing. In some areas cracks wider than four inches have been identified, and there is settling in many locations. This project addresses removal and replacement of existing sidewalks as needed. 10,000 SF of 4" thick concrete sidewalk was used for this estimate. | STEWART CAMPUS SITE | 9971 | Admin | PubWorks | B&G | Stewart | 1890 |  | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9971SIT9 | CRACK FILL & SEAL ASPHALT PAVING | 9971 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 300,000 square feet of asphalt area was used to generate this estimate. | STEWART CAMPUS SITE | 9971 | Admin | PubWorks | B&G | Stewart | 1890 |  | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
0745ENR1 | LIGHTING UPGRADE | 0745 | The existing lighting fixtures are the older incandescent type. The fixtures are older, some are broken and they not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0746ENR1 | LIGHTING UPGRADE | 0746 | The existing lighting fixtures are the older incandescent type. The fixtures are older, some are broken and they not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0747ENR1 | LIGHTING UPGRADE | 0747 | The existing lighting fixtures are the older incandescent type. The fixtures are older, some are broken and they not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0747INT4 | INTERIOR DOOR REPLACEMENT | 0747 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0744INT5 | KITCHEN REMODEL | 0744 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0746INT4 | INTERIOR DOOR REPLACEMENT | 0746 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0746INT5 | KITCHEN REMODEL | 0746 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0747INT5 | KITCHEN REMODEL | 0747 | The kitchen and associated cabinets in the are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0746ELE1 | ELECTRICAL UPGRADE | 0746 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23960
0744ELE1 | ELECTRICAL UPGRADE | 0744 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23960
2160EXT2 | EXTERIOR FINISHES | 2160 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #070 BARN (B&G STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1910 | 2160 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10800
2163EXT2 | DEMOLISH STRUCTURE | 2163 | The building is an old garage that is no longer in use. It has significant structural failures and the roof is completely deteriorated. It is recommended that this structure be demolished. | #108 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1929 | 750 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0731ADA4 | ADA ACCESSIBLE PATH OF TRAVEL | 0731 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 10000
2157EXT2 | ROOF REPLACEMENT | 2157 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single ply membrane roof. This estimate includes removal and disposal of the old roofing. | #161 WATER PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1978 | 938 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11256
0744ENR1 | LIGHTING UPGRADE | 0744 | The existing lighting fixtures are the older incandescent type. The fixtures are older, some are broken and they not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0745ELE1 | ELECTRICAL UPGRADE | 0745 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24060
0745INT3 | RESTROOM REMODEL | 0745 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0747ELE1 | ELECTRICAL UPGRADE | 0747 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24060
0744INT4 | INTERIOR DOOR REPLACEMENT | 0744 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0745INT4 | INTERIOR DOOR REPLACEMENT | 0745 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 8 interior doors was used in this estimate. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0734EXT2 | EXTERIOR FINISHES | 0734 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 8150
0419INT3 | FLOORING INSTALLATION | 0419 | The floor coverings in the building have been removed and disposed of leaving the plywood sub-floor exposed. This project would provide for installing new 12x12 VCT with a 6" base, heavy duty commercial grade carpet and ceramic tile in the restrooms in the next 2-3 years. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44816
0454SFT6 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0454 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4500
0455ADA2 | ADA RAMP REPLACEMENT | 0455 | This building has an ADA accessible ramp located on the north side of the building. This ramp is on the accessible path of travel from the parking space to the rear entrance of the building. The ramp does not have proper landings, curbs or handrails. This project would provide for replacing the ramp with a fully compliant ramp. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0455ADA3 | ADA RESTROOM UPGRADE | 0455 | One side of the duplex has some ADA improvements, but it is due for an upgrade. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0454ELE2 | ELECTRICAL UPGRADE | 0454 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34580
0455SFT2 | SMOKE ALARM INSTALLATION | 0455 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 800
0455SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0455 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Alterations, repairs, additions or changes of occupancy. 1. Chapter 34 of the International Building Code, 2006 edition, will be used to determine whether an alteration, repair, addition or change of occupancy of an existing building or structure must comply with the requirements for a new building or structure. 2. Structures existing before November 1, 1994, must comply with the requirements set forth in section 3410.2 of the International Building Code, 2006 edition. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 25206
0419SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0419 | The stone exterior is exposed to water damage from the lawn sprinklers. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the stone. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0687ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0687 | This building contains 3 water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 8000
0454SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0454 | This building is lacking a fire detection and alarm system and only has one smoke detector. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 7200
0419PLM1 | WATER HEATER REPLACEMENT | 0419 | There is a 30 gallon electric water heater in the building that was installed in 1995. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0419ENR3 | HVAC EQUIPMENT REPLACEMENT | 0419 | The four HVAC units were installed in 2001. They are not energy efficient and have reached the end of their expected and useful life. The flex ducting throughout the building is not in compliance with Section 7.3.10 of the Nevada State Public Works Division Adopted Standards which limits the length of flexible ducting to 5 feet. There is also no provisions in the system to introduce outdoor ventilation to the HVAC system. This project would provide for installation of four new HVAC packaged units and replacing the duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84030
0419EXT2 | EXTERIOR FINISHES | 0419 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 28010
0419SEC2 | SECURITY SYSTEM INSTALLATION | 0419 | The building does not have a security system. If the building is reopened as a museum, it will be necessary to secure the building and its artifacts. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28010
0419ENR2 | LIGHTING UPGRADE | 0419 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14005
0419ADA3 | ADA SIGNAGE | 0419 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 750
0734INT2 | INTERIOR DOOR REPLACEMENT | 0734 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 12 interior doors was used in this estimate. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0687INT3 | RESTROOM REMODEL | 0687 | The two large restrooms in the dormitory have not been remodeled for at least 20 years and are in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0424PLM1 | WATER HEATER REPLACEMENT | 0424 | There is a 80 gallon electric water heater in the building that is more than ten years old. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0419SFT6 | SEISMIC RETROFIT | 0419 | This building is an unreinforced stone masonry structure which requires seismic strengthening to meet current life safety codes. An initial study was done under CIP 05-M46 which provided detailed recommendations for a seismic retrofit. The roof portion of the repairs has already been completed so this estimate is for the remaining work that is required. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112040
0420EXT5 | EXTERIOR FINISHES | 0420 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 29585
0420ADA3 | KITCHEN REMODEL | 0420 | The kitchen is in fair to poor condition and does not meet the Americans with Disabilities Act (ADA) requirements. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components and incorporating ADA elements into the design such as providing an accessible sink and faucet handles. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 35000
0420ENR1 | LIGHTING UPGRADE | 0420 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5917
0420SFT5 | EXTERIOR LANDING INSTALLATION | 0420 | Section 1008.1 of the 2012 IBC describes the requirements for egress doors including floor elevations and landings. Landings shall have a length measured in the direction of travel of not less than 44 inches. There are three doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for three exterior doors. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 7500
0424INT3 | RESTROOM REMODEL | 0424 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinet, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0424SFT2 | SMOKE ALARM INSTALLATION | 0424 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 1000
0454SFT5 | ADA DOOR HARDWARE REPLACEMENT | 0454 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4500
0424ENR2 | HVAC UPGRADE | 0424 | The existing HVAC system consists of a natural gas fired furnace and a window mounted evaporative cooler. This project would provide for replacing the existing equipment with an exterior ground mounted packaged unit that provides natural gas-fired heating as well as air conditioning. Ducting and vents will need to be installed in the basement as well. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0454SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0454 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 25200
0447EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0447 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #025 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 127920
0454ELE1 | ELECTRICAL UPGRADE | 0454 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0454ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 0454 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0454ADA3 | INTERIOR ACCESSIBILITY UPGRADES | 0454 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. An accessible path of travel throughout the interior of the building is necessary to comply with ADA accessibility requirements. There are at least two areas of the building that have a change in level greater than 1/2". This project would provide for raising the floor level to match or installing compliant ramps at these locations. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 25000
0454ADA4 | ADA RESTROOM UPGRADE | 0454 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0454SFT2 | INTERIOR STAIRWAY REPLACEMENT | 0454 | The stairs and handrails between the first floor and the second floor do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. This project would provide funding to remove and replace the stairway and handrail. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 9000
0687ADA3 | ADA SIGNAGE | 0687 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 1500
0424SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0424 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 8888
0732SFT4 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0732 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4365
0732INT2 | KITCHEN REMODEL | 0732 | The kitchen in each unit of the duplex is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components in both living units. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 30000
0732ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 0732 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the building entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 10000
0455ELE1 | ELECTRICAL UPGRADE | 0455 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34580
0731ELE1 | ELECTRICAL UPGRADE | 0731 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0732ELE1 | ELECTRICAL UPGRADE | 0732 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34920
0732SFT1 | SMOKE ALARM INSTALLATION | 0732 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 1600
0419ADA1 | ADA RESTROOM UPGRADE | 0419 | The building does not have an accessible restroom. The three existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements and all three have older fixtures and finishes. A complete retrofit of each restroom necessary. This project would provide funding for construction of a unisex accessible restroom and remodeling the other two restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 45000
0732SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0732 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 6984
0732ENR1 | WINDOW REPLACEMENT | 0732 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0731SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0731 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 1500
0734SFT2 | CONCRETE STAIR REPLACEMENT | 0734 | The 4 sets of concrete stairs that access the building are deteriorating and do not have compliant handrails or landings. Spalling and cracking have occurred. Exposure to the elements is a contributing factor. This project recommends replacing the concrete stairs and installing new stairs and handrails in accordance with IBC Section 1012. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 24000
0734ADA2 | ADA RESTROOM UPGRADE | 0734 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom for one of the units in the duplex. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 10000
0734INT3 | RESTROOM REMODEL | 0734 | The two restrooms in the duplex are more than 20 years old and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom for one of the units in the duplex. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0734ELE1 | ELECTRICAL UPGRADE | 0734 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32600
0734SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0734 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4075
0734ENR1 | FURNACE REPLACEMENT | 0734 | The building is heated by a natural gas-fired furnace. It is more than 15 years old and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new natural gas-fired unit including connections to utilities. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0732SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0732 | The building is a R-1 occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 24444
0729EXT2 | CONSERVE AND PROTECT VACANT BUILDINGS | 0729 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #047 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 2183 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 43660
0687INT4 | JANITORS CLOSET REPAIRS | 0687 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitors Closets. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0687SFT3 | EGRESS LIGHTING UPGRADE | 0687 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and providing additional lights on the main exit routes and in individual rooms as needed. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2700
0687HVA1 | EXHAUST FAN INSTALLATION | 0687 | There are two rooms in the building with laundry facilities. These rooms are not equipped with any type of exhaust system to ventilate the rooms. When the laundry machines are running, heat and moisture build up in the rooms and the occupants prop open the fire rated doors. This compromises the fire safety design for the building. This project would provide for the purchase and installation of exhaust fan assemblies in each room including connections to utilities. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0727EXT5 | EXTERIOR DOOR REPLACEMENT | 0727 | The 2 exterior wood man doors are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0727INT2 | FLOORING REPLACEMENT | 0727 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with 12x12 VCT with a 6" base in the next 2-3 years. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
0727INT3 | RESTROOM REMODEL | 0727 | The restroom in the building is in overall poor condition. The finishes, fixtures, cabinets, toilets and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0727SFT2 | CONCRETE STAIR REPLACEMENT | 0727 | The concrete stairs that access the building are not code compliant and many areas of the concrete are spalling and cracking. It appears these stairs are original to the building and should be scheduled for replacement. This project would provide for removal and disposal of the existing concrete stairs and handrails and installation of new compliant stairs and handrails. The estimate is for the replacement of 2 separate stairs. 2012 IBC Chapter 10 was used as a reference for this project. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0732ADA1 | ADA RESTROOM UPGRADE | 0732 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of one of the restrooms is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0728SFT1 | FIRE EXTINGUISHER INSTALLATION | 0728 | The building does not have a portable fire extinguisher available. The building is currently used for storage and staff enters and exits the building. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | #046 STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 2590 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 1000
0732EXT2 | EXTERIOR DOOR REPLACEMENT | 0732 | The 4 exterior wood man doors are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0731EXT2 | EXTERIOR FINISHES | 0731 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 7-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 15000
0731INT2 | INTERIOR FINISHES | 0731 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 15000
0731INT3 | FLOORING REPLACEMENT | 0731 | The sheet vinyl and wood plank flooring in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be upgraded. This project would provide for removal and disposal of the existing sheet vinyl flooring and installation of new 12x12 VCT with a 6" base in its place as well as covering the wood planks with VCT. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0731INT4 | INTERIOR DOOR REPLACEMENT | 0731 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 18 interior doors was used in this estimate. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0731ENR1 | LIGHTING UPGRADE | 0731 | The existing lighting fixtures are the older incandescent type, are not energy efficient and several of the fixtures are damaged. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0731ENR2 | HVAC EQUIPMENT REPLACEMENT | 0731 | The existing HVAC system consists of wall mounted hydronic radiators and there is no cooling equipments. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas-fired heating as well as air conditioning. Ducting and vents will need to be installed in either the attic or the crawlspace as well. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0734ENR2 | LIGHTING UPGRADE | 0734 | The existing lighting fixtures are the older incandescent type, are not energy efficient and several of the fixtures are damaged. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4075
0728EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0728 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #046 STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 2590 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 51800
0731ADA2 | ADA RESTROOM UPGRADE | 0731 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of one of the restrooms is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0744EXT3 | EXTERIOR FINISHES | 0744 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 5990
0745EXT4 | EXTERIOR DOOR REPLACEMENT | 0745 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new wood doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0739EXT1 | ROOF REPLACEMENT | 0739 | The asphalt composition shingle roof and the corrugated metal roof on this building were in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #096 B&G WAREHOUSE | 9971 | Admin | PubWorks | B&G | Stewart | 1940 | 2710 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 32520
0740EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0740 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #056 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 2075 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 41500
0744EXT4 | EXTERIOR DOOR REPLACEMENT | 0744 | The 3 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new wood doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0747EXT3 | EXTERIOR FINISHES | 0747 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 6015
0740EXT1 | ROOF REPLACEMENT | 0740 | The wood shake shingle and asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #056 GARAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 2075 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 24900
0746EXT3 | EXTERIOR FINISHES | 0746 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 5990
0742EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0742 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #112 BARN (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 2450 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 49000
0742EXT1 | ROOF REPLACEMENT | 0742 | The tin shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new tin shingle roof and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #112 BARN (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 2450 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 29400
0741ELE1 | ELECTRICAL UPGRADE | 0741 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0741SIT1 | TREE REMOVAL | 0741 | The building has two trees which are growing up against the structure. The trees move in windy conditions, rubbing the roofs, which can cause premature failure of the roof system and voiding roof warranties. The root systems are causing shifting and heaving of the foundation and sidewalks, creating unsafe conditions. This project recommends removing the trees. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0743EXT1 | ROOF REPLACEMENT | 0743 | The tin shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new tin shingle roof and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #114 WAREHOUSE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 3200 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 38400
0424SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0424 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0743EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0743 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #114 WAREHOUSE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 3200 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 64000
0745EXT3 | EXTERIOR FINISHES | 0745 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 6015
0450EXT1 | ROOF REPLACEMENT | 0450 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #028 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3523 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 52845
0452EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0452 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #030 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2569 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 51380
0452EXT1 | ROOF REPLACEMENT | 0452 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #030 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2569 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 38535
0440ENR2 | HVAC SYSTEM UPGRADE | 0440 | The HVAC system consists of two natural gas-fired boilers that were installed in 2000 and three large air handlers that are original to the building. There is no central cooling in the building. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system including cooling equipment and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 557250
0440EXT1 | ROOF REPLACEMENT | 0440 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445800
0440EXT2 | EXTERIOR FINISHES | 0440 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the open faced downspouts and other painted finishes and caulking of the pre-cast stone panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 185750
0440INT1 | INTERIOR FINISHES | 0440 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 185750
0440SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0440 | The building is partially a B occupancy per the 2012 IBC and is over 12,000 square feet in area. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 520100
0730EXT2 | CONSERVE AND PROTECT VACANT BUILDINGS | 0730 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #048 NDOC STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1920 | 4070 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 81400
0730EXT1 | ROOF REPLACEMENT | 0730 | The wood shingle roof on this building was in poor condition at the time of the survey and is at the point of failure. It is recommended that this building be re-roofed immediately with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #048 NDOC STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1920 | 4070 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 61050
0428EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0428 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #120 PUMP HOUSE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 220 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
0424INT1 | INTERIOR FINISHES | 0424 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11110
0746INT2 | FLOORING REPLACEMENT | 0746 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9584
0422EXT1 | EXTERIOR FINISHES | 0422 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93725
0746EXT4 | EXTERIOR DOOR REPLACEMENT | 0746 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new wood doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0454ENV1 | ASBESTOS ABATEMENT, TSI | 0454 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0735PLM1 | WATER HEATER REPLACEMENT | 0735 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0744PLM1 | WATER HEATER REPLACEMENT | 0744 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0745PLM1 | WATER HEATER REPLACEMENT | 0745 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0746PLM1 | WATER HEATER REPLACEMENT | 0746 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0747PLM1 | WATER HEATER REPLACEMENT | 0747 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0736ENV1 | ASBESTOS ABATEMENT, TSI | 0736 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97240
0735ENV1 | ASBESTOS ABATEMENT, TSI | 0735 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42040
0734ENV1 | ASBESTOS ABATEMENT, TSI | 0734 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32600
0732ENV1 | ASBESTOS ABATEMENT, TSI | 0732 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34920
0744INT2 | FLOORING REPLACEMENT | 0744 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9584
0425SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0425 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #011 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 1182 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 23640
0440SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0440 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 18575
0455ENV1 | ASBESTOS ABATEMENT, TSI | 0455 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34580
0727ENV1 | ASBESTOS ABATEMENT, TSI | 0727 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0422INT1 | INTERIOR FINISHES | 0422 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93725
0421SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0421 | The concrete exterior stairs at the entry are lacking handrails as required in the 2012 IBC Chapter 10, Section 1012. This project would provide for tubular steel framed handrails to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #004 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 662 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 5000
0420INT1 | INTERIOR FINISHES | 0420 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29585
0420SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0420 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 14792
0420PLM1 | WATER HEATER REPLACEMENT | 0420 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0420ADA2 | ADA ENTRANCE UPGRADES | 0420 | This facility has an ADA accessible ramp located on the east side of the building and stairs to approach the entrance. The ramp and stairs are on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have proper landings or handrails and the stairs do not comply with Chapter 10 of the 2012 IBC. The ramp and stairs should be scheduled for replacement. This project would provide for installing a code compliant path of travel to the entrance of the building including replacing the stairs and ADA ramp. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 75000
0420ADA1 | ADA RESTROOM REMODEL | 0420 | The building does not have an accessible restroom. The existing Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 56000
0420SFT4 | FIRE ALARM SYSTEM INSTALLATION | 0420 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 23668
0420SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0420 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 82838
0731ENV1 | ASBESTOS ABATEMENT, TSI | 0731 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Thermal System Insulation was found on the piping and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
9971PLM1 | WATER SYSTEM IMPROVEMENTS | 9971 | The water system currently consists of a combination of well water, spring water from Clear Creek and Carson City Public Works potable water. It is distributed throughout the campus in 60-75 year old asbestos concrete pipe. The connection to the city water is not physically on the Stewart campus and does not have backflow prevention. This project recommends improvements to the system to provide a sustainable long term potable water supply and adequate water volume and pressure for fire hydrants and fire protection systems in the buildings. Included in the estimate is installing new PVC piping to extend the city water main to the campus and replacing the existing water distribution pipe throughout the campus with PVC pipe. Miscellaneous items are also included such as Carson City connection fees, valves, meters, fire hydrants, decommissioning the water treatment plant and backflow prevention for the new city connection and all active service connections. Details of the plan by Buildings and Grounds are outlined in the "Proposed Water Supply Plan" report prepared by Farr West Engineering. This project or a portion there of was previously recommended in the FCA report dated 10/3/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 4/3/2013. | STEWART CAMPUS SITE | 9971 | Admin | PubWorks | B&G | Stewart | 1890 |  | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000000
0450EXT2 | CONSERVE AND PROTECT VACANT BUILDINGS | 0450 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #028 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3523 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 70460
0745INT2 | FLOORING REPLACEMENT | 0745 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9624
0440ADA4 | ADA SIGNAGE | 0440 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2250
2160EXT1 | ROOF REPLACEMENT | 2160 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 10/01/2001 and 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #070 BARN (B&G STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1910 | 2160 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 25920
2162EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 2162 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 10/01/2001 and 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #102 INFIRMARY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1904 | 3000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 60000
2162EXT1 | ROOF REPLACEMENT | 2162 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey with active leaks and animals living inside. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 10/01/2001 and 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #102 INFIRMARY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1904 | 3000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 36000
0422ADA4 | ADA SIGNAGE | 0422 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2250
0436SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0436 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #014 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1430 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 28600
0451EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0451 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #029 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3231 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 64620
0451EXT1 | ROOF REPLACEMENT | 0451 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #029 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 3231 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 48465
0687SFT1 | FIRE ALARM SYSTEM UPGRADE | 0687 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 58288
0440SFT1 | FIRE ALARM SYSTEM UPGRADE | 0440 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 148600
9971SIT6 | WELL EVALUATION OR ABANDONMENT | 9971 | There are five wells at the site. None of them have permits as required under NRS 534 of the Division of Water Resources. An application was made in 1982 for the wells, but they were withdrawn in 1984 following protests by the Washoe Tribe and Carson City. The costs to cap the wells depend on the depth of the wells and the casing size. Preliminary estimates run around $40.00 to $50.00 per foot to cap the wells, with a 75 foot minimum charge. No records for the original drillings have been located, and the actual depth of the wells is not known. DWR notes that surrounding wells are typically 100 to 120 feet deep. This report recommends an evaluation of the wells and whether any or all of them could be returned to service. Costs for an evaluation are similar to capping costs, are have been developed to cover either contingency. Well permits would be in addition to stated costs and are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 10/3/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 4/3/2013. | STEWART CAMPUS SITE | 9971 | Admin | PubWorks | B&G | Stewart | 1890 |  | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 25000
0440HVA1 | EXHAUST FAN REPLACEMENT | 0440 | Many of the exhaust fans in the restrooms and shower areas were inoperative and should be scheduled for replacement. Due to excessive humidity concerns, high volume commercial units should be installed. Additionally, the gymnasium's exhaust fans are inoperative and should be replaced with new ones. It is recommended that this project coincide with the HVAC replacement project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0736SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0736 | The building is a R-1 occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 68068
0737SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0737 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 18324
0737EXT2 | STAIR REPLACEMENT | 0737 | There is a set of wood stairs that accesses the north side of the building that serve as a means of egress. They are in poor condition and do not meet current codes. Also, the guardrail on the exterior deck area is missing and / or not to code. This project would provide for the removal of the existing stairs and installation of a new set of wood stairs which comply with Chapter 10 of the 2012 IBC and a wood framed guardrail along the deck area. A 3'x3' concrete landing at the bottom of the stairs is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 7500
0727SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0727 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2600
0422SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0422 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 9372
0455ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 0455 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing entrance. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0747EXT4 | EXTERIOR DOOR REPLACEMENT | 0747 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new wood doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0686SFT1 | FIRE ALARM SYSTEM UPGRADE | 0686 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 58288
0686INT2 | RESTROOM REMODEL | 0686 | The two large restrooms in the dormitory have not been remodeled for at least 20 years and are in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0422ADA1 | ADA RESTROOM UPGRADE | 0422 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 100000
0687ADA1 | ADA RESTROOM UPGRADE | 0687 | The designated unisex ADA accessible restrooms are not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, one of the flush handles is on the wrong side and the grab bars are not compliant. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0430EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0430 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #045 BAND ROOM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 2373 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 47460
0727EXT1 | ROOF REPLACEMENT | 0727 | The existing roof is a tin style shingle in poor condition. This project would provide for the removal of the existing roofing system and installation of a new asphalt composition roofing system. The new roof shall match the other newly installed composition roofs on the site. This project or a portion there of was previously recommended in the FCA report dated 10/3/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/6/2006. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 9750
2157EXT1 | EXTERIOR FINISHES | 2157 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #161 WATER PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1978 | 938 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4690
0437SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0437 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #016 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 8416 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 168320
0725EXT1 | ROOF REPLACEMENT | 0725 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #036 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 1500 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 22500
0440ADA1 | ADA RESTROOM UPGRADE | 0440 | The Men's and Women's locker rooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's locker rooms for accessibility upgrades. These items may include new sinks, water closets, urinals, showers, partitions, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 185000
0726EXT1 | ROOF REPLACEMENT | 0726 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #037 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1956 | 1433 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 21495
0732PLM1 | WATER HEATER REPLACEMENT | 0732 | There are two 40 gallon natural gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0455SFT4 | FIRE ALARM SYSTEM INSTALLATION | 0455 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 6916
0455SFT5 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0455 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4323
0455INT2 | KITCHEN REMODEL | 0455 | Both sides of the duplex have a kitchen that is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components on both sides of the duplex. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0456EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0456 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #034 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 34580
0686ADA2 | ADA RESTROOM UPGRADE | 0686 | The designated unisex ADA accessible restrooms are not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, one of the flush handles is on the wrong side and the grab bars are not compliant. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0442EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0442 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #019 OLD POST OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 1646 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 32920
0726EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0726 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #037 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1956 | 1433 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 28660
0429SFT2 | STORAGE REMOVAL | 0429 | Staff has been using the interior of the building for storage. The interior finishes are failing including drywall and plywood falling off of the ceiling. This creates a safety hazard when people are bringing items in and out of the building. Some of the interior finishes may contain asbestos which further exacerbates the hazard. This project would provide for the removal of all storage items in the building and posting signs to ensure that nobody enters the building. | #015 KITCHEN/DINING (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 11444 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 5000
0429EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0429 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #015 KITCHEN/DINING (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 11444 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 228880
0427SFT1 | EXTERIOR CONCRETE STAIR REPLACEMENT | 0427 | The concrete stairs and porch that access the building are deteriorating. Some sections have completely failed and are a safety hazard. The rest of the concrete is spalling and cracking extensively. It appears the concrete is original to the building and should be scheduled for a complete replacement immediately. | #090 AUDITORIUM (B&G) (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 5857 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 15000
0725EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0725 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #036 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1942 | 1500 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0724EXT1 | ROOF REPLACEMENT | 0724 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #035 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1500 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 22500
0724EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0724 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #035 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1500 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0453EXT1 | ROOF REPLACEMENT | 0453 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #031 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2388 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 35820
0453EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0453 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #031 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2388 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 47760
0427EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0427 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #090 AUDITORIUM (B&G) (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 5857 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 117140
0686ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0686 | This building contains 3 water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 8000
0727EXT2 | WINDOW REPLACEMENT | 0727 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0423SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0423 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #008 DOIT STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 720 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 14400
0426EXT1 | ROOF REPLACEMENT | 0426 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new wood shingle roof and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #002 POST OFFCE (B&G STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 362 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 5430
0426SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0426 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #002 POST OFFCE (B&G STORAGE) | 9971 | Admin | PubWorks | B&G | Stewart | 1926 | 362 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 7240
0731PLM1 | WATER HEATER REPLACEMENT | 0731 | There are two natural gas-fired water heaters in the building, a 40 gallon and a 50 gallon. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #057 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 3000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0687ENR1 | WINDOW REPLACEMENT | 0687 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 70 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
0425EXT1 | ROOF REPLACEMENT | 0425 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new wood shingle roof and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #011 QUARTERS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1925 | 1182 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 17730
2157INT1 | INTERIOR FINISHES | 2157 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #161 WATER PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1978 | 938 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4690
0440ENV1 | BAT ABATEMENT | 0440 | There is a large amount of bat droppings and some dead bats in the mechanical area of the penthouse. Due to the potential risk of disease, this project provides for treatment and clean up of the bats and bat droppings by a licensed pest control business. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2500
0686EXT4 | EXTERIOR FINISHES | 0686 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 72860
0440EXT3 | STOREFRONT SYSTEM REPLACEMENT | 0440 | There are three sets of exterior aluminum entrance storefront systems that appear to be original to the building. They are damaged from age and general wear and tear and are a constant maintenance problem. This project would provide for the replacement and installation of three new exterior aluminum entrance storefront systems including ADA compliant hardware. Removal and disposal of the existing storefronts is included in this estimate. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0440EXT4 | EXTERIOR DOOR REPLACEMENT | 0440 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the 13 metal man doors with new metal doors, frames and ADA compliant hardware. Removal and disposal of the existing doors is included in this estimate. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19500
0421EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0421 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #004 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 662 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 13240
0441EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0441 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #068A & 068B SHOPS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 8588 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 171760
0422INT3 | JANITORS CLOSET REPAIRS | 0422 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitors Closets. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0439EXT1 | ROOF REPLACEMENT | 0439 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It has active leaks and is currently damaging the interior of the building. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #020 OLD GYM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 11933 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 143196
0440PLM1 | WATER HEATER REPLACEMENT | 0440 | There is a 100 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0440ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0440 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2000
0429ENV1 | ASBESTOS ABATEMENT, TSI | 0429 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Piping insulation was found which is believed to contain asbestos, and this report recommends abatement of this material. This project or a portion there of was previously recommended in the FCA report dated 10/1/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/6/2006. | #015 KITCHEN/DINING (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 11444 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 228880
0440ADA5 | ADA DOOR HARDWARE | 0440 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. | #160 NEW GYM | 9971 | Admin | PubWorks | B&G | Stewart | 1973 | 37150 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 31500
0422PLM1 | WATER HEATER REPLACEMENT | 0422 | There is a 68 gallon natural gas-fired water heater in the building that was installed in 1997. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0443EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0443 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #021 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 8662 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 173240
0444EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0444 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #022 DMV&PS STORAGE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 127920
0445EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0445 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #023 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 127920
0446EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0446 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. | #024 DORMITORY (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 6395 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 127920
0449EXT2 | CONSERVE AND PROTECT VACANT BUILDING | 0449 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #027 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2254 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 45080
0423EXT1 | ROOF REPLACEMENT | 0423 | The tin shingle roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new tin shingle roof and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #008 DOIT STORAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 720 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 10800
0422ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0422 | This building contains three water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of six drinking fountains at three different locations to meet the ADA requirements. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 6000
0686ADA4 | ADA SIGNAGE | 0686 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 1500
0686INT3 | JANITORS CLOSET REPAIRS | 0686 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitors Closets. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0686SFT3 | EGRESS LIGHTING UPGRADE | 0686 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and providing additional lights on the main exit routes and in individual rooms as needed. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2700
0686HVA1 | EXHAUST FAN INSTALLATION | 0686 | There are two rooms in the building with laundry facilities. These rooms are not equipped with any type of exhaust system to ventilate the rooms. When the laundry machines are running, heat and moisture build up in the rooms and the occupants prop open the fire rated doors. This compromises the fire safety design for the building. This project would provide for the purchase and installation of exhaust fan assemblies in each room including connections to utilities. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0686PLM1 | WATER HEATER REPLACEMENT | 0686 | There are two 100 gallon gas-fired water heaters in the building that were installed in 1993. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0687EXT3 | EXTERIOR FINISHES | 0687 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 72860
0686EXT1 | WINDOW REPLACEMENT | 0686 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 70 units including wooden frames and additional costs are included due to the historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
0687INT2 | CARPET REPLACEMENT | 0687 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0422SFT3 | CONCRETE STAIR REPLACEMENT | 0422 | The concrete stairs that access the building are not code compliant and many areas of the concrete are spalling and cracking. It appears these stairs are original to the building and should be scheduled for replacement. This project would provide for removal and disposal of the existing concrete stairs and handrails and installation of new compliant stairs and handrails. The estimate is for the replacement of 5 separate stairs. 2012 IBC Chapter 10 was used as a reference for this project. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0441EXT1 | ROOF REPLACEMENT | 0441 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It has active leaks and is currently damaging the interior of the building. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #068A & 068B SHOPS (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 8588 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 103056
0422INT2 | ADA KITCHEN REMODEL | 0422 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0449EXT1 | ROOF REPLACEMENT | 0449 | The transite shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and additional costs have been added for the abatement of asbestos containing materials. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #027 WASHOE TRIBE (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2254 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 33810
0420EXT3 | WINDOW REPLACEMENT | 0420 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 44 units including wooden frames to match the historical style of the building. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
0747INT1 | INTERIOR FINISHES | 0747 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6015
0424INT2 | FLOORING REPLACEMENT | 0424 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17776
0424EXT3 | EXTERIOR DOOR REPLACEMENT | 0424 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0424ENR1 | WINDOW REPLACEMENT | 0424 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units including wooden frames to match the historical style of the building. Removal and disposal of the existing windows is included in this estimate. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0424SIT1 | DRIVEWAY INSTALLATION | 0424 | The driveway is used every day by the resident and is currently not paved. This project would provide for the installation of a new 4" thick concrete slab-on-grade driveway approximately 40'x20' in size. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0424EXT2 | EXTERIOR FINISHES | 0424 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #009 RESIDENCE (POST) | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2222 | 2013-04-03 | Four to Ten Years | Long-Term Needs | 3 | 11110
0439SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0439 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #020 OLD GYM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1938 | 11933 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 238660
0422ADA2 | ADA RAMP REPLACEMENT | 0422 | This facility has ADA accessible ramps located on the east side and the west side of the building. These ramps are on the accessible path of travel from the accessible parking spaces to the front and rear entrances of the building. The ramps do not have proper landings or handrails. This project would provide for removing and replacing both ramps to provide fully ADA compliant access to the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #006 ADMINISTRATION (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 18743 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 70000
0736SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0736 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0454INT1 | INTERIOR FINISHES | 0454 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0735SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0735 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
2702EXT1 | EXTERIOR FINISHES | 2702 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the concrete roof eaves and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 GARAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1964 | 676 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3380
2703INT1 | INTERIOR FINISHES | 2703 | The interior finishes are in fair condition. It is recommended that the interior CMU walls be sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #089 UTILITY ROOM | 9971 | Admin | PubWorks | B&G | Stewart | 2000 | 120 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
2704EXT1 | EXTERIOR FINISHES | 2704 | It is important to maintain the finish, weather resistance and appearance of the water tower. This project would provide for the painting of the water tower and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #087 WATER TOWER | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 900 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0727INT1 | INTERIOR FINISHES | 0727 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3250
0687INT1 | INTERIOR FINISHES | 0687 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 72860
0419INT2 | BASEMENT CLEAN-UP | 0419 | The building contains a daylight basement area in which debris is scattered all around the floor area. This project would provide for a one time clean-up and disposal of the miscellaneous debris and unused items located in the basement area. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 500
0420EXT4 | OVERHEAD DOOR REPLACEMENT | 0420 | The existing 12'x7' overhead garage door in the daylight basement is worn from age and exposure to the elements. This project would provide for the removal and replacement of the wood, raised panel overhead door assembly including hardware and wood trim/ jamb repair. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #003 STEWART INDIAN MUSEUM | 9971 | Admin | PubWorks | B&G | Stewart | 1930 | 5917 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0419ENR1 | WINDOW RETROFIT | 0419 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient, at least one pane is broken and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 42 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63000
0686INT1 | INTERIOR FINISHES | 0686 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 72860
0686SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0686 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #012 DORMITORY (P.O.S.T.) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0455SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0455 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0455EXT1 | EXTERIOR FINISHES | 0455 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8645
0455INT1 | INTERIOR FINISHES | 0455 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #033 NON-PROFIT HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1729 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8645
0454SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0454 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0454EXT1 | EXTERIOR FINISHES | 0454 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #032 NON-PROFIT OFFICE | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 1800 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0687SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0687 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #013 DORM (DMV&PS) | 9971 | Admin | PubWorks | B&G | Stewart | 1941 | 14572 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
2702INT1 | INTERIOR FINISHES | 2702 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 GARAGE | 9971 | Admin | PubWorks | B&G | Stewart | 1964 | 676 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3380
0736EXT1 | EXTERIOR FINISHES | 0736 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24310
0736INT1 | INTERIOR FINISHES | 0736 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #067 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 4862 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24310
0735EXT1 | EXTERIOR FINISHES | 0735 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10510
0735INT1 | INTERIOR FINISHES | 0735 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #065 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 2102 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10510
0734INT1 | INTERIOR FINISHES | 0734 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8150
0419INT1 | INTERIOR FINISHES | 0419 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28010
0419ADA2 | ADA HANDRAIL INSTALLATION | 0419 | The existing concrete ramp at the east side of the building provides an accessible route of travel from the parking lot to the building entrance. The slope of the sidewalk exceeds 5% and is missing handrails. This project would provide for the installation of 1-1/2 inch diameter steel pipe handrails at the ramp as required in Chapter 10 of the 2012 IBC. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 10000
0733EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 0733 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #061 (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1949 | 1630 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8150
0737EXT4 | LOADING DOCK UPGRADES | 0737 | The existing concrete loading dock on the south side of the building is showing signs of damage due to age and weather exposure. The concrete stairs are also damaged and are lacking handrails. This project would provide for an exterior epoxy based concrete repair product to be installed over the spalled and damaged concrete including the stairs. Tube steel handrails for the stairs are also included. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0732EXT1 | EXTERIOR FINISHES | 0732 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8730
0732INT1 | INTERIOR FINISHES | 0732 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #060 NON-PROFIT | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 1746 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8730
0727EXT4 | EXTERIOR FINISHES | 0727 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #044 CAPITOL POLICE SUBSTATION | 9971 | Admin | PubWorks | B&G | Stewart | 1937 | 650 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3250
0419SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0419 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 78428
0419SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0419 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 14005
0419SFT4 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0419 | The existing concrete stairs which provide access to the rear building entrance are missing handrails. The concrete exterior stairs at the entry are lacking a handrail as required in the 2012 IBC Chapter 10, Section 1012. This project would provide for a tubular steel framed handrail to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 5000
0419SFT5 | FIRE ALARM SYSTEM INSTALLATION | 0419 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #001 STEWART MUSEUM (VACANT) | 9971 | Admin | PubWorks | B&G | Stewart | 1923 | 5602 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 22408
0734SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0734 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #062 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1960 | 1630 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0738SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0738 | In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to removing water in the basement, providing drainage away from the building to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76500
0737ELE2 | ELECTRICAL UPGRADE | 0737 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are more than 30 years old, the fuses burn out often and it is difficult to find the correct replacement fuses. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #084 B&G SHOP | 9971 | Admin | PubWorks | B&G | Stewart | 1931 | 4581 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 91620
0747SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0747 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #119 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0744SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0744 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0746INT1 | INTERIOR FINISHES | 0746 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5990
2703EXT0 | EXTERIOR FINISHES | 2703 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the wood finishes, cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #089 UTILITY ROOM | 9971 | Admin | PubWorks | B&G | Stewart | 2000 | 120 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0738INT1 | REMOVE AND SALVAGE EXISTING EQUIPMENT | 0738 | The existing equipment in this building has been abandoned and is no longer required nor in use. There are 4 boilers, holding tanks, piping and ancillary equipment inside that should be removed to allow for a different and efficient use of this facility. Some of the piping contains asbestos insulation based on a previous environmental report conducted in 1989. This project would provide for the removal, disposal and / or salvaging of the equipment currently inside of the building including asbestos removal. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0738EXT1 | ROOF REPLACEMENT | 0738 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #092 CENTRAL HEAT PLANT | 9971 | Admin | PubWorks | B&G | Stewart | 1924 | 3825 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45900
0741INT1 | INTERIOR FINISHES | 0741 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0745INT1 | INTERIOR FINISHES | 0745 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6015
0744INT1 | INTERIOR FINISHES | 0744 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #116 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5990
0741EXT1 | EXTERIOR FINISHES | 0741 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0745SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0745 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #117 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1203 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0741SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0741 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #110 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1939 | 2000 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0746SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0746 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 09/14/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #118 HOUSING | 9971 | Admin | PubWorks | B&G | Stewart | 1963 | 1198 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0438SFT5 | ADA ACCESSIBLE PATH OF TRAVEL | 0438 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office entrance are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the entrance. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0438EXT2 | EXTERIOR FINISHES | 0438 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18500
0438INT1 | INTERIOR FINISHES | 0438 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18500
0438SFT4 | FIRE ALARM SYSTEM UPGRADE | 0438 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 14800
0433EXT1 | EXTERIOR FINISHES | 0433 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete walls, cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #017 SCHOOL (NDOC) | 9971 | Correct | B&G |  | Stewart | 1964 | 41826 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 209130
0433INT1 | INTERIOR FINISHES | 0433 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #017 SCHOOL (NDOC) | 9971 | Correct | B&G |  | Stewart | 1964 | 41826 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 209130
0431EXT2 | EXTERIOR FINISHES | 0431 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 87725
0431INT1 | INTERIOR FINISHES | 0431 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 87725
0431SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0431 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 245630
0431SFT5 | CONCRETE STAIRS REPLACEMENT | 0431 | The concrete stairs that access the building and the wood stairs in the courtyard are not code compliant and many areas of the concrete are spalling and cracking. It appears these stairs are original to the building and should be scheduled for replacement. This project would provide for removal and disposal of the existing concrete and wood stairs and handrails and installation of new compliant stairs and handrails. The estimate is for the replacement of 6 separate stairs. 2012 IBC Chapter 10 was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0438SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0438 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 37000
0431SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0431 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 8773
0431SFT1 | FIRE ALARM SYSTEM UPGRADE | 0431 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 70180
0438ENR2 | HVAC EQUIPMENT REPLACEMENT | 0438 | The HVAC system was has not been upgraded since the 1980's. It consists of two natural gas-fired furnaces and two outdoor condensers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55500
0438SFT1 | EXIT SIGN & EGRESS LIGHTING | 0438 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 9250
0431INT3 | RESTROOM REMODELS | 0431 | The large Men's and Women's restrooms are in overall poor condition and should be scheduled for a remodel. The finishes, fixtures, partitions, water closets, urinals and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0431SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0431 | The building has some damage to the stone exterior from lawn sprinklers wetting the walls. The water has stained the stone and caused premature cracking to the mortar. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0433INT2 | CARPET REPLACEMENT | 0433 | The carpet in the building is showing signs of wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 3-4 years. | #017 SCHOOL (NDOC) | 9971 | Correct | B&G |  | Stewart | 1964 | 41826 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 210000
0438ADA1 | ADA RESTROOM UPGRADE | 0438 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA reports dated 10/1/2001 and 9/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 30000
0433PLM1 | WATER HEATER REPLACEMENT | 0433 | There is a 50 gallon gas-fired water heater in the building that was installed in 2001. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #017 SCHOOL (NDOC) | 9971 | Correct | B&G |  | Stewart | 1964 | 41826 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0438ENR3 | WINDOW REPLACEMENT | 0438 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 22 units. Removal and disposal of the existing windows is included in this estimate. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16500
0438ADA2 | ADA ENTRANCE UPGRADES | 0438 | The existing exterior entrance door and threshold to the Office is not accessible. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2500
0438INT2 | INTERIOR DOOR REPLACEMENT | 0438 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 6 interior doors was used in this estimate. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0438PLM1 | WATER HEATER REPLACEMENT | 0438 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #018 OFFICE (NDOC) | 9971 | Correct | B&G |  | Stewart | 1936 | 3700 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0431ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0431 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0431ADA3 | BREAK ROOM REMODEL | 0431 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2000
0431ADA2 | ADA RESTROOM REMODEL | 0431 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, and the flush handle is on the wrong side. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #089 ADMINISTRATION (NDOC) | 9971 | Correct | B&G |  | Stewart | 1931 | 17545 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2000
0989SIT1 | DRAINAGE UPGRADES | 0989 | The building has a drainage problem near the Traffic Safety entrance where grade does not properly slope away from the building. The rain accumulates in several areas adjacent to the building, creating a water problem which may infiltrate the interior during inclement weather. This project would create positive flow away from the building by regrading, paving and installing additional drainage swales as needed. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0989EXT3 | GUTTER INSTALLATION | 0989 | The building does not have continuous gutters to control the runoff from the roof. The existing gutters and downspouts are only installed at exits. The water currently sheet drains off the roof causing extensive erosion to the built-up dirt slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0989ENR2 | WINDOW REPLACEMENT | 0989 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 67 units. Removal and disposal of the existing windows is included in this estimate. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50250
0989ADA3 | ADA RESTROOM UPGRADE | 0989 | The designated Men's and Women's ADA accessible restrooms are not fully compliant. The flush handle is on the wrong side, the toilet paper dispenser is not in the correct location, and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0989ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0989 | This building contains several water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of 6 drinking fountains to meet the ADA requirements. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 12000
0989INT2 | JANITORS CLOSET REPAIRS | 0989 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of 2 Janitors Closets. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0989SFT5 | WATER HEATER SEISMIC BRACING | 0989 | The water heater is not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 100
0989ADA5 | ADA ACCESSIBLE COUNTER | 0989 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The entrance to the Traffic Safety Office and the Investigations Office have service counters for the public to approach which do not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement for each office. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 2000
0989SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0989 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 16416
0989HVA2 | EXHAUST FAN REPLACEMENT | 0989 | The existing exhaust fans that serve the restrooms are original equipment and are not providing adequate ventilation. Some of them were inoperable at the time of the survey. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 10/01/2001 and 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0989EXT1 | EXTERIOR FINISHES | 0989 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and wood, sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 164160
0989PLM1 | WATER HEATER REPLACEMENT | 0989 | There is a 125 gallon gas-fired water heater in the building that was installed in 1987. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 3500
0989INT1 | INTERIOR FINISHES | 0989 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 98496
0989EXT2 | ROOF REPLACEMENT | 0989 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project is in design under CIP 13-S01 (5) and is scheduled for replacement in early 2014. This project or a portion thereof was previously recommended in the FCA report dated 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 394344
0989ADA1 | ADA SIGNAGE | 0989 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/01/2001 and 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 6000
0989SFT1 | FIRE ALARM SYSTEM UPGRADE | 0989 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA reports dated 10/01/2001 and 09/06/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/03/2013. | #107 STATE FIRE MARSHAL | 9971 | PubSafe | FireMars |  | Stewart | 1963 | 32832 | 2013-04-03 | Immediate to Two Years | Currently Critical | 1 | 131328
2138INT3 | INTERIOR REMODEL | 2138 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2138INT2 | DOOR HARDWARE REPLACEMENT | 2138 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2138EXT4 | EXTERIOR DOOR REPLACEMENT | 2138 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2138EXT3 | WOOD SKIRTING REPLACEMENT | 2138 | The skirting on the modular building is made of T1-11 and was in poor condition at the time of the survey. International Building Code (IBC) 2012, section 2304.11.2.6, wood siding clearance between wood siding and earth on the exterior of a building shall not be less than 6 inches (152 mm) or less than 2 inches (51mm) vertical from concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood. This project would provide for the removal of the T1-11 skirting and the installation of new vinyl skirting. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2138EXT1 | EXTERIOR FINISHES | 2138 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2139INT1 | INTERIOR FINISHES | 2139 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | METAL STORAGE SHED | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 192 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2140INT1 | INTERIOR FINISHES | 2140 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2610
2141INT2 | DOOR HARDWARE REPLACEMENT | 2141 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
1399SFT3 | OSHA COMPLIANT LADDER | 1399 | The ladder in the mezzanine was constructed in-house and does not comply with OSHA guidelines. This project recommends an Occupational Safety and Health Administration (OSHA) compliant ladder per OSHA 1926.1053 for the interior mezzanine storage area of the building. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 800
1399ADA1 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1399 | The stairs and handrails between the first floor and the mezzanine do not meet the requirements in the 2012 International Building Code (IBC) sections 1009 and 1012. This project would provide funding to remove and replace the stairway and handrail and replace with new stairs and handrails. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 9000
2139EXT1 | EXTERIOR FINISHES | 2139 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | METAL STORAGE SHED | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 192 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 384
1605INT3 | INTERIOR FINISHES | 1605 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1605EXT1 | EXTERIOR FINISHES | 1605 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2138INT0 | LIGHTING UPGRADE | 2138 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
2138HVA1 | HEATER REPLACEMENT | 2138 | The existing heating system consists of a wall mounted electric/propane heater and it does not have cooling equipment. The heater is inefficient and should be replaced with a propane fired heater 80% AFUE or higher unit. This project would replace the existing heater. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1605SFT5 | DOOR HARDWARE REPLACEMENT | 1605 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
1605SFT4 | EXIT SIGN UPGRADE | 1605 | The existing exit signs in this building are outdated and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. International Building Code (IBC) 2012 chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 1800
2140INT2 | DOOR HARDWARE REPLACEMENT | 2140 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2140EXT3 | WOOD SKIRTING REPLACEMENT | 2140 | The skirting on the modular building is made of T1-11 and was in poor condition at the time of the survey. International Building Code (IBC) 2012, section 2304.11.2.6, wood siding clearance between wood siding and earth on the exterior of a building shall not be less than 6 inches (152 mm) or less than 2 inches (51mm) vertical from concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood. This project would provide for the removal of the T1-11 skirting and the installation of new vinyl skirting. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2138EXT2 | ROOF REPLACEMENT | 2138 | The metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
2143EXT1 | EXTERIOR FINISHES | 2143 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal siding and caulking the flashing, fixtures and all other penetrations. It is recommended to paint the building within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 960
1399SFT8 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 1399 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. International Building Code (IBC) 2012 chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2400
1399HVA8 | HEATER REPLACEMENT | 1399 | The existing heating system consists of a ceiling mounted propane heater (30,000 - 50,000 BTU) and does not have cooling equipment. The heater is inefficient and should be replaced with a propane fired heater 80% AFUE or higher unit. This project would provide for disposal of the existing unit and replacement with a new propane fired unit including connections to utilities. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2143INT3 | INTERIOR FINISHES | 2143 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 960
2143ENR1 | EXPLOSION PROOF INTERIOR LED LIGHTING | 2143 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with longer life cycles and will be explosion proof. 4' LEDs in class 1 explosion proof fixtures are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2140ENR2 | EXPLOSION PROOF INTERIOR LED LIGHTING | 2140 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with a longer life cycle and will be explosion proof. 4' LEDs with a class 1 explosion proof are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
1399ADA7 | ADA RESTROOM UPGRADE | 1399 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restroom into an ADA compliant restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 40000
1399EXT1 | EXTERIOR FINISHES | 1399 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 1920
2140EXT1 | EXTERIOR FINISHES | 2140 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2610
2139EXT2 | CONCRETE FOUNDATION | 2139 | The Metal Storage Shed floor is made of plywood and was in poor condition at the time of the survey. This project would provide for the removal of the plywood flooring, metal shed walls, and roofing, and additionally for the installation of a stem wall, 4" thick concrete floor and an apron in front of the building. The Metal Storage Shed walls and roof would need to be anchored to the stem wall per the engineer’s or architect’s design. Additionally, this project would require a plan review and permit from State Public Works Division. | METAL STORAGE SHED | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 192 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
1399INT1 | INTERIOR FINISHES | 1399 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
1399PLM1 | WATER HEATER REPLACEMENT | 1399 | There is an electric water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was not working at the time of the survey. It is recommended that a new electric water heater, seismic straps, braided steel hoses, expansion tank, ball valve, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2200
1399EXT3 | OVERHEAD DOOR REPLACEMENT | 1399 | There is a 16'x14' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1399SFT4 | DOOR HARDWARE REPLACEMENT | 1399 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2141INT1 | INTERIOR FINISHES | 2141 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2141EXT0 | EXTERIOR FINISHES | 2141 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2142EXT3 | ROOF REPLACEMENT | 2142 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old asphalt composition shingle roof. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1176
2142EXT2 | EXTERIOR FINISHES | 2142 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 980
2142INT1 | INTERIOR FINISHES | 2142 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 980
1399ELE8 | ELECTRICAL OUTLET REPAIR | 1399 | The building has several interior and exterior electrical outlets which are damaged. Some outlets appear to have shorted out or have arced, leaving burn marks on them. Others are missing safety covers. These problems pose the risk of fire and injury. This project would provide for repair and/or replacement of the damaged electrical outlets. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 600
2147EXT1 | EXTERIOR FINISHES | 2147 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF COMPRESSOR BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 112 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
1605HVA2 | HEATER REPLACEMENT | 1605 | The garage part of the building is heated by two ceiling mounted propane-fired heating units. They are original to the building and one of the units was not working at the time of the survey. They have both reached the end of their useful life. This project provides for the disposal of the existing units and replacement with two new propane-fired units including connections to utilities. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
2140SFT3 | HAZARDOUS MATERIALS STORAGE | 2140 | The Hazardous Material Storage Building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per International Fire Code (IFC) 2012 Hazardous Materials, and in accordance with National Fire Protection Association (NFPA); where hazardous materials are stored, dispensed or used, section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | OFFICE TRAILER | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 261 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
2142SFT2 | HAZARDOUS MATERIALS STORAGE | 2142 | The Fuel Island Building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per International Fire Code (IFC) 2012 Hazardous Materials, and in accordance with National Fire Protection Association (NFPA); where hazardous materials are stored, dispensed or used, section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
2143SFT4 | HAZARDOUS MATERIALS STORAGE | 2143 | The Hazardous Material Storage Building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per International Fire Code (IFC) 2012 Hazardous Materials, and in accordance with National Fire Protection Association (NFPA); where hazardous materials are stored, dispensed or used, section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
1399STR6 | STRUCTURAL REPAIRS | 1399 | A storage area has been constructed in the Maintenance Shop, accessed via stairs. There is no record of a Capital Improvement Project (CIP) for this work or of any structural evaluations having been conducted. This project recommends adding structural members to the existing framing to ensure proper load bearing capacity. This will require a structural design from a licensed engineer, inspections and permitting which are not included in the estimate. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 8000
1605PLM4 | WATER HEATER REPLACEMENT | 1605 | There is a 40 gallon electric water heater in the building that was installed in 2011. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2143HVA1 | EXHAUST FAN INSTALLATION | 2143 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HAZARDOUS MATERIAL STORAGE BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 96 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1605ELE1 | LIGHTING UPGRADE | 1605 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
1605ADA1 | ADA RESTROOM UPGRADE | 1605 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. The project should be implemented concurrently with the Shower Installation project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 14000
1605ADA2 | ADA SIGNAGE | 1605 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3000
2138SIT1 | STAIRWAY REPAIRS | 2138 | The 2012 International Building Code (IBC) section 1009.11 requires handrails to be installed on stairs with two or more risers. There are two stairways that provide access to the saw shop. They do not have any handrails. This project would provide for the repair of the existing stairs and installation of handrails on each side of the stairways. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | SAW SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 480 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1605INT1 | ADA SHOWER INSTALLATION | 1605 | The Nevada Division of Forestry (NDF) uses large quantities of herbicides, chemicals and also provides fire fighting services. After spraying chemicals, there is no shower for NDF employees to wash off these chemicals and no place to clean up after fighting a fire. This project would provide funding for the installation of an accessible unisex shower. Cost includes plumbing, fiberglass shower stall, exhaust fan, gypsum board, and needed electrical. The final design may impact these costs and are not included in this estimate. This project should coincide with the ADA Restroom Upgrade project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 7500
1605SFT0 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1605 | The building is a B occupancy per the 2012 International Building Code (IBC). Pursuant to the Nevada State Fire Marshal Regulation, Nevada Administrative Code (NAC) 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project also includes an allowance for 100 lineal feet of 4" water line, excavation and backfill, all fittings and an above ground backflow prevention device. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 50000
1605ADA4 | ADA UPGRADES | 1605 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 7000
2147ELE1 | GFCI OUTLETS | 2147 | The existing receptacles in the compressor room and outside are standard duplex receptacles. The 2011 National Electrical Code (NEC) 210.8 requires these locations to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF COMPRESSOR BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 112 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 800
2142EXT1 | EXTERIOR SIDING REPLACEMENT | 2142 | The wood siding has some areas that are damaged from exposure to the elements and should be replaced. This project would provide for the removal and replacement of damaged siding and trim including caulking and painting to match existing conditions. | FUEL ISLAND BUILDING | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 98 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2450
2141SFT1 | SAFETY CABINETS | 2141 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or International Fire Code (IFC) for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with Occupational Safety and Health Administration (OSHA) 1910.106 (d) and IFC chapter 57 section 5704.3.2.1.3. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MECHANICAL SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1988 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 10000
1605ADA5 | ADA ACCESSIBLE COUNTER | 1605 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF ADMINISTRATION OFFICE | 9972 | CNR | Forestry |  | Winnemucca | 1986 | 1800 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1399SFT2 | EMERGENCY EYE WASH STATION | 1399 | The building has outdated containers of eye wash solution. Where the eyes or body of any person may be exposed to injurious corrosive materials, suitable facilities for quick drenching or flushing of the eyes and body shall be provided within the work area for immediate emergency use, Occupational Safety and Health Administration (OSHA) 1910.151(c). This project would provide funding for the purchase and the installation of an emergency eye and body wash station. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | NDF MAINTENANCE SHOP | 9972 | CNR | Forestry |  | Winnemucca | 1987 | 960 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3500
1394SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1394 | This building does not have an automatic fire suppression system. This building has more than 12,000 square feet on the first floor. Current state regulations require state-owned buildings having more than 12,000 square feet on one floor, or more than 24,000 square feet total, must be retrofitted with fire sprinklers during the next remodel or addition. Also, this building is equipped with an automatic fire detection and alarm system. This project would provide funding for the installation of fire sprinklers, including backflow prevention devices, and a visual/audible alarm notification, in accordance with ADA requirements. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 174692
9972SIT4 | SITE DRAINAGE UPGRADES | 9972 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per International Building Code (IBC) 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9972SEC0 | FENCE UPGRADE | 9972 | The chain link perimeter fence is currently 7’ high. For security purposes the staff has requested repairs to the bottom tension wire to prevent inmates from bending the fence up and crawling underneath. This project will provide for 2000’ of new tension wire that will be installed at the bottom of the existing perimeter fence. It will also provide for the removal of dirt that has built up along the fence. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 10000
9972SEC2 | EXTERIOR LIGHTING | 9972 | The entrance road, parking area and site have insufficient, poor and none functional lighting. Considering the environment of the site, this area needs to be well lit. This project will provide funding for the purchase and installation of 30 additional LED fixtures; 30’ light poles and 30" diameter raised concrete bases; electrical trenching; conduit; wiring, and required connections to the existing utilities. The light poles should match the existing light poles located in the surrounding area. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 240000
1395ADA4 | ADA TABLE UPGRADE | 1395 | Per the United States Access Board Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 section 902 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 4 of the fixed seats, which will allow access for four wheel chairs. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
9972ADA2 | ADA PARKING SPACE AND PATH OF TRAVEL | 9972 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not meet the current requirements. This project will provide funding to bring the existing ADA parking space up to code, and will include the removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. This project will also provide for the addition of a path of travel from the parking space to the gate to the visitor’s entrance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
1395SFT5 | FLUE REPLACEMENT | 1395 | There are several water heater flues in the building, which do not comply with International Mechanical Code (IMC) 2012 chapter 8, chimneys and vents. The vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. The flex ductwork is connected with metal tape and per 803.10.1 supports and joints ductwork shall be fastened with sheet metal screws, rivets or other approved means. Some of the flues are aluminum flex ducts and per 803.8 vent connector construction, vent connectors shall be constructed of metal. The minimum thickness of the connector shall be (no. 28 gage) for galvanized steel. The flues are in poor condition and have cracks. Per 801.18.2 flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that all flues throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flues should be installed by a licensed contractor. This project would provide funds to replace all the flues throughout the building. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 8000
1394SFT2 | FLUE REPLACEMENT | 1394 | There are several water heater and heater flues in the building, which do not comply with International Mechanical Code (IMC) 2012 chapter 8, chimneys and vents. The vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. The flex ductwork is connected with metal tape and per 803.10.1 supports and joints ductwork shall be fastened with sheet metal screws, rivets or other approved means. Some of the flues are aluminum flex ducts and per 803.8 vent connector construction, vent connectors shall be constructed of metal. The minimum thickness of the connector shall be (no. 28 gage) for galvanized steel. The flues are in poor condition and have cracks. Per 801.18.2 flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that all flues throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flues should be installed by a licensed contractor. This project would provide funds to replace all the flues throughout the building. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 48000
1394HVA2 | HEATER REPLACEMENT | 1394 | The heating system was installed in 1997. It consists of propane gas-fired furnaces. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of new heating systems and the cleaning of the existing duct work and grilles. The new systems shall be designed to significantly reduce electrical and propane usage in order to comply with the 2012 International Energy conservation Code (IECC) and American Society of Heating Refrigerating and Air-Conditioning Engineers (ASHRAE) 90.1 and to reduce utility costs. This project includes the removal and the disposal of the existing heating units and all required connections to utilities. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1395EXT7 | EXTERIOR SIDING REPLACEMENT | 1395 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. The estimate is based on 340 linear feet of 4' wide panels at $17.00 per linear foot. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5780
1397PLM5 | PLUMBING REPLACEMENT | 1397 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and the ABS sanitary wastewater line are off gassing in several locations due to improper repairs from inmates. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
1400EXT1 | EXTERIOR SIDING REPLACEMENT | 1400 | The Pump House has painted plywood siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the plywood siding and replacing it with T1-11 panels finished with an oil-based paint. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
1395PLM1 | WATER HEATER REPLACEMENT | 1395 | There is a 97 gallon propane water heater in the building. The average lifespan of a water heater is eight to ten years. This water heater was installed in 2013. This project would provide for a new propane water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan to be installed in the next 5-6 years. Removal and disposal of the existing equipment is also included in this estimate. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 3000
1398EXT4 | EXTERIOR DOOR REPLACEMENT | 1398 | There are two exterior doors that are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new solid core wood doors. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 2 doors. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1395INT2 | INTERIOR FINISHES | 1395 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1395EXT1 | EXTERIOR FINISHES | 1395 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
1395SFT6 | EGRESS LIGHTING INSTALLATION | 1395 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 1350
1396INT2 | INTERIOR FINISHES | 1396 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GATEHOUSE/ GUARD SHACK | 9972 | Correct | HCC |  | Winnemucca | 1987 | 36 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
1397INT5 | INTERIOR FINISHES | 1397 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1397EXT1 | EXTERIOR FINISHES | 1397 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
1397PLM2 | SEDIMENT TRAP INSTALLATION | 1397 | The gas line serving the appliances in the Multi-Purpose Building does not have sediment traps. Per International Fuel Gas Code (IFGC) 2012, section 408, where a sediment trap is not incorporated as part of the appliance, a sediment trap shall be installed downstream of the appliance shutoff valve as close to the inlet of the appliance as practical. The sediment trap shall be either; a tee fitting, having a capped nipple, of any length, installed vertically in the bottommost opening of the tee, or other device approved as an effective sediment trap. This project would provide for all labor and materials to have sediment traps installed near all gas appliances. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
1398SFT1 | EXTERIOR LANDING INSTALLATION | 1398 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing that complies with International Building Code (IBC) 2012. IBC section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1398INT1 | INTERIOR FINISHES | 1398 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1880
1398EXT3 | EXTERIOR FINISHES | 1398 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 1880
1400INT1 | INTERIOR FINISHES | 1400 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
1400EXT2 | EXTERIOR FINISHES | 1400 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3200
1397INT4 | DOOR HARDWARE REPLACEMENT | 1397 | The doors have manually operated flush bolts with a padlock on the outside of each door. International Building Code (IBC) 2012 chapter 10 Means of Egress, section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1396INT1 | VCT FLOORING REPLACEMENT | 1396 | The Vinyl Composite Tile (VCT) flooring in the Gatehouse/ Guard Shack is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | GATEHOUSE/ GUARD SHACK | 9972 | Correct | HCC |  | Winnemucca | 1987 | 36 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 324
3754SFT1 | EXTERIOR FINISHES | 3754 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ARSENIC TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2010 | 160 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 1600
1400ENR1 | INSULATE BUILDING | 1400 | The building is not insulated and is not energy efficient. Due to this, the heater continuously runs and the water pipes are at risk of damage caused by freezing temperatures. This project will install (R19) batt insulation in the walls and (R38) batt insulation in the ceiling with impermeable vinyl surface to help moderate temperature fluctuations. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 4800
1400EXT3 | EXTERIOR DOOR REPLACEMENT | 1400 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1396EXT0 | EXTERIOR FINISHES | 1396 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | GATEHOUSE/ GUARD SHACK | 9972 | Correct | HCC |  | Winnemucca | 1987 | 36 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
1398EXT2 | EXTERIOR SIDING REPLACEMENT | 1398 | The storage shed has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3760
9972ENV1 | ABOVE GROUND WASTE OIL TANK CONTAINMENT | 9972 | The existing above ground waste oil tank is located on dirt. This project would install a concrete slab under the tank to prevent soil contamination and provide secondary containment and make it easier for maintenance and operations personnel to access the tank. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2200
1398EXT1 | ROOF REPLACEMENT | 1398 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next year with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | STORAGE SHED | 9972 | Correct | HCC |  | Winnemucca | 1986 | 188 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2256
1394SFT4 | CARBON MONOXIDE DETECTOR INSTALLATION | 1394 | International Fire Code (IFC) 2012 section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with a single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with National Fire Protection Agency (NFPA) 720 and the manufacturer’s instructions. This project would provide funding for the purchase and installation of 3 carbon monoxide alarms in accordance with this code. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 600
1394ADA6 | ADA DOOR HARDWARE REPLACEMENT | 1394 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
1394PLM5 | WATER HEATER REPLACEMENT | 1394 | There are three 97 gallon propane water heaters in the building. The average lifespan of a water heater is eight to ten years. The units were installed in 2013. It is recommended that 3 new propane water heaters, straps, braided steel hose, expansion tanks, ball valves, new flex gas lines and pans be installed in the next 5-6 years. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 9000
1395HVA2 | EVAPORATIVE COOLER REPLACEMENT | 1395 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed, including all required connections to utilities. The estimate includes removal and disposal of the old evaporative cooler. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1400HVA2 | ELECTRIC HEATER REPLACEMENT | 1400 | There are two electric heaters in the building that are not adequate and have reached the end of their expected life. This project recommends replacing the two electric heaters and installing an additional electric heater. The estimate includes removal and disposal of the existing equipment. | PUMP HOUSE | 9972 | Correct | HCC |  | Winnemucca | 1987 | 320 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 6000
3754INT1 | INTERIOR FINISHES | 3754 | It is recommended to maintain the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. This will include cleaning all surfaces, if needed, adding additional adhesive or fasteners to the FRP, caulking and to make necessary repairs to expansion joints and moldings. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | ARSENIC TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2010 | 160 | 2016-07-07 | Four to Ten Years | Long-Term Needs | 3 | 1600
2554EXT2 | EXTERIOR FINISHES | 2554 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain a weather tight condition. It is recommended that this project is implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | WATER TANK | 9972 | Correct | HCC |  | Winnemucca | 2006 | 1500 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2554EXT3 | GUARDRAIL | 2554 | The National Fire Protection Association (NFPA) 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an American Water Works Association (AWWA) D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | WATER TANK | 9972 | Correct | HCC |  | Winnemucca | 2006 | 1500 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 12000
9972SIT5 | HAZARDOUS COMMUNICATION PROGRAM | 9972 | Due to the storage of hazardous materials, this site shall comply with International Fire Code (IFC) 2012 Chapter 4 Emergency Planning and Preparedness, and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2000
2554INT1 | INTERIOR FINISHES | 2554 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all American National Standards Institute (ANSI), National Sanitation Foundation (NSF) and American Water Works Association (AWWA) approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | WATER TANK | 9972 | Correct | HCC |  | Winnemucca | 2006 | 1500 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 5000
3786EXT1 | EXTERIOR FINISHES | 3786 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WASTEWATER TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2006 | 120 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
3786EXT2 | EXTERIOR DOOR REPLACEMENT | 3786 | The exterior metal door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | WASTEWATER TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2006 | 120 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3786INT1 | INTERIOR FINISHES | 3786 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WASTEWATER TREATMENT BUILDING | 9972 | Correct | HCC |  | Winnemucca | 2006 | 120 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1397ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1397 | The existing wood working equipment has only partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have full collection capability. This project will provide for the replacement of the existing system and installation of additional capacity to minimize explosion hazard and disruption to production. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 20000
1394SIT1 | REPLACE EXIT STAIRS, SIDEWALK AND RAMP | 1394 | The concrete sidewalk and exit stairs for the housing unit appear to be part of the original construction. They are deteriorating mainly from exposure to the weather. Spalling and cracking has occurred, and in some instances they are unsafe. The stairs are not up to current code (existing 8" risers at entry, cannot exceed 7" per chapter 10 of the 2012 IBC) and there is not an ADA accessible entrance. This project would provide funding for the removal and replacement of the sidewalk, main entrance concrete stairs, including other exit stairs, and construction of an ADA accessible ramp into the building. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 75000
1397SEC1 | EXTERIOR DOOR REPLACEMENT | 1397 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of five new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9972SIT1 | SIDEWALK REPLACEMENT | 9972 | The sidewalks serving the buildings on this site are deteriorated and failing. In some areas cracks wider than four inches have been identified, and there is settling in many locations. This project addresses removal and replacement of existing sidewalks as needed. 4" thick concrete sidewalks were used for this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project includes providing an accessible path of travel from the ADA parking area through the gatehouse to the visitors area which is located in the Housing Unit. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 76000
1397SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 1397 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to Nevada Administrative Code (NAC) 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 International Building Code (IBC) chapter 9, section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 56000
1397ELE1 | LIGHTING UPGRADE | 1397 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24500
1397SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1397 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. International Building Code (IBC) 2012 chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3500
1397ADA1 | ADA RESTROOM REMODEL | 1397 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 15000
1395HVA1 | EXHAUST HOOD INSTALLATION | 1395 | Section 507.2.2 of the Uniform Mechanical Code (UMC) states, "Hoods shall be installed at or above all commercial-type dishwashing machines and similar equipment which produce comparable amounts of steam..." This project would provide funding to install a Type II exhaust hood above the dishwasher in the culinary area. This project will provide for an exhaust hood, roofing repairs, electrical and installation. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 9200
1395ELE1 | LIGHTING UPGRADE | 1395 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1394ADA1 | ADA RESTROOM UPGRADE | 1394 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 40000
1397PLM1 | WATER HEATER REPLACEMENT | 1397 | There is a electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3750
1394INT1 | REPLACE SUBFLOORING | 1394 | Areas exist where the sub-floor has been damaged due to water infiltration and a lack of bracing in the rooms, hallways, showers and bathroom areas. Age and constant traffic have contributed to the deterioration. This project would provide funding to remove the existing damaged sub-floor and install new bracing and plywood sub-flooring where needed. This work should be performed prior to installing new toilets, urinals and any other remodeling of the bathrooms and rooms. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 30000
1394ELE3 | ELECTRICAL UPGRADE | 1394 | The building has numerous electrical outlets and switches which are missing covers or broken, extension cords that are used to supply electrical power, and exposed electrical wires on equipment and the distribution system in attic. This project would provide for repairs and/or replacement of the damaged electrical outlets and switches, installation of 110volt ground fault circuit interrupter (GFCI) outlets, as needed, and repairing the exposed electrical. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 5000
1394ELE2 | EXHAUST FAN REPLACEMENT | 1394 | Many of the exhaust fans in the restrooms and shower areas were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of 10 high volume commercial exhaust fans. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 20000
1394INT3 | FLOORING REPLACEMENT | 1394 | The floor covering throughout this building is in poor condition and has reached the end of its useful life. The current floor covering is Vinyl Composition Tile (VCT) in the corridors and circulation areas, sheet vinyl in restrooms and carpet in office and sleeping areas. This project would provide funding to replace all of the floor coverings with VCT and non-slip sheet vinyl in the restrooms. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 124780
1395ADA1 | ADA RESTROOM UPGRADE | 1395 | The culinary area is often used for an inmate visitation area. The men's and women's designated restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 25000
1395ADA2 | ADA SIGNAGE | 1395 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1394SEC1 | EXTERIOR DOOR REPLACEMENT | 1394 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of seven new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/21/2000 and 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1395INT3 | FLOORING REPLACEMENT | 1395 | The floor coverings throughout this building are in generally poor condition and have reached the end of their serviceable lives. At the present time, most of the floor surfaces have been removed in the cafeteria and culinary area. This presents health and sanitation issues. The remaining floor covering has 12" Vinyl Composition Tile (VCT) floor covering. This project would provide funding to replace the entire floor with non-slip sheet vinyl, and includes removing and installing the Culinary preparation and cooking equipment, tables and chairs. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63000
9972SIT3 | SITE BOLLARDS | 9972 | The site has a fueling area for agency vehicles. The above ground fuel tank requires bollards for protection from vehicle impact per International Fire Code (IFC) 2012. This project would provide for the purchase and installation of 12 - 8" concrete filled steel bollards to protect the fuel tank. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 12000
1397STR1 | STRUCTURAL REPAIRS | 1397 | A storage area has been constructed in the Maintenance Shop, accessed via stairs. There is no record of a Capital Improvement Project (CIP) for this work or of any structural evaluations having been conducted. This project recommends adding structural members to the existing framing to ensure proper load bearing capacity. This will require a structural design from a licensed engineer, inspections and permitting which are not included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 8000
1397HVA1 | FURNACE REPLACEMENT | 1397 | The existing ceiling-mounted propane fired furnaces appear to be original to the building and have reached the end of their expected life. They are showing signs of aging and at the time of the survey were inoperable. This project would provide for the removal and disposal of the old furnaces and installation of 4 new ceiling-mounted propane fired furnaces. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1397HVA2 | REPLACE EVAPORATIVE COOLERS | 1397 | Evaporative coolers are installed on the side of this building. They are severely scaled and have reached the end of their useful and expected life. This project would provide for 2 new evaporative coolers to be installed including all required connections to utilities. The estimate includes removal and disposal of the old coolers. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1395ADA3 | ADA UPGRADES | 1395 | The existing threshold at the door entrance exceeds ½ inch. Americans with Disabilities Act (ADA) requirements state that the threshold should not be any higher than ½ inch for accessibility, ICC/ANSI A117.1-2009 404.2.5. The door knobs on the building are round and require a gripping action. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. This project would provide funding for the removal and replacement of the threshold and the door knobs to meet these requirements. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 15000
1395SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1395 | The building is a B occupancy per the 2012 International Building Code (IBC). Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 98000
1394PLM3 | EVAPORATIVE COOLER REPLACEMENT | 1394 | There are currently nine evaporative coolers mounted on the roof of the Housing Unit, three for each wing. They are severely scaled and have reached the end of their serviceable life. This project would provide for nine new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
1394PLM2 | PLUMBING REPLACEMENT | 1394 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted and failing especially underground. This project would provide for replacement all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | ADMINISTRATION/ HOUSING UNIT | 9972 | Correct | HCC |  | Winnemucca | 1986 | 12478 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187170
1395CUL1 | ADA ACCESSIBLE COUNTER | 1395 | The plastic laminate countertop for serving food is: non Americans with Disabilities Act (ADA) compliant, is separating, falling down and has deteriorated to a point where it presents health, safety and sanitation issues. This project would provide funding for the removal of the existing countertop and installation of a new plastic laminate countertop. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | CAFETERIA/ CULINARY BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 12750
1397SFT3 | HANDRAIL INSTALLATION | 1397 | The handrail serving the stairs to the Mezzanine does not meet the 2012 International Building Code (IBC) 1009.11 which requires two handrails and extensions. This project would provide for the installation of new handrails in the stairwell. This project should coincide with any projects related to the Mezzanine structural recommendations project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 2500
9972SIT8 | CRACK FILL & SEAL ASPHALT PAVING | 9972 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and driving test areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 87,120 square feet of asphalt area was used to generate this estimate. It is recommended that this project coincide with the ADA Parking Space project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108900
9972SIT2 | BUILDING SIGNAGE | 9972 | The site contains numerous buildings with no signage identifying function or contents. Some of the buildings contain flammable liquids or gases. In case of emergency the buildings should be identified for safety purposes. This project would provide funding for signage to be installed on all of the buildings. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | HUMBOLDT CONSERVATION CAMP SITE | 9972 | Correct | HCC |  | Winnemucca | 1986 |  | 2016-07-07 | Immediate to Two Years | Currently Critical | 1 | 6000
1397INT1 | GYPSUM BOARD REPAIR | 1397 | Water leaks and moisture has damaged the gypsum board in the laundry room. If the gypsum board is not removed and replaced, the moisture potentially could cause mold and dry-rot. This project recommends removing the gypsum board, and replacing it with green board and installing Fiberglass Reinforced Panels (FRP). Per International Building Code (IBC) 2012 section 1210 was used as a reference fro this project. This project or a portion thereof was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/07/2016. | MULTI-PURPOSE BUILDING | 9972 | Correct | HCC |  | Winnemucca | 1986 | 7000 | 2016-07-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2150EXT1 | EXTERIOR FINISHES | 2150 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF PAINT STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1995 | 64 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1581ENR2 | REPLACE WATER HEATER | 1581 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear. It is recommended that a new gas fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, bracing and labor for installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2750
1581INT1 | INTERIOR FINISHES | 1581 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 8860
2155ENV1 | INSTALL DUST COLLECTION SYSTEM | 2155 | The existing wood working equipment has partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project will provide for the replacement of the existing system and installation of additional capacity to minimize explosion hazard and disruption to production. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF WOOD SHOP | 9973 | CNR | Forestry |  | Carlin | 1998 | 1050 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 13000
1581ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1581 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and installation of new signage to meet the criteria for ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2149EXT2 | EXTERIOR ELEVATIONS | 2149 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CUBIE/EUREKA COUNTY STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1989 | 385 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1155
1581ADA1 | ADA RESTROOM REMODEL | 1581 | A restroom is present in this building. It does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ADA accessibility. This project would provide funding for construction of a unisex ADA restroom. These items may include new sinks, toilets, urinals, partitions, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 25000
1581SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1581 | The existing exit signs in this building are non-illuminated or the older type style and should be replaced with new self-illuminated or LED style signs with a battery-backup. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project would provide for 3 emergency lights and three exit signs including required electrical connections and installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3000
2154EXT1 | EXTERIOR FINISHES | 2154 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF TOOL SHED | 9973 | CNR | Forestry |  | Carlin | 1997 | 180 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2152EXT1 | EXTERIOR FINISHES | 2152 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF PROPANE STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1988 | 48 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2151EXT1 | EXTERIOR FINISHES | 2151 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF HERBICIDE STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1988 | 48 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1581ADA4 | INSTALL LEVER ACTION DOOR HANDLES | 1581 | The existing door handles in the building are older round type and do not meet the ADA requirements for grasping. This project would provide for new lever action door hardware to be installed on all doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3000
1581ADA5 | ACCESSIBLE BUILDING ENTRANCE | 1581 | The building has a ramp and a step leading into the main entrance. This configuration does not meet the requirements for ADA Accessibility This project would provide funding for an accessible concrete ramp, including upper and lower landing areas, handrails, curbing, and replacement of the door hardware and threshold for ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 15000
2156EXT1 | EXTERIOR FINISHES | 2156 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF SHOP | 9973 | CNR | Forestry |  | Carlin | 1988 | 2692 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2692
2549EXT1 | EXTERIOR FINISHES | 2549 | It is important to maintain the finish, weather resistance and appearance of the water tank on a cyclical basis. This project recommends work to protect the exterior tank envelope including sand blasting, painting, staining, or other applied finishes to maintain the tank in good, weather tight condition. | CCC WATER TANK | 9973 | CNR | Forestry |  | Carlin | 1988 |  | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 50000
1581ADA3 | ACCESSIBLE COUNTERTOP | 1581 | The plastic laminate countertop at the public information window in the building does not meet ADA requirements. This project addresses removal and replacement of the plastic laminate countertop. This will bring the reception counter into conformance with ADA requirements. The project includes the removal of the countertop, casework modifications, replacement of countertop, and gypsum board repair and painting. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2148EXT1 | EXTERIOR FINISHES | 2148 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF CHAIN LINK STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1990 | 385 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2155SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2155 | The existing exit signs in this building are non-illuminated and should be replaced with new self-illuminated or LED style signs with a battery-backup. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project would provide for two emergency lights and one exit sign including required electrical connections and installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF WOOD SHOP | 9973 | CNR | Forestry |  | Carlin | 1998 | 1050 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1500
2155EXT1 | EXTERIOR FINISHES | 2155 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF WOOD SHOP | 9973 | CNR | Forestry |  | Carlin | 1998 | 1050 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
2156INT1 | INTERIOR FINISHES | 2156 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF SHOP | 9973 | CNR | Forestry |  | Carlin | 1988 | 2692 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13460
2154ELE1 | ELECTRICAL WIRING | 2154 | The building wiring is a nonmetallic sheathed cable. Nevada State Public Works Board Adopted Standards requires "All building interior power, telephone, signal and other low voltage wiring (whether plenum-rated or not) shall be installed in raceways" 8.4.1. This project would provide funding to rewire the electrical outlets in raceways. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF TOOL SHED | 9973 | CNR | Forestry |  | Carlin | 1997 | 180 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1500
2150SFT1 | SAFETY CABINETS | 2150 | Flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity, shall have a proper storage container, reference OSHA 1910.106 (7) (d). This project will provide one OSHA approved storage cabinet for gasoline, aerosol cans, and other flammable items. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | NDF PAINT STORAGE SHED | 9973 | CNR | Forestry |  | Carlin | 1995 | 64 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3000
1581SEC1 | WINDOW REPLACEMENT | 1581 | The rear exit door has a wire glass window that is broken. This project would provide funding for the removal and replacement of the wire glass window. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | NDF ADMINISTRATION OFFICE | 9973 | CNR | Forestry |  | Carlin | 1988 | 3544 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 500
0697EXT4 | EXTERIOR FINISHES | 0697 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67385
0697SEC1 | EXTERIOR DOOR REPLACEMENT | 0697 | The existing exterior doors and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. The frames are damaged as well as the hinges. Because of security concerns and the door's condition, this project would provide funding to replace the door, frame, locks and hardware, typical of 8. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
9973SEC1 | INSTALL POLE LIGHTING AROUND PARKING LOT | 9973 | The entrance road and parking area have insufficient lighting. Considering the environment of the site, this area needs to be well lighted. This project would provide funding for purchase and installation of 12 additional 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. LED Light fixtures should be considered for energy savings. The poles should match the existing light poles surrounding the site. This project or a portion there of was previously recommended in the FCA report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
1580ADA1 | ADA RESTROOM REMODEL | 1580 | Two restrooms are present in this building. They do not meet the Americans with Disabilities Act (ADA) regulations. This project would provide funding for remodeling one of the restrooms into a unisex restroom for ADA compliance. These items may include new sinks, toilets, urinals, partitions, hardware, mirrors, fixtures, accessible showers, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 15000
1580ELE1 | LIGHTING UPGRADE | 1580 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0697INT1 | REPLACE FLOORING | 0697 | The flooring in this building consists of carpet in the living and office areas, VCT (vinyl composite tile) in the corridors and bathrooms, and ceramic tile in the culinary area. These floor finishes are reaching the end of their useful life. The tile in the culinary has numerous areas missing tiles It is recommended that the flooring in the building be replaced. This project or a portion there of was previously recommended in the FAC report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 161724
1580SEC1 | EXTERIOR DOOR REPLACEMENT | 1580 | The two existing exterior doors, frames and locks appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. The frames are damaged as well as the hinges. Because of security concerns and the condition of the doors, this project would provide funding to replace the doors, frames, locks and hardware including paint. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0697ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0697 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and installation of new signage to meet the criteria for ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3500
1580EXT1 | OVERHEAD DOOR REPLACEMENT | 1580 | The existing 10’x16’ sectional overhead door is damaged from abuse and is original to the building. It has holes, bent panels, and no longer operates properly. This project would provide funding for removal and disposal of the old overhead door and the purchase and installation of a new insulated sectional overhead door with a motor, including connections to utilities as required. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 15500
1580ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1580 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for the purchase and installation of new signage to meet the criteria for ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 3750
1580SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1580 | The existing exit signs in this building are non-illuminated or the older type style and should be replaced with new self-illuminated or LED style signs with a battery-backup. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project would provide for 3 emergency lights and three exit signs including required electrical connections and installation. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1600
0697SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0697 | This building does not have an automatic fire suppression system. This building has more than 12,000 square feet on the first floor. NAC 477.917 indicates every existing building owned by the State of Nevada must: (a) Comply with the provisions of NRS 477.100 to 477.170, inclusive; (b) Meet the requirements of the building code in effect when the building was constructed; (c) If the building: (1) Is designated as a B occupancy; (2) Regardless of occupancy designation, has a floor area which exceeds 12,000 square feet on any floor or 24,000 square feet on all floors, including any mezzanines; or (3) Is an R-1, R-2 or R-4 occupancy be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building; This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 94339
0697HVA3 | SHOWER EXHAUST FAN REPLACEMENT | 0697 | Many of the exhaust fans in the restrooms and shower area were damaged, missing covers and inoperative. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of 6 exhaust fan assemblies including ducting and connections to utilities. Due to excessive humidity concerns, high volume commercial units should be installed. This project there of was previously recommended in the FAC report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 4800
0697HVA1 | ROOF-MOUNTED EVAPORATIVE COOLER REPLACEMENT | 0697 | There are 7 evaporative coolers installed on the roof of this building. It appears that they have reached the end of their useful life. It is recommended that the evaporative coolers be replaced. Connection to the existing utilities is included in this estimate This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0697ADA1 | ADA RESTROOM REMODEL | 0697 | Restrooms are present in this building. They do not meet the Americans with Disabilities Act (ADA) regulations. This project would provide funding for remodeling one of the restrooms for ADA compliance. These items may include new sinks, toilets, urinals, partitions, hardware, mirrors, fixtures, accessible showers, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/19/2000 and 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 40000
0697SFT3 | HANDRAIL INSTALLATION | 0697 | There are two exterior sets of stairs which are lacking handrails. The 2012 IBC Chapter 10, Section 1012 outlines the requirements for handrails. This project would provide for the installation of handrails on each side of the exterior stairs an two locations. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 1100
1580HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1580 | The building has a side discharge evaporative cooler. The cooler is beginning to rust and alkaline has scaled the unit to the point of plugging up the fins. This project would provide funding for the purchase and installation of a new side discharge evaporative cooler. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1580ELE2 | MINOR ELECTRICAL REPAIRS | 1580 | The building has numerous electrical outlets and switches which are missing covers or broken, have extension cords being used to supply electrical power, and no GFCI outlets. This project would provide for repairs and/or replacement by a licensed contractor to repair and/or replace the damaged electrical outlets, switches, covers and conduit. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date 09/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9973SIT2 | BUILDING SIGNAGE | 9973 | The site contains several different buildings with no signage to identify the contents or use. Some of the buildings contain paint, propane tanks and other possible flammable items. In case of an emergency the buildings should be labeled. This project would provide funding for signage to be installed on all the buildings. This project or a portion there of was previously recommended in the FCA report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1580STR1 | STRUCTURAL ASSESSMENT | 1580 | An upper level storage mezzanine has been constructed inside of the multi-purpose building. The 2012 IBC has a minimum requirement of 125 p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. This project or a portion there of was previously recommended in the FCA report dated 9/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 9/17/2013. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 2500
2146EXT1 | EXTERIOR FINISHES | 2146 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC STORAGE SHED | 9973 | Correct | CCC |  | Carlin | 1988 | 100 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
9973SFT1 | PORTABLE FIRE EXTINGUISHERS | 9973 | Several of the buildings do not have fire extinguishers. Portable fire extinguishers shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. On Class A fires, the placement of extinguishers shall be located so that the travel distance for employees to any extinguisher is 75 feet or less and on Class B fires, placement of extinguishers shall be located so that the travel distance for employees to any extinguisher is 50 feet or less. Reference OSHA 1910.157(d). This project would provide funding for the purchase of 10 fire extinguishers, cabinets, and the hardware necessary to install them. This project or a portion there of was previously recommended in the FCA report dated 09/19/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Immediate to Two Years | Currently Critical | 1 | 5000
1580EXT2 | EXTERIOR FINISHES | 1580 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, metal siding repairs, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Four to Ten Years | Long-Term Needs | 3 | 7000
1580INT2 | INTERIOR FINISHES | 1580 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1580ENR2 | WINDOW REPLACEMENT | 1580 | There are three small old single pane window units that should be scheduled for replacement. This project would provide for the installation of three new insulated window units. Removal and disposal of the old units is included in this estimate. | CCC MULTI-PURPOSE BUILDING | 9973 | Correct | CCC |  | Carlin | 1990 | 7000 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2145EXT2 | EXTERIOR FINISHES | 2145 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC GATEHOUSE | 9973 | Correct | CCC |  | Carlin | 1988 | 48 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2144EXT1 | EXTERIOR FINISHES | 2144 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CCC WELL PUMP HOUSE | 9973 | Correct | CCC |  | Carlin | 1988 | 98 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
9973SIT4 | CRACK FILL AND SEAL ASPHALT PAVING | 9973 | The existing paved area around the site is in fair condition. This project recommends filling in the minor cracks, applying a slurry seal and re-striping the parking area and entrance road in the next two to three years. This project or a portion there of was previously recommended in the FCA report dated 09/29/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/17/2013. | CARLIN CONSERVATION CAMP | 9973 | Correct | CCC |  | Carlin | 1988 |  | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0697HVA4 | BOILER REPLACEMENT | 0697 | There are two gas fired boilers that are original to the housing unit and are reaching the end of their expected life. This project would provide for 2 new gas fired boilers to be installed. Removal of the old boilers and connection to existing utilities is also included in this estimate. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0697INT2 | INTERIOR FINISHES | 0697 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CCC HOUSING UNIT | 9973 | Correct | CCC |  | Carlin | 1988 | 13477 | 2013-09-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67385
0621ENR4 | WINDOW REPLACEMENT | 0621 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0622EXT1 | EXTERIOR FINISHES | 0622 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0622INT1 | INTERIOR FINISHES | 0622 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 9600
0622SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0622 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 4800
0622EXT4 | CONCRETE APRON REPAIRS | 0622 | The exterior concrete aprons have extensive cracking and are due for replacement. This project would provide for the installation of two new 4" thick concrete slab-on-grade aprons at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0622ENV1 | SPILL CONTAINMENT | 0622 | The shop does not have a method for containing spills or leakage from hazardous materials. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. This project would provide proper storage containers and secondary containment pallets as needed and install placards on the building exterior. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 6500
2165EXT1 | EXTERIOR FINISHES | 2165 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF STORAGE SHED #1 | 9974 | CNR | Forestry |  | Wells | 1985 | 160 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 320
0621ADA4 | EXTERIOR DOOR REPLACEMENT | 0621 | The exterior entrance door is on an accessible path of travel, but the door hardware and threshold are not compliant. The door and frame are also damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for replacement of the door and frame including ADA compliant door hardware and a compliant threshold. ADA compliant signage is also included in this project. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 6000
0621ADA3 | INSTALL LEVER ACTION HARDWARE | 0621 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0622EXT2 | OVERHEAD DOOR REPLACEMENT | 0622 | There is a 10'x14' overhead door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead door and replacement with a motorized door. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0621SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0621 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 16800
0621ADA5 | ADA ACCESSIBLE COUNTER | 0621 | The ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 4000
0621INT3 | VCT FLOORING REPLACEMENT | 0621 | The VCT flooring in the building is worn and damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0621EXT1 | EXTERIOR FINISHES | 0621 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0621SFT4 | WATER HEATER SEISMIC BRACING | 0621 | The water heater is not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 500
2165INT1 | DOOR HARDWARE REPLACEMENT | 2165 | The door has a manually operated flush bolt with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved lever. | NDF STORAGE SHED #1 | 9974 | CNR | Forestry |  | Wells | 1985 | 160 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2165EXT2 | CONCRETE FOUNDATION | 2165 | The metal storage shed’s floor and landing is dirt. This project would provide for the removal of the metal shed and would provide for the installation of a stem wall, 4” thick concrete floor and a landing in front of the building. The metal shed would need to be anchored to the stem wall per the engineer’s or architect’s design. Additionally, this project would require a plan review and permit from State Public Works Division. | NDF STORAGE SHED #1 | 9974 | CNR | Forestry |  | Wells | 1985 | 160 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 16000
0622ELE2 | ELECTRICAL PANEL UPGRADES | 0622 | The electrical subpanel in the building does not have a cover that properly protects individuals from touching the breakers. This does not comply with NEC 2011 or OSHA 1910. This project would provide funds to fabricate and install a new cover in accordance with NEC 2011 and OSHA 1910. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0622ELE1 | WIRING CLEANUP | 0622 | The wiring in the building is disorganized and not in proper electrical boxes and doesn’t have covers on the boxes. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0622EXT3 | ROOF REPLACEMENT | 0622 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
0621INT1 | INTERIOR FINISHES | 0621 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0621ENR3 | REPLACE WATER HEATER | 0621 | There is a 19 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0621ENR2 | HVAC UPGRADE | 0621 | The propane heaters and window mounted air conditioners were installed in 1985. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC system which will result in energy savings and efficiency. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0621ADA6 | BREAK ROOM REMODEL | 0621 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes the removal and the disposal of the existing materials. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 15000
0621ADA1 | ADA RESTROOM REMODEL | 0621 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of one unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 15000
0621ADA2 | ADA SIGNAGE | 0621 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1500
0622INT2 | DOOR HARDWARE REPLACEMENT | 0622 | The doors have manually operated flush bolts with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 2000
0621ELE1 | WIRING CLEANUP | 0621 | The wiring in the Administration Office is disorganized and not in proper electrical boxes with covers. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 2000
0622HVA1 | HEATER REPLACEMENT | 0622 | The existing HVAC system consists of a ceiling mounted propane heater and does not have cooling equipment. The heater is inefficient and should be replaced with a propane fired heater 80% AFUE or higher unit. This project would provide for disposal of the existing unit and replacement with a new propane fired unit including connections to utilities. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0621EXT2 | GUTTER REPLACEMENT | 0621 | The existing gutter on the Administration Office eave has numerous joints that have proven impossible to seal against leaks. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with a seamless gutter. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0621ENR5 | LIGHTING UPGRADE | 0621 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0622ENR2 | LIGHTING UPGRADE | 0622 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7680
0622SFT3 | STORAGE REMOVAL | 0622 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, Storage shall be maintained 2 feet or more below the ceiling in nonsprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings. This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
0621SIT1 | IRRIGATION UPGRADE | 0621 | The existing irrigation system for the building was not working at the time of the survey. The irrigation system should be scheduled for repair. This project would provide for the repairs of the existing irrigation lines. | NDF ADMINISTRATION OFFICE | 9974 | CNR | Forestry |  | Wells | 1985 | 1200 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0622SFT2 | SAFETY CABINETS | 0622 | The building contains many different paints, stains, gas and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | NDF GARAGE/ SAW SHOP | 9974 | CNR | Forestry |  | Wells | 1986 | 960 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0708PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 0708 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 annual maintenance fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1391INT5 | GYMNASIUM FLOOR REPAIRS | 1391 | The concrete floor in the gymnasium is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface, and applying an appropriate finish product where applicable. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2993EXT1 | EXTERIOR FINISHES | 2993 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1440
0708INT4 | INTERIOR FINISHES | 0708 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 140000
0708EXT3 | EXTERIOR FINISHES | 0708 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 140000
1391INT4 | INTERIOR FINISHES | 1391 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1391EXT5 | EXTERIOR FINISHES | 1391 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 14000
9974ADA2 | ADA SIDEWALK REPLACEMENT | 9974 | The sidewalks serving the buildings and recreation areas on this site are constructed of pieces of concrete. An ADA accessible path of travel should be provided. This project addresses the removal and the replacement of the existing concrete pieces, as needed, to provide new concrete sidewalks. 4,800 SF of 4" thick concrete was used for this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 72000
2136SFT1 | EXTERIOR LANDING INSTALLATION | 2136 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
2136EXT1 | EXTERIOR FINISHES | 2136 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting of the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
2995EXT1 | EXTERIOR FINISHES | 2995 | It is important to maintain the finish, weather resistance and appearance of the Water Tank. This project recommends work to protect the exterior of the Water Tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. It is recommended to conduct inspections and testing on a cyclical basis based per NAC 445. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WATER TANK | 9974 | Correct | WCC |  | Wells | 1985 | 250 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2136INT1 | INTERIOR FINISHES | 2136 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
2137INT1 | INTERIOR FINISHES | 2137 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1440
2994EXT2 | ROOF REPLACEMENT | 2994 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1092
2137EXT1 | EXTERIOR FINISHES | 2137 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1440
2136EXT2 | ROOF REPLACEMENT | 2136 | The asphalt roofing system on the building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1391EXT6 | ROOF REPLACEMENT | 1391 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 84000
2994EXT1 | EXTERIOR FINISHES | 2994 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting of the wood gables, door and fascia, caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 364
0708INT5 | VCT FLOORING REPLACEMENT | 0708 | The VCT flooring throughout the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126000
0708SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0708 | This building does not have an automatic fire suppression system and has more than 12,000 square feet on the first floor. Current state regulations require state-owned buildings having more than 12,000 square feet on one floor, or more than 24,000 square feet total, must be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers, including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 196000
0708SFT3 | FIRE ALARM SYSTEM UPGRADE | 0708 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Per NAC 477.917, If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 56000
0708HVA2 | AIR CONDITIONER INSTALLATION | 0708 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0708ENR3 | BOILER REPLACEMENT | 0708 | There are two hot water boilers servicing the building. They are original to the building dating back to 1984. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valve and replacement with new energy efficient equipment including all required connections to utilities and equipment. The estimate is based on a 300 MBH output hot water boiler. This project should be implemented concurrently with the water treatment project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0708ENR2 | WATER HEATER REPLACEMENT | 0708 | There are five 100 gallon propane-fired water heaters throughout the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended to replace the water heaters with an energy efficient on-demand tankless water heaters. The estimate is based on the purchase and installation of five 7.4 gallon per minute propane gas fired units and includes disposal of the old equipment. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
1391ELE3 | ELECTRICAL UPGRADE | 1391 | The existing electrical system in the building is old, has exposed romex, loose wiring, and is at its maximum capacity. This project would provide for a complete upgrade to the system. It would include new stranded wires in conduit and to remove the existing Romex wiring throughout the building. It would secure the loose wiring and add a new subpanel with increased capacity. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
9974SEC3 | SECURITY SYSTEM INSTALLATION | 9974 | There is no central security camera or recording system for the site. This is a safety issue for the public, staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire site and all required connections to existing utility systems. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 75000
0708EXT4 | EXTERIOR DOOR REPLACEMENT | 0708 | The existing exterior metal doors and frames appear to be original to the building. They are damaged and showing signs of wear and deterioration from constant use and inmate abuse. This project would provide for the removal and replacement of ten new metal door assemblies including frames, locks, hardware and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0708ADA3 | ADA RAMP UPGRADE | 0708 | The ramp at the entrance to the building does not fully meet ADA ramp accessibility guidelines. The design and geometry of rails are incorrect and there is no curb on the open side of the ramp. This project recommends the installation of new handrails and a curb to comply with current ADA accessibility standards. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 35000
1391PLM3 | WATER TREATMENT SYSTEM REPLACEMENT | 1391 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and have approached the end of their expected life. Failure of the equipment causes wear and tear on the domestic water supply lines, clothes washing equipment, and plumbing fixtures. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program, including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 annual maintenance fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1391SFT2 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1391 | There are two sets of interior stair handrails that are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to the bottom of the landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railings is included in this estimate. NRS 338.180, 2012 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 18000
1391PLM2 | WATER HEATER REPLACEMENT | 1391 | There is a 100 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1391PLM1 | LAUNDRY ROOM REMODEL | 1391 | The Laundry Room does not have enough space or equipment to keep up with demand. The equipment takes up most of the floor space leaving very little space to maneuver. It is recommended to remodel the area creating a larger space for the Laundry Room and to upgrade the existing equipment. This project would provide for remodeling the area and replacing the existing washers and dryers. Removal and disposal of the existing equipment and construction materials is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0708HVA3 | EVAPORATIVE COOLER REPLACEMENT | 0708 | There are currently nine evaporative coolers mounted on the roof of the Housing Unit, three for each wing. They are severely scaled and have reached the end of their serviceable life. This project would provide for nine new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 16000
2994SFT2 | EXTERIOR LANDING INSTALLATION | 2994 | There is an out-swinging exterior door which swings out over dirt and does not have a landing in compliance with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0708ADA7 | ADA UPGRADES | 0708 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 27000
0708SFT9 | EXTERIOR LANDING INSTALLATION | 0708 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 10000
0708SFT8 | SMOKE CARBON MONOXIDE ALARM | 0708 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. Per IFC 2012 Section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with these codes. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 13500
0708EXT5 | GUTTER REPLACEMENT | 0708 | The existing gutter on the building and downspouts have numerous joints that have proven impossible to seal against leaks. The leaking gutters and downspouts will cause premature deterioration to the building finishes and the site hardscape. The downspouts currently terminate within inches of the rain gutter with no continuous drainage away from the building. This project would replace the existing segmented gutter with seamless gutter, downspouts and extensions to approximately 5'-0" away from the perimeter of the building. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55000
2994ELE1 | GFCI OUTLETS | 2994 | The existing receptacles in the Fuel Station Storage Shed are standard duplex receptacles. The 2011 NEC 210.8 requires these locations to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
2994ENR1 | LIGHTING UPGRADE | 2994 | The existing light fixture is the older fluorescent type, and is not energy efficient. This project will upgrade the fixture to a higher efficiency unit with a longer life cycle. 5,000K LED lamps, without the ballast, is suggested, and new tombstones (if needed). An occupancy sensor will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 728
0708ADA5 | ADA TABLE UPGRADE | 0708 | Per the United States Access Board Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 Section 902 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 3 of the fixed seats, which will allow access for four wheel chairs. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 3000
9974ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 9974 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 18750
2995INT1 | INTERIOR FINISHES | 2995 | It is important to maintain water quality, quantity and the interior finish of the Water Tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the Water Tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | WATER TANK | 9974 | Correct | WCC |  | Wells | 1985 | 250 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
2994SFT1 | PROPANE TANK RELOCATION | 2994 | There is an above ground propane storage tank at the front of the building. According to Table 3504.2.1 of the 2012 IFC, flammable gases must be stored at least 5 feet away from a building of non-rated construction. This project would provide for relocating the propane storage tank to comply with code. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 3500
2994INT2 | DOOR HARDWARE REPLACEMENT | 2994 | The door has a manually operated flush bolt with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved lever. | FUEL STATION STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 91 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2993SFT1 | EXTERIOR LANDING INSTALLATION | 2993 | There is an out-swinging exterior door which swings out over dirt and does not have a landing in compliance with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 5000
2993INT2 | DOOR HARDWARE REPLACEMENT | 2993 | The door has a manually operated flush bolt with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project is to install new Schlage grade 1 or approved equal keyed ADA approved lever. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2993EXT2 | ROOF REPLACEMENT | 2993 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | NDF STORAGE SHED #2 | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1728
2137ADA1 | ADA UPGRADES | 2137 | The existing threshold at the door entrance exceeds ½ inch. ADA requirements state that the threshold should not be any higher than ½ inch for accessibility, ICC/ANSI A117.1-2009 404.2.5. The door dead bolt on the door is round and requires a gripping action. Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. This project would provide funding for the removal and replacement of the threshold and the door dead bolt to meet these requirements. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 6000
2137EXT2 | ROOF REPLACEMENT | 2137 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | TOOL STORAGE SHED | 9974 | Correct | WCC |  | Wells | 1985 | 144 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1728
1391SFT4 | FLUE VENT REPLACEMENT | 1391 | There are several flue vents in the building which do not comply with IMC 2012 chapter 8, chimneys and vents. The flue vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. It is recommended that all flue vents throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flue vents should be installed by a licensed contractor. This project would provide funds to replace all the flue vents throughout the building. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 8000
9974PLM1 | SEPTIC SYSTEM REPLACEMENT | 9974 | The septic system serving the site is failing. This project recommends replacing the septic tank and moving the leach field. The estimate includes abandoning and filling the old septic tank and the installation of a new tank and leach field. This estimate is for an engineered system which will conform to all required environmental rules and regulations including NDEP. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
2136EXT3 | EXTERIOR DOOR REPLACEMENT | 2136 | The existing exterior metal doors and frames appear to be original to the building. They are damaged and are showing signs of wear and deterioration and are no longer plumb, due to building foundation settling. This project would provide for the removal and replacement of two new metal door assemblies including frames, locks, hardware and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0708PLM1 | PLUMBING REPLACEMENT | 0708 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted and failing especially underground. This project would provide for replacement all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 210000
0708SIT1 | SITE DRAINAGE UPGRADES | 0708 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0708SFT5 | FLUE REPLACEMENT | 0708 | There are several flues in the building, which do not comply with IMC 2012 chapter 8, chimneys and vents. The flue vents were installed with improper flues and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The vents, in some cases, are too close to combustibles and don’t have the proper clearances, per IMC 2012 this can cause a fire hazard. The ductwork is connected with metal tape and per 803.10.1 supports and joints ductwork shall be fastened with sheet metal screws, rivets or other approved means. The flues are in poor condition and have cracks. Per 801.18.2 flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that all flues throughout the building be replaced. Replacements shall meet the manufacture’s specifications and IMC 2012. The flues should be installed by a licensed contractor. This project would provide funds to replace all the flues throughout the building. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 48000
1391EXT7 | EXTERIOR SIDING REPLACEMENT | 1391 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 150000
1391ENV1 | BIRD ABATEMENT | 1391 | The building has been inhabited by birds. The birds introduce a potential risk of disease, cause maintenance problems with the roofing systems and cost labor time for general clean-up. This project would provide for the removal and the disposal of bird debris, eggs and carcasses from the site and building by a licensed pest control business. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 3000
1391INT6 | DOOR HARDWARE REPLACEMENT | 1391 | The doors have manually operated flush bolts with a padlock on the outside of each door. Per IBC 2012 Chapter 10 Means of Egress, Section 1008, manually operated flush bolts or surface bolts are not permitted. This project would install new Schlage grade 1 or approved equal keyed ADA approved dead bolts and levers. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 7000
1391HVA1 | HEATER REPLACEMENT | 1391 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 4500
1391SFT3 | BATTERY STORAGE | 1391 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2012 IFC. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 25000
2136ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 2136 | There is an outlet in the Pump House building which is not GFCI protected. This outlet should be changed to GFCI type outlet per the NEC. This project would provide for the purchase and installation of one GFCI outlet. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
2136ENR1 | LIGHTING UPGRADE | 2136 | The existing lighting fixture is the older incandescent type, and is not energy efficient. This project will upgrade the fixture to a higher efficiency unit with a longer life cycle. A 5,000K LED is suggested. An occupancy sensor will be installed for additional savings. Any electrical wiring upgrades are not included in this estimate. | PUMP HOUSE | 9974 | Correct | WCC |  | Wells | 1984 | 125 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 1000
0708ENR5 | LIGHTING UPGRADE | 0708 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Four to Ten Years | Long-Term Needs | 3 | 112000
0708HVA1 | EXHAUST HOOD INSTALLATION | 0708 | Section 507.2.2 of the UMC states, Hoods shall be installed at or above all commercial-type dishwashing machines and similar equipment which produce comparable amounts of steam. This project would provide funding to install a Type II exhaust hood above the dishwasher in the culinary area. This project will provide for an exhaust hood, roofing repairs, electrical and installation. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 9200
0708SEC1 | INSTALL ALARMS ON BACK DOORS OF CULINARY | 0708 | Add delayed egress alarms to all exterior doors. These are 30 second delayed egress magnetic locks that interface with the fire alarm. Under normal conditions they give off an "attempt to egress tone" and then unlock the door 30 seconds after being activated by pushing on the crash bar. The locks automatically release upon activation of the fire alarm. They also have a bypass feature for times when the door needs to be left open or unalarmed i.e. making deliveries, etc. The alarms also have remote annunciators that can be located in one or more locations i.e. control room, etc. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 70000
0708SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0708 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 28000
1391ENR2 | REPLACE INSULATION | 1391 | There are numerous areas of damaged insulation at the ceiling that is in need of replacement. This project would provide for the removal of the ceiling insulation and would install a faced R-38 insulation which will help to reduce energy costs. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1391EXT1 | WINDOW REPLACEMENT | 1391 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, energy efficient units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1391ENR1 | LIGHTING UPGRADE | 1391 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1391SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1391 | The emergency egress lighting is nonexistent and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 14000
1391EXT2 | OVERHEAD DOOR REPLACEMENT | 1391 | There is a 10'x12' overhead coiling door which is damaged and does not function properly. Exposure and wind have caused the door to bend, crack and lose its finish. It has also been struck and dented by vehicles. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1391EXT4 | EXTERIOR DOOR REPLACEMENT | 1391 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the three exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1391ADA2 | ADA SIGNAGE | 1391 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 600
0708ADA2 | ADA SIGNAGE | 0708 | The ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 2500
0708ADA1 | ADA RESTROOM REMODEL | 0708 | There are no ADA compliant restrooms in the facility. There should be an ADA restroom for visitors as well as for the inmates. The existing visitors restroom, the inmate restrooms and shower rooms will require a complete retrofit. This project would provide funding for construction of a unisex accessible restroom for visitors and an accessible restroom and shower area for the inmates in one of the housing wings. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 150000
0708INT1 | CULINARY FLOOR REPLACEMENT | 0708 | The painted concrete floor in the kitchen is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | HOUSING/ CULINARY/ ADMINISTRATION | 9974 | Correct | WCC |  | Wells | 1984 | 14000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 9200
9974SEC1 | INSTALL EXTERIOR SITE LIGHTING | 9974 | The site has minimal site lighting in the parking lot and between the buildings which is a security and safety concern. This project would provide funding for the purchase and installation of twelve 20'-0" high light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | WELLS CONSERVATION CAMP SITE | 9974 | Correct | WCC |  | Wells | 1984 |  | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 110400
1391ADA1 | ADA RESTROOM UPGRADE | 1391 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of one unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2000 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2016. | MULTI-PURPOSE/ GYMNASIUM | 9974 | Correct | WCC |  | Wells | 1985 | 7000 | 2016-08-24 | Immediate to Two Years | Currently Critical | 1 | 15000
1620ADA3 | ADA DOOR HARDWARE REPLACEMENT | 1620 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and Sections 309.4 and 404.2.7 of the 2010 ADA Standards for Accessible Design were used as references for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 10000
1620SIT1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 1620 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the chair, shelf and other items currently blocking the working space. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 250
1620SFT3 | FIRE RATED CEILING REPAIRS | 1620 | The fire rated ceiling in the equipment closet is damaged and should be scheduled for immediate repair. A square hole has been cut in the one hour fire rated assembly which compromises the fire protection design of the building. This project would provide for repair of the gypsum board ceiling with a 5/8" type X fire rated gypsum board to include tape, mud, texture and paint. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2500
1620ADA5 | ADA SHOWER UPGRADE | 1620 | This project would provide for an ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of a stainless steel ADA compliant shower cabinet unit complete with accessible plumbing fixtures, seat, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 25000
2493EXT3 | EXTERIOR FINISHES | 2493 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years. It is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12960
2493ENV1 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 2493 | This project will provide for the purchase of 4 OSHA approved drum spill pallets capable of storing 4 drums each, and the purchase of 1 OSHA approved storage cabinet for miscellaneous items, such as gas cans, etc. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 25000
2493SIT1 | REPLACE CONCRETE APRON | 2493 | The NDF Industry Building has a 20' x 50' concrete apron leading up to the overhead doors. The concrete is damaged and should be scheduled for replacement in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1620EXT3 | OVERHEAD DOOR REPLACEMENT | 1620 | The existing 8' x 10' metal overhead coiling door does not function properly due to age and abuse and repair parts are difficult to find. This project would provide for the removal and disposal of the existing door and the purchase and installation of a new manually operated overhead coiling door. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1620EXT2 | EXTERIOR DOOR REPLACEMENT | 1620 | The existing hollow metal doors and frames are original to the building and are showing signs of age and are damaged. This project would provide for the removal of the existing door assemblies and installation of new metal door assemblies including all required hardware and painting. ADA door hardware is included for the main entrance. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2493INT1 | INTERIOR FINISHES | 2493 | It is recommended that the interior walls be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12960
2493EXT0 | EXTERIOR DOOR REPLACEMENT | 2493 | The existing exterior doors to the Industry Building are original. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors were used to generate this estimate. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 9000
2493EXT4 | OVERHEAD DOOR REPLACEMENT | 2493 | There is an overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and the replacement with a motorized door. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 8000
2493SFT8 | FLUE REPLACEMENT | 2493 | There is a heater flue in the building, which does not comply with UMC 2012 Chapter 8, Chimneys and Vents. The flue was installed with an improper flue and per Section 804 Direct-Vent Terminations, vent terminals for direct-vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue is disconnected, and some of the flue is aluminum flex duct and per 803.8 Vent Connector Construction, vent connectors shall be constructed of metal. The minimum thickness of the connector shall be (No. 28 gage) for galvanized steel. Per 801.18.2, flue passageways, the flue liner, chimney inner wall or vent inner wall shall be continuous and shall be free of cracks, gaps, perforations or other damage or deteriorations, which would allow the escape of combustion products, including gases, moisture and creosote. It is recommended that the flue be replaced. Replacements shall meet the manufacture’s specifications and UMC 2012. The flue should be installed by a licensed contractor. This project would provide funds to replace and install 1 new flue to the existing heater. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2000
24936 | COMPRESSED AIR SYSTEM LEAKS | 2493 | The air compressor is leaking. This is causing the compressor to cycle frequently and is inefficient. This project will provide for repairs, and/or removal of the lines to stop the leaks. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 500
1620INT5 | FLOORING REPLACEMENT | 1620 | The VCT flooring in the NDF Administration Building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22068
1620EXT7 | EXTERIOR FINISHES | 1620 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 24520
1620ADA6 | ADA ACCESSIBLE COUNTER | 1620 | ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project would provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1620PLM4 | WATER HEATER REPLACEMENT | 1620 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 2500
1620HVA1 | HVAC EQUIPMENT REPLACEMENT | 1620 | The HVAC split system was installed in 1990. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1620INT3 | JANITORS CLOSET REPAIRS | 1620 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced plastic (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1620ADA4 | ADA PARKING SPACE | 1620 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2500
1620ENR1 | LIGHTING UPGRADE | 1620 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19616
1620INT1 | INTERIOR FINISHES | 1620 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24520
1620ADA2 | ADA SIGNAGE | 1620 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces for buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide for accessible signage which is required under ADA. All signage shall conform to ICC/ANSI A117.1-2009 Chapter 7 requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF ADMINISTRATION BUILDING | 9975 | CNR | Forestry |  | Tonopah | 1990 | 2452 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 3000
2493EXT1 | WINDOW REPLACEMENT | 2493 | The building has two dual pane windows. Both windows are broken. This project would provide funding for the purchase and installation of two dual pane windows as well as disposal of the existing windows. This project or a portion thereof was previously recommended in the FCA report dated 09/01/2005 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | NDF INDUSTRY BUILDING | 9975 | CNR | Forestry |  | Tonopah | 2004 | 1296 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4800
1619PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1619 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines and plumbing fixtures. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual costs are not included in the project cost. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. For budgeting purposes a $12,000 annual maintenance fee is suggested. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1619HVA3 | HEATER REPLACEMENT | 1619 | The gymnasium part of the building is heated by four ceiling mounted propane-fired heating units. They are original to the building and two of the units were missing at the time of the survey. They have reached the end of their useful life. This project provides for the disposal of the existing units and replacement with four new propane-fired units including connections to utilities. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 10000
1619EXT2 | EXTERIOR SIDING REPLACEMENT | 1619 | The corrugated metal panels covering the building are original and the lower section of the walls should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5780
1619HVA2 | HVAC EQUIPMENT REPLACEMENT | 1619 | The HVAC split system was installed in 1990. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1619EXT4 | WINDOW REPLACEMENT | 1619 | The existing windows in this building are single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the 4 windows with new dual pane security rated window systems. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
1618INT6 | RESURFACE CULINARY WING FLOOR | 1618 | The painted concrete floor in the culinary wing is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
1618EXT5 | WINDOW REPLACEMENT | 1618 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, wire mesh and higher efficiency units. This estimate is for the replacement of 70 units. Removal and disposal of the existing windows is included in this estimate. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
1618ADA3 | RESTROOM AND ADA REMODEL | 1618 | The bathroom and shower rooms are in overall poor condition. The countertops in each wing show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the bathrooms and shower rooms. The restrooms do not meet ADA regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2009 Sections 603 - 604 and 2012 ICC Chapter 11. Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for three Men's restroom facilities, one in each residential wing. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 1500000
1618EXT3 | EXTERIOR DOOR REPLACEMENT | 1618 | There are nine existing exterior doors that are damaged from abuse and age. This project would provide for the removal of the existing doors and the purchase and installation of new metal doors. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 9 doors. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
1619ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1619 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1618INT5 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 1618 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware, including lever action door handles and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 27 doors were used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
2723EXT1 | EXTERIOR FINISHES | 2723 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. It is also recommended to conduct inspections and testing on a cyclical basis per NAC 445. This project or a portion thereof was previously recommended in the FCA report dated 07/16/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | WATER TANK | 9975 | Correct | TCC |  | Tonopah | 1990 | 1133 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11330
1618ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1618 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of one drinking fountain to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1618EXT4 | LOADING DOCK REPAIRS | 1618 | The loading dock behind the culinary area and the driveway leading up to it are worn and damaged and in need of repair. This project provides for the repairing and resurfacing of the concrete, as well as installing new hardware, such as the truck guard. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1618HVA4 | BOILERS AND HEATING SYSTEM RENOVATION | 1618 | There are two 500 MBH hot water boilers; one 100 MBH water heater; one 40 MBH water heater; circulation pumps, and baseboard heaters that are used for the heating system in this building. The life expectancy of the heating system is between 20 to 25 years with proper maintenance and with the use of a water treatment program. This heating system is original to the building and dates back to 1990. Replacement parts for routine and emergency maintenance are hard to find. This project would provide for the removal and disposal of the existing heating system and the installation of a new heating system, to include all required connections to the existing utilities. The existing chemical water treatment system will need to be tested and adjusted once the equipment is operational. $2,000 is included in this estimate for testing the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 353500
1621INT1 | INTERIOR FINISHES | 1621 | It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 6720
2724INT1 | INTERIOR FINISHES | 2724 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/16/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
1619INT2 | STAIRS AND HANDRAIL REPLACEMENT | 1619 | The existing interior stairs on the east side are constructed of wood and do not meet current building codes. Also, the hand rails do not meet the requirements in the 2012 IBC section 1012. This project would provide for the removal and disposal of the existing stairs and construction of a new wood framed set of stairs and handrails. The door swings outward, therefore, a three foot wide landing will be required at the top of the stairs and is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 15000
1619EXT1 | EXTERIOR FINISHES | 1619 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project should be completed on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 70000
1621SFT1 | EGRESS LIGHTING UPGRADE | 1621 | The existing emergency egress illumination is outdated and does not meet current standards as required by the 2012 ICC Chapter 10, Section 1006.1. This project would provide for the installation of new emergency egress lighting including connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 750
2724EXT2 | EXTERIOR SIDING REPLACEMENT | 2724 | The storage shed has painted T1-11 siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 900
1618HVA3 | EXHAUST FAN REPLACEMENT | 1618 | Many of the exhaust fans in the restrooms and shower areas were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2723EXT2 | GUARDRAIL INSTALLATION | 2723 | The Water Tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | WATER TANK | 9975 | Correct | TCC |  | Tonopah | 1990 | 1133 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 12000
2723INT1 | INTERIOR FINISHES | 2723 | It is important to maintain water quality, quantity and the interior finish of the Water Tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | WATER TANK | 9975 | Correct | TCC |  | Tonopah | 1990 | 1133 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 5000
1619PLM2 | WATER HEATER REPLACEMENT | 1619 | There is a 97 gallon propane-fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9975SIT0 | SITE BOLLARDS | 9975 | There are two above ground fuel tanks on the site, one for diesel and one for unleaded gasoline that do not have adequate bollard coverage. Per IFC 2012 Section 312 Vehicle Impact Protection, this project recommends that steel posts be installed, not less than 4 inches in diameter and filled with concrete. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for ten new bollards to be located in-between the other bollards around the tanks. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2724EXT3 | ROOF REPLACEMENT | 2724 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 432
1621EXT3 | EXTERIOR FINISHES | 1621 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 6720
9975SIT6 | SITE DRAINAGE UPGRADES | 9975 | The grade does not slope away from the buildings effectively. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3, site grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. If physical obstructions or lot lines prohibit 10 feet (3048 mm) of horizontal distance, a 5-precent slope shall be provided to an approved alternative method of diverting water away from the foundation. Swales used for the purpose shall be sloped a minimum of 2 percent where located within 10 feet (3048 mm) of the building foundation. Impervious surfaces within 10 feet (3048 mm) of the building foundation shall be sloped a minimum of 2 percent away from the building. This project would create positive flow away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9975SFT1 | GAS LINE SERVICE | 9975 | The propane tank farm has a damaged braided steel flex line after the pressure regulator. During the time of the survey there was a strong odor of gas. This project would provide for a licensed plumber to test all gas lines within the propane tank farm and repair any needed items. When completed, the licensed plumber should perform a manometer test on the gas lines. This project will provide for the replacement of the damaged flex line, the repair of any leaks and will certify the propane lines and tanks. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 15000
1619EXT6 | EXTERIOR DOOR REPLACEMENT | 1619 | The existing exterior doors to the Multi-Purpose building are original. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and the replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1619SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1619 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1618INT9 | DEDICATED CIRCUIT/ MICROWAVE | 1618 | The housing unit does not have adequate power supply for the use of the microwaves that are located in the hallway. This project would provide for twelve (20 ampere) dedicated circuits to be run to the microwave location and for the purchase of twelve new microwaves. This project includes the hook-up to the electrical panel and breakers. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
1618INT8 | FLOORING REPLACEMENT | 1618 | The VCT flooring in the Housing Unit is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 87399
1618PLM3 | WATER HEATER REPLACEMENT | 1618 | There are (3) ninety one gallon propane-fired water heaters in the building. The average life span of a water heater is 8-10 years. The units are showing signs of wear and should be scheduled for replacement within the next year. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 9000
1618HVA5 | AIR CONDITIONER INSTALLATION | 1618 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of one air conditioner, to include all required connections to existing utilities. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1618INT7 | INTERIOR FINISHES | 1618 | It is recommended to paint the interior walls and ceilings in the next 2-3 years. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129480
1621ENR4 | LIGHTING UPGRADE | 1621 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5376
1621SFT7 | EXTERIOR LANDING INSTALLATION | 1621 | There are two out-swinging exterior doors which swing out over dirt and do not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | PUMP HOUSE | 9975 | Correct | TCC |  | Tonopah | 1990 | 672 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1618SFT4 | EXTERIOR LANDING INSTALLATION | 1618 | Section 1008.1 of the 2012 IBC describes the requirements for doors, including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landings at two of the doors of the building do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1619PLM4 | PLUMBING REPLACEMENT | 1619 | There is a water softener upstairs in the storage room that is draining into an open sewer line. It does not have a P-Trap. This creates an "off gas" of Hydrogen Sulfide into the air. Hydrogen Sulfide can cause irritation to the eyes and respiratory tract and can cause headaches, dizziness, drowsiness, nausea and nervousness. Exposure to high concentrations of Hydrogen Sulfide can be fatal at extremely high levels. This project will remove the sewer line serving the water softener. A new sewer line will be installed that will correct the deficiencies per IPC 2012. This estimate includes the removal and disposal of the existing system, as required. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1618EXT6 | EXTERIOR FINISHES | 1618 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 129480
1618SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1618 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/ or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
1619INT3 | INTERIOR FINISHES | 1619 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Four to Ten Years | Long-Term Needs | 3 | 70000
1619ADA2 | ADA SIGNAGE | 1619 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces for buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide for accessible signage which is required under the ADA. All signage shall conform to ICC/ANSI A117.1-2009 Chapter 7 requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 2500
1618ADA2 | ADA SIGNAGE | 1618 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces for buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide for accessible signage which is required under the ADA. All signage shall conform to ICC/ANSI A117.1-2009 Chapter 7 requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 3000
1618HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1618 | Ten evaporative coolers are installed on the roof of the building. They are in poor condition and it is recommended that these units be replaced in the next 2-3 years. Utility connections are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9975SEC1 | SITE POLE LIGHT INSTALLATION | 9975 | The entrance road and parking area have insufficient lighting. Considering the environment of the site, this area needs to be well lit. This project would provide funding for the purchase and installation of 12 additional 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110448
1618ENR1 | LIGHTING UPGRADE | 1618 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 103584
9975ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9975 | The existing sidewalks throughout the site have deteriorated and are failing. In some areas cracks wider than four inches have been identified and there is settling in a number of locations. This project addresses the removal and replacement of the existing sidewalks site-wide with sidewalks providing curbing and rails where needed to address accessibility concerns. This project includes providing an accessible path of travel from the parking lot to the visitor’s area to meet ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 100000
1618ADA1 | ADA RESTROOM REMODEL | 1618 | The staff and visitors restroom does not meet ADA regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2009 Sections 603- 604, 2012 IBC Chapter 11 and ADAAG. Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for one men's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project should be done concurrent with the restroom remodel project. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | HOUSING/ CULINARY UNIT | 9975 | Correct | TCC |  | Tonopah | 1990 | 12948 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 50000
9975SIT1 | REMOVE OLD FOUNDATION | 9975 | The concrete stem wall foundation structure (used for the weight lifting) remains in the ground. Some of the hardware remains such as Simpson Strong Ties, which pose an injury hazard. This project provides for the demolition and disposal of the remaining foundation and hardware at the weight lifting area. This estimate is for contractor pricing. Using inmate labor will reduce the cost. This project or a portion thereof was previously recommended in the FCA report dated 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1619ENR1 | LIGHTING UPGRADE | 1619 | The existing lighting fixtures are the older fluorescent and metal halide type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1619ADA1 | ADA RESTROOM REMODEL | 1619 | The restroom does not meet current ADA regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2009 Sections 603 - 604 and 2012 ICC Chapter 11. Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucet, mirror, dispensers and door hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one unisex restroom facility. The removal and disposal of the existing restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | MULTI-PURPOSE BUILDING | 9975 | Correct | TCC |  | Tonopah | 1990 | 7000 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 50000
9975ADA1 | ADA PARKING | 9975 | The ADA provides for accessibility to sites and services for people with physical limitations. This project would provide for (1) concrete van accessible ADA parking space/ loading space and the pouring of a concrete walkway to reach and meet up with the existing walkway/ sidewalk. This will require grading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 1000 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 09/11/2000 and 07/12/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | TONOPAH CONSERVATION CAMP SITE | 9975 | Correct | TCC |  | Tonopah | 1990 |  | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 30000
2724EXT1 | EXTERIOR FINISHES | 2724 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 1-2 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 07/16/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2016. | DUMP STATION | 9975 | Correct | TCC |  | Tonopah | 1990 | 36 | 2016-06-07 | Immediate to Two Years | Currently Critical | 1 | 360
0880ENR1 | LIGHTING UPGRADE | 0880 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1980
0882SFT1 | REBUILD HANDRAILS / GUARDRAILS | 0882 | The handrails and guardrails at the stairway and storage mezzanine do not meet the building code requirements in their current configuration. This project would provide for the removal of the existing wood framed railing and replacement with new wood framed handrails and guardrail that will meet the 2006 IBC code Chapter 10, Section 1012 and 1013. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0880HVA1 | REPLACE CEILING MOUNTED HEATER | 0880 | The building is heated by one ceiling mounted gas heater. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement of the unit and associated utility connections. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0881ENR1 | LIGHTING UPGRADE | 0881 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3660
0880INT1 | INTERIOR FINISHES | 0880 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3300
0880EXT1 | EXTERIOR FINISHES | 0880 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF FIRE HOUSE STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 660 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 6600
0881PLM2 | REPLACE WATER HEATER | 0881 | The average life span of a water heater is eight to ten years. The existing 30 gallon propane water heater in the building has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 30 gallon propane water heater. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0881EXT1 | EXTERIOR FINISHES | 0881 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 6100
0881HVA1 | REPLACE HVAC EQUIPMENT | 0881 | Several heating and cooling units throughout the building are original and have reached the end of their expected life. This project would provide for replacement of the window mounted evaporative cooler and two electric baseboard heaters and includes removal and disposal of the existing units and all required connections to utilities. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0881INT1 | INTERIOR FINISHES | 0881 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6100
0881SFT3 | INSTALL FIRE SUPPRESSION SYSTEM | 0881 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NRS 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is classified as a B occupancy. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 6100
0882HVA1 | REPLACE CEILING MOUNTED HEATER | 0882 | The building is heated by one ceiling mounted gas heater. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement of the unit and associated connections to utilities. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0882INT1 | INTERIOR FINISHES | 0882 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7475
0881INT2 | REMODEL INTERIOR | 0881 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement at the time. This project should be concurrent with all other projects having to do with the interior of the building including the fire safety, lighting upgrade and ADA projects. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30500
0882EXT1 | EXTERIOR FINISHES | 0882 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF GARAGE/STORAGE | 9976 | CNR | Forestry |  | Ely | 1987 | 1495 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 7475
0881SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0881 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 5000
0881ADA1 | ADA RESTROOM REMODEL | 0881 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-1998 Sections 603 - 604, 2006 IBC Chapter 11 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 45000
0881SFT1 | FIRE ALARM SYSTEM UPGRADE | 0881 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907.2.1 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 3660
0881PLM1 | 4" BACKFLOW, SHUTOFF, VAULT, AND POWER | 0881 | State Health law now mandates backflow prevention devices be installed on all domestic, fire protection and irrigation systems to prevent contamination. This project makes allowance for installing a 4" reduced pressure backflow prevention assembly, required fittings, an above ground vault, and allowance for 200 feet of 1" conduit to provide power for the required heat source inside the vault. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 25000
0881ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0881 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to parking, building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | NDF OFFICE | 9976 | CNR | Forestry |  | Ely | 1987 | 1220 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1500
1388SFT3 | INSTALL FIRE SUPPRESSION SYSTEM | 1388 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NRS 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building exceeds 12,000 s.f. and is partially classified as a B occupancy. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 69840
1388HVA4 | REPLACE EXPANSION TANK BLADDERS | 1388 | At the time of the 2007 survey, the maintenance staff reported that the bladders in the two expansion tanks had failed. It is assumed that the age of the equipment is the cause of the failure. This project provides funding for removal of the existing bladders and installation of two new bladders in the existing expansion tanks. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1388INT6 | RESTROOM REMODEL | 1388 | The bathroom and shower rooms are in overall poor condition. The countertops in each wing show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the bathrooms and shower rooms. Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for three Men's restroom facilities, one in each residential wing. The removal and disposal of the old restroom fixtures is included in this estimate. This project should be coordinated with the ADA restroom project and water line replacement project. This will also address the issue with the floor not properly sloping to the drains. This project or a portion thereof was previously recommended in the FCA report dated 12/01/2001. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500000
1388HVA5 | REPLACE WATER TREATMENT SYSTEMS | 1388 | The existing water softening/ treatment systems in the building are currently operational, but are original to the building and approaching the end of their lifecycles. Failure of the equipment would cause wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1388SFT4 | GFCI DUPLEX OUTLET REPLACEMENT | 1388 | There are 6 GFCI outlets in the restrooms which are not GFCI protected outlets. These outlets are near sinks requiring the outlets to be protected. This project would provide for the purchase and installation of 6 new GFCI duplex outlets. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1500
1388PLM2 | REPLACE DOMESTIC WATER PIPING | 1388 | The domestic water piping under the building are original to the building and are beginning to fail. At the time of the survey, staff reported that the lines are continuously developing leaks. The maintenance time and loss of water is enough to warrant an entire replacement of the piping. This project would provide funding for the removal and disposal of the existing domestic water lines and installation domestic water supply piping. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
1388CUL1 | REPLACE KITCHEN EQUIPMENT | 1388 | The kitchen cooking equipment is original to the building and is reaching the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next two to three years, including ovens, grills and the dishwasher. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. This estimate is a lump some for budgeting purposes. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
1389EXT1 | EXTERIOR FINISHES | 1389 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 33715
1389HVA1 | REPLACE CEILING MOUNTED HEATERS | 1389 | The building is heated by three ceiling mounted gas unit heaters. They are original to the building and are reaching the end of their useful life. This project provides for disposal of the existing units and replacement of the existing units and associated utility connections. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1389HVA2 | REPLACE WATER HEATER | 1389 | The average life span of a water heater is eight to ten years. The existing 100 gallon propane water heater will be reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal of the existing water heater and the replacement with a new water heater including required connections to utilities. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1389EXT2 | REPLACE OVERHEAD COILING DOOR | 1389 | There is a 12'x12' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and replacement of the manually operated overhead coiling door. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1389ADA1 | ADA RESTROOM REMODEL | 1389 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-1998 Sections 603 - 604 and 2006 ICC Chapter 11. Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucet, mirror, dispensers, and door hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Men's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 50000
1388INT5 | NONABSORBANT FINISHES | 1388 | 2006 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1389SFT3 | REBUILD HANDRAILS / GUARDRAILS | 1389 | The handrails and guardrails at the stairway and storage mezzanine do not meet the building code requirements in their current configuration. This project would provide for the removal of the existing wood framed railing and replacement with new wood framed handrails and guardrail that will meet the 2006 IBC code Chapter 10, Section 1012 and 1013. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
9976SEC1 | INSTALL POLE LIGHTING AROUND PARKING LOT | 9976 | The entrance road and parking area have insufficient lighting. Considering the environment of the site, this area needs to be well lit. This project would provide funding for purchase and installation of twelve 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110448
1389ENR1 | LIGHTING UPGRADE | 1389 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20229
1388ADA1 | ADA RESTROOM REMODEL | 1388 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-1998 Sections 603 - 604, 2006 IBC Chapter 11 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers, hardware and an accessible shower stall. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Men's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 60000
1389SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1389 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1500
1389SFT2 | LAUNDRY ROOM REPAIRS | 1389 | The Laundry Room has a base board heater installed in the wall due to the inadequate heating of the building. When the ceiling mounted heating units are replaced, this base board heater should be removed and the gypsum board repaired. The base board heater poses a fire risk as it is currently installed and is not an acceptable solution to the heating inefficiencies. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 1000
1388HVA1 | BATHROOM EXHAUST FAN REPLACEMENT | 1388 | The exhaust fans in the showers and restroom areas are inoperative and/ or insufficient, contributing to moisture accumulation and possible mold infiltration. After the moisture issues are mitigated and wall repairs and repainting occur, the exhaust fans should be replaced. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9976SIT2 | PATCH / SLURRY SEAL ASPHALT PAVING | 9976 | It is important to maintain the asphalt concrete paving on the site. This project would provide for patching, minor crack filling and slurry sealing of the paving site wide including loading zones, access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. This project should coincide with the ADA parking project. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9976PLM1 | INSTALL NEW SEPTIC SYSTEM | 9976 | The existing septic system backs-up frequently and requires frequent pumping. Visual inspection of the septic tanks and leach field piping at the time of the survey showed that the system was virtually inoperable. This project provides funding for abandonment of the existing system and installation of new septic tanks and leach fields for the facility. The system must comply with local, State and Federal environmental laws. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 100000
2728EXT1 | EXTERIOR FINISHES | 2728 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | SHADE RAMADA | 9976 | Correct | ECC |  | Ely | 0 | 352 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 704
1388EXT3 | REPLACE ROOF | 1388 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The roof has many patches on it and is a constant maintenance problem. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 140000
1388HVA3 | HEATING CONTROLS REPLACEMENT AND UPGRADE | 1388 | The existing heating system controls are malfunctioning or inoperative. This project will provide a new master panel with remote monitoring, pulling new wire, associated controls and thermostats. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1388PLM1 | REPLACE WATER HEATERS | 1388 | The average life span of a water heater is eight to ten years. The three existing 100 gallon propane water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of three new 100 gallon propane water heaters. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1388HVA2 | REPLACE AIR CONDITIONING UNITS | 1388 | The building has four window-mounted air conditioning units. These units have a life span of 10 years under normal operating conditions. From a visual assessment it appears they will be reaching the end of their useful life within a few years. This project provides funding for removal and disposal of the existing units and replacement with new units. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1388SEC1 | EXTERIOR DOOR REPLACEMENT | 1388 | The existing exterior commercial grade metal door assemblies appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. Due security concerns and the condition of the doors, this project recommends the installation of new metal doors, frames and hardware and includes the disposal of the existing door assemblies. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1388INT2 | REPAIR JANITORS CLOSET | 1388 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1388ENR1 | LIGHTING UPGRADE | 1388 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41904
2727EXT1 | EXTERIOR FINISHES | 2727 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | PHONE RAMADA | 9976 | Correct | ECC |  | Ely | 0 | 352 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 704
1389ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1389 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to parking, building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
1388ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1388 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to parking, building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restroom. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
1389INT1 | INTERIOR FINISHES | 1389 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | MULTI-PURPOSE/GYMNASIUM | 9976 | Correct | ECC |  | Ely | 1987 | 6743 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33715
9976ADA1 | ADA PARKING SPACE | 9976 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. 1,000 square feet of concrete was used for this estimate. Signage and striping is included. IBC - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. | ELY CONSERVATION CAMP SITE | 9976 | Correct | ECC |  | Ely | 1984 |  | 2017-05-24 | Immediate to Two Years | Currently Critical | 1 | 25000
2131EXT1 | EXTERIOR FINISHES | 2131 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WEIGHT ROOM BUILDING | 9976 | Correct | ECC |  | Ely |  | 590 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 2950
2130EXT1 | EXTERIOR FINISHES | 2130 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | TOOL SHED | 9976 | Correct | ECC |  | Ely |  | 102 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 1020
1388INT1 | INTERIOR FINISHES | 1388 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69840
2129EXT1 | EXTERIOR FINISHES | 2129 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE SHED | 9976 | Correct | ECC |  | Ely |  | 80 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 800
1388EXT1 | EXTERIOR FINISHES | 1388 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Four to Ten Years | Long-Term Needs | 3 | 139680
1388EXT2 | REPLACE EXTERIOR WINDOWS | 1388 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 52 units. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/20/2007. | ADMINISTRATION/HOUSING/CULINARY | 9976 | Correct | ECC |  | Ely | 1984 | 13968 | 2017-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
9977ADA1 | ADA PARKING UPGRADE | 9977 | The existing three ADA curb ramps that lead from the parking lot to the sidewalk in front of the Bradley Building are too steep, they all exceed 1:12. The maximum slope allowed for these ramps is 1:12. The maximum slope allowed for the flared sides of these ramps is 1:10. Refer to IBC/ANSI A117.1 - 2003 Chapter 4. It is recommended these curb ramps be replaced. Saw cutting, removal and disposal of concrete is included in this estimate. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2008. | EAST SAHARA SITE | 9977 | Admin | PubWorks | B&G | Las Vegas |  | 0 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 25000
9977SIT1 | SLURRY SEAL ASPHALT PAVING | 9977 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including loading zones, access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 381,000 square feet of asphalt area was used to generate this estimate which includes the parking areas around and between the DMV and the Bradley buildings as well as the access roads. | EAST SAHARA SITE | 9977 | Admin | PubWorks | B&G | Las Vegas |  | 0 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 228600
0266ELE3 | ELECTRICAL UPGRADE | 0266 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels are at their limit and the breakers trip often. The receptacles are in the floor. There are not enough receptacles and the floor mounted system is old and problematic. It is recommended the entire system be upgraded to meet the evolving needs of the building including switchgear, interior transformers, panel boxes, breakers, wiring and receptacles. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565500
0266SFT8 | FIRE ALARM INSTALLATION | 0266 | This building is equipped with an automatic fire detection and alarm system that is the original system and should be scheduled for replacement. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide smoke detection, horns and strobes throughout the facility in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 113100
0266ADA6 | BUILDING / SITE ADA IMPROVEMENTS | 0266 | The existing ADA accessible parking curb cuts are not completely ADA compliant. The restrooms are not 100% ADA compliant and the building is lacking ADA compliant signage. This project would provide for removing and replacing the non-compliant ADA curb cuts, minor restroom modifications including new and / or relocated fixtures, and a sign package for the entire facility. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 30000
0266INT4 | JANITOR CLOSET FRP | 0266 | There are three Janitor's closets that are in need of wall protection. This project would provide for the installation of a fiberglass reinforced panel (FRP) to be installed on the walls adjacent to the mop sink. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0266ADA5 | ELEVATOR EQUIPMENT UPGRADE | 0266 | The elevators were built and installed in 1975 and require periodic repairs. However, they are currently due for a complete refurbishment of all mechanical parts to maintain the elevator in a safe working order including the hydraulic motors. They are also not ADA compliant and will require new signage, call buttons, two-way communication and any other necessary equipment to comply with the ADA. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0266INT3 | FLOORING REPLACEMENT | 0266 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 168000
0266SFT6 | FIRE SUPPRESSION PIPE REPLACEMENT | 0266 | It is estimated that after installing the double check valve on the fire riser that the water pressure in the fire suppression piping will be reduced by 10%. This reduction in pressure will not supply enough water to the 3rd floor. The Las Vegas Valley Water District is installing a backflow prevention device on the line, the pressure will be reduced by an additional 10%. To compensate for the reduced pressure, it is recommended to replace the 3rd floor piping with larger diameter pipes. This project would provide for re-piping the fire suppression system lines on the 3rd floor to maintain an adequate supply of water for the system. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 12000
0266ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0266 | This building contains drinking fountains on each floor. The drinking fountains on the 1st and 2nd floors have been upgraded to meet current requirements, but the 3rd floor is still without a compliant drinking fountain. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains on the 3rd floor to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 2000
0266ADA4 | BREAK ROOM REMODEL | 0266 | The kitchenettes and associated cabinets in the employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. The estimate is for remodeling 3 break rooms, one on each floor. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 30000
0266INT2 | INTERIOR FINISHES | 0266 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 141375
0266SFT3 | EMPLOYEE BREAK ROOM CONVERSION | 0266 | There is a portion of the existing garage located along the north side of the building which has been converted to an employee break room. The ceiling in this space is less than the required 7'-6" minimum ceiling height for habitable spaces. In addition, the corridor serving the space appears to not meet the requirements for egress. The only way into or out of the space is through a narrow corridor. This project recommends abandoning the use of this space as an employee break room and converting it into a storage room. Signage indicating the use of the space for storage is suggested. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1000
0266EXT4 | EXTERIOR FINISHES | 0266 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the metal paneling and stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 141375
0266SIT3 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0266 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and the sloped concrete and stone walls at the base of the building. Water also flows across the concrete sidewalks causing damage to the concrete and creating a potential slipping hazard. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0266HVA1 | HVAC REPLACEMENT | 0266 | The building is equipped with a central heating and air conditioning system controlled by a direct digital control system. Staff reported during the 2013 survey that the DDC system is no longer operating. The maintenance staff and building occupants report that the air conditioning and heating in the building does not maintain a consistent temperature and is inadequate in some areas. The addition of computers and other electronic equipment, which gives off heat, was thought to contribute to problems with the cooling system. The EvapCo cooling tower is rusting through on the upper portion and is starting to leak. It was also noted that the heat in the building is inadequate. The third floor is heated, the 1st floor does not have a heating coil to provide heat in the cold season and the 2nd floor has been retrofitted with a heating coil but it is inadequate and problematic from a maintenance perspective. This project recommends a building-wide system upgrade which includes the boiler, chiller, cooling tower, air handlers, VFD's, DDC system and duct system in the next 1-2 years. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1200000
0266EXT1 | EXTERIOR METAL WALL PANEL REPLACEMENT | 0266 | The exterior is a dark anodized enamel aluminum wall panel system and is faded due to weather. The dark color increases summertime heat gain, which puts a strain on the HVAC system. There is also discoloration on the south side of the building below the state seal. This project recommends replacing it with a lighter metal wall panel system for increased energy efficiency. Includes removal and disposal of the old system. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Four to Ten Years | Long-Term Needs | 3 | 660000
0266EXT3 | ROOF REPLACEMENT | 0266 | The rolled asphalt roof on this building was in poor condition at the time of the survey. Efforts have been made to repair leaks many times, but the water proofing ability of the roofing is at the end of its useful life. It is recommended that this building be re-roofed in the next 1-2 years with a new single ply roofing membrane and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 200000
0266SFT7 | RELOCATE SPRINKLER HEADS | 0266 | Numerous areas in the facility have inadequate sprinkler coverage due to partition wall construction and relocation, which has cut-off many sprinkler heads. This project would re-design the system and correct the coverage deficiencies. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 25000
0266PLM2 | DOUBLE CHECK VALVE INSTALLATION | 0266 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a double check valve on the fire riser to comply with these requirements. This project or a portion there of was previously recommended in the FCA report dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 15000
0266PLM3 | DOMESTIC WATER LINE INSTALLATION | 0266 | The domestic water currently comes into the building through the same pipe as the fire suppression system water. Once inside the building, this 6" pipe turns vertically for the fire riser, but there is a tee to a 2 1/2" pipe for the domestic water just below the riser. There should be a dedicated line for the domestic water from the main city line and there is no backflow prevention or double check valves on any portion of the water pipes. This project would provide for installing a new 2 1/2" domestic water line from the city main water line in the street to the building including a backflow prevention device between the main and the building. A hot tap, traffic control and asphalt concrete road patching is included. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 90000
0266EXT2 | EXTERIOR INSULATION & FINISH SYSTEM REPAIRS | 0266 | The EIFS (Exterior Insulation and Finish System) near the South building exit and at the column areas is showing signs of damage, cracking and appears to be failing. This project will provide for repair and painting of the damaged areas. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0266ELE1 | INSTALL GFCI OUTLETS | 0266 | Each restroom has a standard Decora style outlet near the sink. These outlets must be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of GFCI duplex outlets. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1500
0266HVA2 | ELEVATOR MACHINE ROOM VENTILATION | 0266 | The elevator Machine Room has solid state elevator equipment located inside. The IBC 2012, Chapter 30, Section 3006.2 requires ventilation of the elevator Machine Room. This project will provide for a ventilation system for this room. It is recommended that this work be done at the same time as the HVAC upgrades. This project or a portion there of was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 25000
0266SFT5 | FIRE CAULK PENETRATIONS | 0266 | Numerous locations throughout the building have piping, conduits and other penetrations through fire rated assemblies. This project would provide fire caulking and/or Intumescent and listed sealants to return the assemblies to full rating. This project or a portion thereof was previously recommended in the FCA reports dated 02/10/2005 and 02/05/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 6/5/2013. | BRADLEY BUILDING (VACANT) | 9977 | Admin | PubWorks | B&G | Las Vegas | 1975 | 28275 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 5000
2062EXT4 | REPLACE EXTERIOR DOOR | 2062 | The existing exterior commercial grade metal door assemblies appear to be original to the building. They are showing signs of wear and deterioration from constant use and abuse. Due security concerns and the condition of the doors, this project recommends the installation of new metal doors, frames and hardware and includes the disposal of the existing door assemblies. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2062EXT3 | EXTERIOR FINISHES | 2062 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. An elastomeric paint is recommended for the stucco. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 8380
2062INT2 | INTERIOR FINISHES | 2062 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4190
2062ADA1 | ADA UPGRADE | 2062 | The only restroom in this building is not compliant with the Americans with Disabilities Act (ADA) regulations and a retrofit is necessary. Given the current configuration of the bathroom, the work will include the installation of a new water closet, a urinal, sink, grab bars, faucets, mirrors, dispensers, hardware and to provide for a unisex restroom. It is also necessary to create an accessible parking area for this building to comply. The parking lot near the building is compliant and proper striping is the only thing necessary to achieve this. A marked crossing across the vehicle way will also be required. The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 25000
2062SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2062 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 1000
2062ELE1 | LIGHTING UPGRADE | 2062 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2514
2062EXT2 | REPLACE OVERHEAD COILING DOOR | 2062 | The existing overhead coiling door appears to be original to the building. It has been damaged and is showing signs of wear and deterioration. The trim around the perimeter of the door is also damaged. This building is being used as a classroom and the door is not used very frequently. It has been stated that larger pieces of equipment are used occasionally in the classroom and the size of the door is necessary. It is recommended that it be replaced with a new insulated overhead coiling door and also the trim be replaced. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2062SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2062 | This building is lacking a fire alarm and detection system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. This project or a portion there of was previously recommended in the FCA report dated 03/17/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | DMV INSPECTION TRAINING GARAGE | 9977 | MtrVeh | B&G |  | Las Vegas | 1976 | 838 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 5866
0153SFT2 | STAIRWAY HANDRAIL INSTALLATION | 0153 | The existing concrete exterior stairs at the entry are lacking a handrail as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for a wood framed handrail to be installed. Material and construction should match the existing guardrail. | GOVERNOR'S MANSION COOK'S COTTAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1965 | 928 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 1500
0154SIT2 | LANDSCAPE WALL REPAIR | 0154 | The concrete landscape wall bearing the name of the pavilion is cracking and flaking. The top layer of paint and concrete is flaking off and is due for resurfacing. It is recommended to resurface the wall by removing the existing paint, sealing the concrete and applying a new finished surface of elastomeric paint. | LLEWELLYN B. GROSS MEMORIAL PAVILION | 9978 | Admin | PubWorks | B&G | Carson City | 1969 | 2827 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0153INT4 | INTERIOR FINISHES | 0153 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION COOK'S COTTAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1965 | 928 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4640
0154ADA1 | ADA SIDEWALK REPAIR | 0154 | The concrete sidewalk to the north of the Pavilion is in need of replacement. Settling has created a non-ADA complaint change of level at the upper transition. The concrete in this area also has minor cracking and spalling. This project would provide for the removal and replacement of the concrete sidewalk. 48 SF of 4" thick concrete sidewalk was used for this estimate. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LLEWELLYN B. GROSS MEMORIAL PAVILION | 9978 | Admin | PubWorks | B&G | Carson City | 1969 | 2827 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 720
0154EXT2 | EXTERIOR FINISHES | 0154 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other attachments to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | LLEWELLYN B. GROSS MEMORIAL PAVILION | 9978 | Admin | PubWorks | B&G | Carson City | 1969 | 2827 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 28270
0707EXT1 | EXTERIOR FINISHES | 0707 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNORS MANSION NORTH HALL | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 6608 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 66080
0707INT1 | INTERIOR FINISHES | 0707 | The interior finishes are in good condition. The walls are covered by wallpaper, wood wainscot and wood trim. The coffered ceiling is covered by painted gypsum board and wood trim. It is recommended that the interior wood areas of the walls and the entire ceiling be stained or painted as appropriate at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GOVERNORS MANSION NORTH HALL | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 6608 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33.04
0707PLM1 | WATER HEATER REPLACEMENT | 0707 | The average life span of a water heater is eight to ten years. The existing 100 gallon natural gas water heater is original to the building. It is approaching the end of its expected life and should be scheduled for replacement in the next 3 to 5 years. This project would provide for the removal and disposal of the old water heater and installation of a new 100 gallon water heater. | GOVERNORS MANSION NORTH HALL | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 6608 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 3500
2455EXT1 | EXTERIOR FINISHES | 2455 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE BUILDING | 9978 | Admin | PubWorks | B&G | Carson City | 2003 | 720 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 7200
2456INT1 | INTERIOR FINISHES | 2456 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EQUIPMENT SHED | 9978 | Admin | PubWorks | B&G | Carson City | 2003 | 120 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
0151EXT3 | EXTERIOR FINISHES | 0151 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 140415
9978SIT1 | FRENCH DRAIN INSPECTION | 9978 | Staff reported that the french drains in the rear yard do not drain correctly causing the grass and sidewalks to flood during normal irrigation practices and precipitation events. The reason for this backup was not known at the time of the survey, but was suspected to be blocked or crushed pipes in the drains. This project would provide funding to scope the french drains by a certified inspector to determine the cause of the problem. Any future projects would come from the inspector's report recommendations. | GOVERNOR'S MANSION SITE | 9978 | Admin | PubWorks | B&G | Carson City | 1907 |  | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 1000
9978SIT2 | LANDSCAPE WALL REPAIR | 9978 | The painted concrete masonry unit landscape walls around the site show varying degrees of wear including cracking and flaking. The top layer of paint and concrete is flaking off in many areas and is due for resurfacing. It is recommended that these areas be resurfaced by removing the existing paint, sealing the concrete masonry unit blocks and applying a new finished surface of elastomeric paint. This project also provides for repairing the significant damage near the rear driveway by the garage. This work may require some new concrete masonry unit blocks and wall caps as well as resurfacing. | GOVERNOR'S MANSION SITE | 9978 | Admin | PubWorks | B&G | Carson City | 1907 |  | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0151EXT4 | DECK AND PAVER REPAIR | 0151 | The brick pavers that accent the driveway and walkways on the east side of the grounds are failing. Also, the poured deck material on the second floor of the Mansion is cracking and failing. The brick pavers are not tied into the surrounding concrete and they consistently move around independently from the concrete. This is due to moisture infiltration between the bricks and the concrete which contributes to ground heaving and erosion. The bricks are dislodged to the point of causing a tripping hazard and are a constant maintenance problem. The second floor decking material is cracking and no longer provides a waterproof barrier to the plywood decking and the floor below. The plywood is warping and buckling causing the joints to separate which contributes to the failed waterproofing system. This project would provide for removing the brick pavers and replacing them with stamped concrete to resemble the original brick. The new concrete should be tied into the existing concrete with rebar connectors. This project would also provide for replacing the poured deck material and repairing any damaged plywood decking below it. Note: This project has been recommended by the State Public Works Board for the 2009 CIP. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 125000
2456EXT1 | EXTERIOR FINISHES | 2456 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | EQUIPMENT SHED | 9978 | Admin | PubWorks | B&G | Carson City | 2003 | 120 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 1200
0151INT2 | INTERIOR FINISHES | 0151 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93610
0151SEC1 | SECURITY SYSTEM UPGRADE | 0151 | The current security surveillance system is outdated and ineffective particularly for night surveillance. The surveillance of the mansion and surrounding grounds is inadequate due to poor placement of cameras, outdated cameras and monitoring equipment and not enough cameras overall. This project would provide for replacing the cameras to color low light cameras and upgrading the monitoring equipment. More effective surveillance will be provided to the security staff by adding more cameras and by selecting new camera locations. Note: This project has been recommended by the State Public Works Board for the 2009 CIP. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 200000
0153EXT3 | EXTERIOR FINISHES | 0153 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION COOK'S COTTAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1965 | 928 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 9280
0152EXT1 | EXTERIOR FINISHES | 0152 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | GOVERNOR'S MANSION GARAGE | 9978 | Admin | PubWorks | B&G | Carson City | 1998 | 912 | 2018-09-11 | Four to Ten Years | Long-Term Needs | 3 | 9120
0151HVA2 | INSULATE ATTIC | 0151 | The attic insulation appears to be original to the building. It has deteriorated and should be replaced. Many locations in the attic are completely missing the insulation or it was not reinstalled after construction work was completed in the past. It is recommended that the entire attic area be reinsulated with R-30 insulation. This will increase energy efficiency and be more resistant to heat loss. The estimate is based on 13" thick blown fiberglass insulation. This project or a portion thereof was previously recommended in the FCA report dated 03/10/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/15/2008. | GOVERNOR'S MANSION | 9978 | Admin | PubWorks | B&G | Carson City | 1908 | 9361 | 2018-09-11 | Immediate to Two Years | Currently Critical | 1 | 12054
1901EXT1 | EXTERIOR FINISHES | 1901 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | SEWAGE BUILDING(VACANT) | 9979 | Admin | PubWorks | B&G | Carson City | 1960 | 96 | 2005-02-14 | Four to Ten Years | Long-Term Needs | 3 | 500
9980SFT1 | HAZARDOUS COMMUNICATION PROGRAM | 9980 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 2000
9980ADA4 | ADA SIDEWALK REPLACEMENT | 9980 | The concrete sidewalk around the building is in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 22500
9980ADA3 | ADA SIDEWALK REPLACEMENT | 9980 | The concrete sidewalk around the building is in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 22500
9980SIT2 | PARKING LOT STRIPING | 9980 | It is important to maintain the striping on the pavement at the site. This project would provide for the necessary striping and painting of the curbs and parking spaces. An ADA parking and loading space emblem will be painted on the concrete that is designated for ADA parking. This project should be scheduled on a 2 year cyclical basis to maintain the integrity of the striping, painting and ADA designation. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0342SFT2 | FIRE ALARM SYSTEM UPGRADE | 0342 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. The facility is also in the process of acquiring licensure under the Centers for Medicare and Medicaid (CMS) which has additional fire alarm system requirements. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 143216
0342ADA2 | ADA SIGNAGE | 0342 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that existing signage be relocated or replaced as needed. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/31/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/12/2012. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0342HVA3 | HVAC REPLACEMENT | 0342 | The central HVAC system consists of two hot water boilers, two rooftop outside air HVAC units, several rooftop packaged units and other related equipment throughout the building. This equipment was installed in the late 1990's, are not energy efficient and should be scheduled for replacement. The boilers are of poor quality and require constant maintenance including replacement of major components. This project would provide for installation of new boilers, rooftop units, associated equipment and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 537060
9980PLM1 | GATE VALVE REPLACEMENT | 9980 | The 6" main water line coming into the site is equipped with a gate valve to control the irrigation system. It has reached the end of its expected life, leaks and should be replaced in the next one to two years. A contributing factor to the deterioration of the valve is that the vault that contains the valve does not have solid sides and allows dirt to build up and bury the valve. This project would provide for replacing the valve and installing a new vault around the valve with a solid cover and solid walls. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
9980SEC1 | SITE SECURITY SYSTEM REPLACEMENT | 9980 | The site is equipped with a motion detecting security system to monitor and report activity outside of the building. The system is outdated and should be scheduled for replacement. It is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the sensors and scan pens that the staff carries. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the motion detection system including equipment, wiring and controls site wide. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 150000
9980ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9980 | There are ten existing light poles around the site with either one or two light fixtures each. The existing lighting fixtures are the older metal halide type, and are not energy efficient. With increased traffic and development in the area, insufficient site lighting is a security and safety concern. This project would provide for the installation of 14 solar powered LED exterior light fixtures on 10 light poles with 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles may be acceptable to re-use. If so, the estimate can be reduced accordingly. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
0342EXT2 | EXTERIOR FINISHES | 0342 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit and cement plaster walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 179020
0342SFT4 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0342 | This building has an automatic fire suppression system. This system is outdated and is not equipped with current code required items such as seismic anchors. The facility is also in the process of acquiring licensure under the Centers for Medicare and Medicaid (CMS) which has additional fire protection system requirements. This project recommends replacing the existing system with a double-interlock pre-action fire suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 429648
0342ADA5 | ADA EMPLOYEE LOUNGE UPGRADES | 0342 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 2000
0342ADA4 | ADA ACCESSIBLE COUNTER | 0342 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1000
0342INT3 | FLOORING REPLACEMENT | 0342 | The carpet in the building is damaged and reaching the end of its useful life. It is recommended that the carpet in the administration areas be replaced with carpet and the carpet in the client areas be replaced with VCT (vinyl composite tile) or sheet vinyl. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
0342HVA2 | VENT INSTALLATION | 0342 | The client sleeping rooms have no natural or mechanical ventilation which is required by code. Per the 2006 International Building Code section 1203.4, "Natural ventilation of an occupied space shall be through windows, doors, louvers or other openings to the outdoors. The operating mechanism for such openings shall be provided with ready access so that the openings are readily controllable by the building occupants." This project would provide for the purchase and installation of a louvered vent in the exterior wall of each of the 51 client sleeping quarters to provide ventilation according to the 2006 IBC. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 76500
0342INT2 | INTERIOR FINISHES | 0342 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 179020
9980SIT1 | SLURRY SEAL ASPHALT PAVING | 9980 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the perimeter road and some regrading on the north west portion of the parking lot. This area does not drain well and causes water to pool up in the parking area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 45,000 square feet of asphalt area was used to generate this estimate. | LAKES CROSSING CENTER SITE | 9980 | HHS | DPBH | Lakes | Sparks | 1974 |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33750
0342ADA3 | ADA RESTROOM UPGRADE | 0342 | The Men's and Women's designated ADA restrooms for the staff offices do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of Men's and Women's accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 25000
0342PLM1 | FLOORING REPAIRS | 0342 | Two of the isolation rooms are fitted with floor drains in the concrete floor. Both of these drains are at a point in the floor other than the lowest point resulting in poor drainage when the floor becomes wet. This project recommends removing the top section of the concrete and pouring a new concrete floor with a positive slope towards the drain in each of the two rooms. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0342SEC3 | SECURITY CONTROL SYSTEM REPLACEMENT | 0342 | This building is equipped with a security control system that is outdated and should be scheduled for immediate replacement. Problems exist with the door control panel and door motor systems for the client rooms and access doors. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. The wiring and conduit are aging and in some areas were not installed properly resulting in premature wear and a higher probability of failure. It is also recommended to install new communications from the main control room to the Nursing Station. Currently, there is no video surveillance in the Nursing Station to monitor clients in the five isolation rooms. Treatment for the clients in the isolation rooms could be enhanced by providing monitoring equipment to the medical staff. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the control panels, matrix system, conduit, wiring and door motor systems and installing new conduit, wiring and video surveillance to connect the Nursing Station to the system. This project should be implemented concurrently with the Video Security System Replacement project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 250000
0342SEC2 | VIDEO SECURITY SYSTEM REPLACEMENT | 0342 | The video security system for the building and the site is outdated and should be scheduled for immediate replacement. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. The wiring and conduit are aging and in some areas were not installed properly resulting in premature wear and a higher probability of failure. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the cameras, conduit and wiring throughout the facility with all digital equipment as well as sufficient storage capacity. This project should be implemented concurrently with the Security Control System Replacement project. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 250000
0342SEC1 | INTERIOR DOOR REPLACEMENT | 0342 | The interior doors are damaged from general abuse and age. There are 115 doors within the secured area and 20 doors outside of the secured area. Some of the doors within the secured area are fire rated doors that do not have magnetic hold opens. These fire doors are often propped open for ease of circulation which compromises the fire rating of the area. There are many doors that are loose in their frames and have worn out locking mechanisms. This project would provide for the removal of the existing doors and the purchase and installation of new doors, frames and hardware. This estimate is for 115 security grade hollow metal doors and 20 solid core wood doors. | LAKES CROSSING CENTER - BUILDING #13 | 9980 | HHS | DPBH | Lakes | Sparks | 1974 | 35804 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 250000
0322SIT1 | SITE DRAINAGE IMPROVEMENTS | 0322 | The building has considerable damage to the exterior finishes and foundation from improper drainage around the building. The grade does not slope away from the building in many areas. This is causing water to pool up next to the building, infiltrate the windows and damage the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. This project should coincide with the Landscaping Upgrade. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0322INT4 | ADA RESTROOM UPGRADE | 0322 | The building does not have accessible restrooms. The existing restrooms do not meet ADA requirements. A complete retrofit is necessary of all 10 restrooms. This project would provide funding for construction of 10 unisex accessible restrooms. Items may include relocating walls, new sinks, toilets, hardware, mirrors, fixtures, flooring, showers and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0322SFT4 | SECURITY SYSTEM INSTALLATION | 0322 | The building does not have a security system and several burglaries have taken place. For security and safety purposes, this project recommends motion detection, door switches, access control and related items to be installed and interfaced with the fire alarm. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 66930
0322INT3 | KITCHEN REMODEL | 0322 | The kitchens were in poor condition at the time of the survey. The cabinets and equipment are showing signs of wear and tear and are approaching the end of their expected life. The electrical outlets are older and do not appear to be GFCI protected. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures, outlets and equipment with mid-range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0322PLM4 | HOSE BIB REPLACEMENT | 0322 | The building has a hose bib that has reached the end of its expected life, has been damaged by freezing temperatures and should be replaced in the next 2-3 years. This project would provide funding for the removal of the existing hose bib and the replacement with a new frost freeze hose bib. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0322SFT12 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0322 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 9000
0322EXT6 | EXTERIOR FINISHES | 0322 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Four to Ten Years | Long-Term Needs | 3 | 133860
0322EXT5 | REPAIR/ REPLACE FASCIA AND SOFFITS | 0322 | The fascia and the soffits on the building are weather beaten, peeling, and are showing signs of considerable wear. This project would provide funding for the removal and disposal of the existing fascia and soffit and the replacement with new fascia and soffit. Also included in this estimate is the sanding, scraping, priming, painting, and any needed roof repairs. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Four to Ten Years | Long-Term Needs | 3 | 24750
0322SIT2 | LANDSCAPING UPGRADES | 0322 | The landscaping is overgrown and is causing structural, egress and drainage issues. Water accumulates in several areas adjacent to the building which may infiltrate the interior during inclement weather. This standing water also causes premature deterioration of the paving and other landscape improvements. This project would provide for the removal of all trees and bushes surrounding the building and will grade the terrain at a 5% slope for 10’ away from the building and will provide for new landscaping. This project should coincide with the Site Drainage Improvements project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0322SFT14 | OPEN FLAME GRILL REMOVAL | 0322 | There are two fixed open flame grills located within 10 feet of the building. Per IFC 2012 Section 308.1.4 Open-flame cooking device, charcoal burners and other open-flame cooking devices shall not be operated on combustible balconies or within 10 feet (3048 mm) of combustible construction. This project would provide funding for the removal of two grills to comply with this code. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0322ELE4 | ELECTRICAL TRANSFORMER REPLACEMENT | 0322 | There is an electrical transformer that is original to the building. The transformer is beyond its life expectancy and should be scheduled for replacement. This project recommends replacing the transformer with a new 30 kVA or greater power transformer. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0322EXT4 | EXTERIOR DOOR REPLACEMENT | 0322 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 15 new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0322SFT11 | FLUE REPLACEMENT | 0322 | The flue vents in the building do not comply with UMC 2012 Chapter 8, Chimneys and Vents. The flue vents were installed with improper flues and per Section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vents are too close to combustibles, do not have the proper clearances and have a potential to leak CO. Replacements shall meet the manufacturer’s specifications and UMC 2012. The flue vents should be installed by a licensed contractor. This project would provide funds for replacement of the flue vents in the building. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 22000
0322ENR1 | LIGHTING UPGRADE | 0322 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 107088
0322ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0322 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system needs have changed. The electrical system is utilized to its current maximum potential, all the bedrooms require AFCI breakers and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical and communications systems to meet the evolving needs of the building. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 334650
0322SFT7 | SPRINKLER HEAD REPLACEMENT | 0322 | The existing fire suppression sprinkler heads are an older style. They are not functioning properly and are susceptible to damage. This project recommends that all of the existing fire suppression sprinkler heads in the building be removed and replaced with new tamper-resistant fire suppression sprinkler heads. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 5800
0322SFT9 | SMOKE ALARM INSTALLATION | 0322 | IRC 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012 requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws in the event that the building is used as a residential occupancy sometime in the future. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 20000
0322ENV1 | ASBESTOS ABATEMENT | 0322 | The building was tested in September, 2017 and found to have asbestos in the ceiling, joint compound, texture and the flooring mastic. This project would entail the abatement of all asbestos containing materials throughout the building per OSHA Standards (29 CFR 1910.1001) and (29 CFR 1926.58) and the removal and disposal following all OSHA standards. This project should coincide with the alterations and/or remodels listed in this report. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 348036
0322SFT6 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0322 | This building has an antiquated automatic fire suppression system. This project recommends replacing the existing system with a double-interlock pre-action fire suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 187404
0322SFT13 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0322 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 26772
0322ELE3 | GFCI OUTLETS | 0322 | There are several outlets throughout the building which are not GFCI protected. These outlets should be changed to GFCI type outlets per the NEC. There are also several GFCI outlets throughout the building which are damaged and not working properly. This project would provide for the purchase and installation of GFCI duplex outlets. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
0322INT5 | INTERIOR FINISHES | 0322 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 133860
0322INT6 | FLOORING REPLACEMENT | 0322 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" cove base and heavy duty commercial grade carpet in the next 2-3 years. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 107088
0322INT7 | CEILING SYSTEM REPLACEMENT | 0322 | There is a small section near one of the kitchens where the ceiling height does not meet current code. IBC 2012 Section 1208.2 Minimum Ceiling Heights Occupiable spaces, habitable spaces and corridors shall have a ceiling height of not less than 7 feet 6 inches (2286 mm). Bathrooms, toilet rooms, kitchens, storage rooms and laundry rooms shall be permitted to have a ceiling height of not less than 7 feet (2134 mm). This project would provide funding for the removal and replacement of the ceiling to meet these requirements to include the framing, drywall, texture and paint. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0322HVA2 | HVAC EQUIPMENT REPLACEMENT | 0322 | The HVAC split systems are not energy efficient and have reached the end of their expected and useful life. The R-22 refrigerant in the cooling systems are no longer EPA compliant and the production is mandated to be phased out completely by January 1, 2020. This project would provide for the installation of 11 new HVAC split systems and the cleaning of the existing duct work and grilles. This project includes the removal and disposal of the existing equipment and all required connections to utilities. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
0322PLM1 | WATER HEATER REPLACEMENT | 0322 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0322PLM2 | WATER HEATER REPLACEMENT | 0322 | There is a 5 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0322PLM3 | PLUMBING REPLACEMENT | 0322 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. The sewer lines are rusted, plugging up and failing especially underground. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 334650
0322SFT10 | FIRE ALARM SYSTEM REPLACEMENT | 0322 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 " If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure." When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and NAC 477 the State Fire Marshal's requirements. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 107088
0322ADA4 | ADA DOOR HARDWARE REPLACEMENT | 0322 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999, 08/24/2006 and 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 25000
0322ADA6 | ADA SIDEWALK REPLACEMENT | 0322 | Many sidewalk sections serving the building and parking areas are deteriorated and failing. In some areas the concrete is spalling considerably and other areas are heaving and settling due to either expansive soils or tree roots. This project addresses the removal and the replacement of the existing sidewalks as needed. 1,250 SF of 4" thick concrete sidewalk was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 12675
0322ADA7 | ADA SIGNAGE | 0322 | The ADA provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and the installation of ADA signage to include updated parking signage and directional signage from the accessible parking spaces to the accessible building entrances. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 5000
0322EXT2 | WINDOW REPLACEMENT | 0322 | The windows are original, single pane construction in wood frames. These older windows are drafty and not energy efficient. The windows do not comply with IBC 2012 Chapter 24 Glass and Glazing which requires safety glazing where the bottom edge of the glazing is less than 18" above the floor. This project recommends replacing the windows with dual pane, higher efficiency units that are safety glazed following IBC 2012 Section 2406 Safety Glazing. This estimate is for the replacement of 101 windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999, 08/24/2006 and 06/21/2012. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/07/2017. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 151500
0322ENR2 | EXTERIOR LIGHTING REPLACEMENT | 0322 | There are 25 perimeter light fixtures surrounding the building that are incandescent, fluorescent and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, including wall packs and can lights and will use the existing wiring. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
0322EXT7 | FENCE REPLACEMENT | 0322 | The Redwood fencing at this building is currently falling over and is unsafe. This project would provide for the removal and the replacement of the Redwood fencing with new 465’ of 6’ Redwood fencing. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16275
0322ELE5 | GENERATOR REPLACEMENT | 0322 | There is a diesel generator on site that has reached the end of its useful life. A reliable generator is a high priority due to the function and use of these buildings. It is recommended that a new 12 kW diesel generator be installed. This estimate includes the removal and disposal of the old generator. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 100000
0322ADA5 | ADA ACCESSIBLE PATH OF TRAVEL | 0322 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 3500 square feet of concrete was used for this estimate. It is recommended that this project coincide with the Crack Fill & Seal Asphalt Paving project. | SRC TRAINING & ADMIN, BLDG #600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 13386 | 2017-09-07 | Immediate to Two Years | Currently Critical | 1 | 87500
0517INT4 | JANITORS CLOSET REPAIRS | 0517 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0517EXT3 | ROOFING REPLACEMENT | 0517 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85404
0517INT3 | CARPET REPLACEMENT | 0517 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
0517ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0517 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 177925
0517ENR1 | AIR CONDITIONER REPLACEMENT | 0517 | Two of the four air conditioners on the west side of the building are older and have reached the end of their useful and expected life. This project would provide for two new split system air conditioners to be installed including all required connections to utilities. The new units shall be designed to significantly reduce electrical usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0345EXT2 | EXTERIOR DOOR REPLACEMENT | 0345 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1955INT6 | FLOORING REPLACEMENT | 1955 | The painted concrete and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be repaired or replaced. This project would provide for stripping and re-painting the concrete with an elastomeric or other water resistant paint and removal and disposal of the carpet and installation of heavy duty commercial grade carpet in the next 4-5 years. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 19424
0345HVA1 | HVAC INSTALLATION | 0345 | The building does not currently have any heating or cooling equipment. It is uncomfortably hot in the summer and cold in the winter. It is recommended to install heating and cooling equipment in the building to ensure a comfortable work environment. This project would provide for the purchase and installation of a packaged heating and cooling unit including all required connections to existing utilities. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0345EXT3 | ROOF REPLACEMENT | 0345 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0345ENR1 | LIGHTING UPGRADE | 0345 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Any electrical wiring upgrades are not included in this estimate. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
0345EXT4 | WINDOW REPLACEMENT | 0345 | One of the two windows is original, single pane construction in a metal frame. The older window is drafty and not energy efficient. This project recommends replacing the window with a dual pane, higher efficiency unit. Removal and disposal of the existing window is included in this estimate. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0345SEC1 | SECURITY SYSTEM INSTALLATION | 0345 | The building does not have a security system. It has been broken into several times and expensive tools and equipment have been stolen. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm in the Administration building. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0344EXT3 | DEMOLISH STRUCTURE | 0344 | The building contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | SRC MR GROUP CARE HOME, BLDG #18(VACANT) | 9981 | HHS | ADSD | SRC | Sparks | 1963 | 1618 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16180
0518HVA1 | AIR CONDITIONER REMOVAL | 0518 | The utility room near the front entrance has a small air conditioner in it that is not installed correctly. The air intake has been punched through the exterior wall and does not meet code for proper installation. It is recommended to remove the air conditioner. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1955ENR1 | HVAC UPGRADE | 1955 | The existing HVAC system consists of natural gas fired furnaces and split system air conditioning units. This equipment is original to the building, has required excessive maintenance in recent years and replacement parts are no longer available. This project would provide for replacing the existing equipment with new energy efficient equipment. The current design does not provide return air ducting from the sleeping rooms. This issue should be analyzed by the mechanical engineer to determine whether these returns should be installed. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36420
0345INT1 | INTERIOR FINISHES | 0345 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0323ENR1 | WINDOW REPLACEMENT | 0323 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 15 units. Removal and disposal of the existing windows is included in this estimate. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11250
0325ADA4 | ADA RESTROOM REMODEL | 0325 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0325ENR2 | AIR CONDITIONER REPLACEMENT | 0325 | One of the two air conditioners is older and has reached the end of its useful and expected life. This project would provide for a new split system air conditioner to be installed including all required connections to utilities. The new unit shall be designed to significantly reduce electrical usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1957EXT3 | DEMOLISH STRUCTURE | 1957 | The building contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | SRC ICF/MR 6-BED HOME,BLDG #16(VACANT) | 9981 | HHS | ADSD | SRC | Sparks | 1963 | 1618 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16180
0324ENR1 | WINDOW REPLACEMENT | 0324 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 25 units. Removal and disposal of the existing windows is included in this estimate. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
0324EXT3 | EXTERIOR DOOR REPLACEMENT | 0324 | Three of the exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors for both utility rooms and the fire riser room with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0324ADA4 | ADA RESTROOM REMODEL | 0324 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0324INT5 | KITCHEN REMODEL | 0324 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0324SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0324 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3363
0324ENR2 | HVAC EQUIPMENT REPLACEMENT | 0324 | The HVAC system was installed in 1988 and is original to the building. It consists of two natural gas-fired furnaces and two outdoor condensers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0325ENR1 | WINDOW REPLACEMENT | 0325 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 30 units. Removal and disposal of the existing windows is included in this estimate. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0323INT4 | INTERIOR FINISHES | 0323 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 17220
0325INT3 | KITCHEN REMODEL | 0325 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0323ADA4 | ADA RESTROOM REMODEL | 0323 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 3 restrooms is necessary. This project would provide funding for construction of three unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 45000
0323SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0323 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1722
2692EXT1 | EXTERIOR FINISHES | 2692 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SRC STORAGE BUILDING | 9981 | HHS | ADSD | SRC | Sparks | 0 | 80 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80
2691EXT2 | EXTERIOR DOOR REPLACEMENTS | 2691 | The exterior wood man door and sliding barn door appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SRC MAINTENANCE SHOP | 9981 | HHS | ADSD | SRC | Sparks | 0 | 600 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2691INT1 | INSTALL BUILDING INSULATION | 2691 | This building has no insulation. The temperature extremes create an uncomfortable work environment and are contributing to accelerated decay of the maintenance equipment and supplies. This project will install batt insulation in the walls and ceiling to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | SRC MAINTENANCE SHOP | 9981 | HHS | ADSD | SRC | Sparks | 0 | 600 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100
2060EXT2 | EXTERIOR FINISHES | 2060 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EAST STORAGE AT BUILDING 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 288 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 1440
0346EXT3 | DEMOLISH STRUCTURE | 0346 | The building contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | SRC ICF/MR 6-BED HOME, BLDG #17(VACANT) | 9981 | HHS | ADSD | SRC | Sparks | 1963 | 1618 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16180
1956EXT2 | EXTERIOR FINISHES | 1956 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SOUTH STORAGE AT BUILDING 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 348 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1740
0994EXT2 | EXTERIOR FINISHES | 0994 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WEST STORAGE AT BLDG 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 360 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0994INT1 | INTERIOR FINISHES | 0994 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | WEST STORAGE AT BLDG 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 360 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0324SFT4 | FIRE RISER REPLACEMENT | 0324 | This building has an automatic fire suppression system with an older fire riser. The fire riser appears to be more than 15 years old and should be scheduled for replacement. This project recommends replacing the fire riser and any other older components of the system. Removal and disposal of the existing riser is included in the estimate. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0324INT4 | INTERIOR FINISHES | 0324 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 33625
0323ADA3 | ADA SIGNAGE | 0323 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0323INT3 | KITCHEN REMODEL | 0323 | The two kitchens are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design of one of the kitchens such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0518EXT1 | EXTERIOR FINISHES | 0518 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48290
0518INT1 | CARPET REPLACEMENT | 0518 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31500
0325INT2 | INTERIOR FINISHES | 0325 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24145
0324INT3 | INTERIOR DOOR REPLACEMENT | 0324 | The existing interior doors and frames are damaged from abuse and age. This project would provide for the removal of the existing doors and frames and the purchase and installation of new solid core wood doors and frames. All hardware and painting is included in this estimate. This estimate is for 25 doors. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0517EXT1 | EXTERIOR FINISHES | 0517 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35585
0517INT1 | INTERIOR FINISHES | 0517 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35585
0323PLM1 | WATER HEATER REPLACEMENT | 0323 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0517ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0517 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 18750
0324PLM1 | WATER HEATER REPLACEMENT | 0324 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0320ADA3 | ADA SIGNAGE | 0320 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0516ADA3 | ADA SIGNAGE | 0516 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0320ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0320 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 21000
0516ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0516 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 21000
0320SFT1 | EXIT SIGNS & EGRESS LIGHTING UPGRADE | 0320 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
0323ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0323 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 11250
0516SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0516 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
0517ADA1 | ADA SIGNAGE | 0517 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ADMINISTRATION, BLDG #605 | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 7117 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0324EXT1 | EXTERIOR FINISHES | 0324 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34440
1955INT1 | INTERIOR FINISHES | 1955 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12140
1955EXT1 | EXTERIOR FINISHES | 1955 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24280
1955INT3 | KITCHEN COUNTERTOP REPLACEMENT | 1955 | The countertops in the kitchen are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1955INT4 | JANITORS CLOSET REPAIRS | 1955 | The mop sink in the Janitors Closet has reached the end of its expected life and the adjacent gypsum board walls are showing signs of water damage. This project would provide for replacement of the sink and faucet and fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1955SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1955 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
1955ADA2 | ADA DOOR HARDWARE REPLACEMENT | 1955 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 14000
1955ADA3 | ADA SIGNAGE | 1955 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0516EXT1 | EXTERIOR FINISHES | 0516 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22480
0323EXT3 | EXTERIOR FINISHES | 0323 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34440
0320INT4 | JANITORS CLOSET REPAIRS | 0320 | The mop sink in the Janitors Closet has reached the end of its expected life and the adjacent gypsum board walls are showing signs of water damage. This project would provide for replacement of the sink and faucet and fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0320EXT1 | EXTERIOR FINISHES | 0320 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24280
0325EXT1 | EXTERIOR FINISHES | 0325 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is repairing damaged areas, power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48290
0323SFT1 | FIRE ALARM SYSTEM UPGRADE | 0323 | This building is equipped with an automatic fire detection and alarm system that is more than 15 years old and should be scheduled for replacement. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #602, 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 6725 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 15000
0320HVA1 | EXHAUST FAN REPLACEMENT | 0320 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0320PLM2 | WATER HEATER REPLACEMENT | 0320 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2691EXT1 | EXTERIOR FINISHES | 2691 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC MAINTENANCE SHOP | 9981 | HHS | ADSD | SRC | Sparks | 0 | 600 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2060INT1 | INTERIOR FINISHES | 2060 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | EAST STORAGE AT BUILDING 600-601 | 9981 | HHS | ADSD | SRC | Sparks | 1970 | 288 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0324ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0324 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
0324ADA3 | ADA SIGNAGE | 0324 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR, BLDG #603, 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1979 | 3444 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3500
0516INT4 | JANITORS CLOSET REPAIRS | 0516 | The mop sink in the Janitors Closet has reached the end of its expected life and the adjacent gypsum board walls are showing signs of water damage. This project would provide for replacement of the sink and faucet and fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0518INT3 | INTERIOR FINISHES | 0518 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24145
0518INT4 | JANITORS CLOSET REPAIRS | 0518 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0518SIT1 | REMOVE SHRUBS AND TREES | 0518 | There are several shrubs and trees that are in need of removal or trimming to prevent damage to the structure and to prevent injuries. The shrubs and trees are scratching the exterior finishes and the roots are damaging the foundation. The shrubs at the front entrance are encroaching on the walkway and can scratch people walking into the building. This project would provide for the trimming and/ or removal of the shrubs and trees near the building and along the entrance walkway. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0516ENR1 | HVAC UPGRADE | 0516 | The existing HVAC system consists of natural gas fired furnaces and split system air conditioning units. This equipment is original to the building, has required excessive maintenance in recent years and replacement parts are no longer available. This project would provide for replacing the existing equipment with new energy efficient equipment. The current design does not provide return air ducting from the sleeping rooms. This issue should be analyzed by the mechanical engineer to determine whether these returns should be installed. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36420
0518ADA3 | ADA SIGNAGE | 0518 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 1500
1955ADA4 | ADA RESTROOM REMODEL | 1955 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0518PLM1 | WATER HEATER REPLACEMENT | 0518 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0518ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0518 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR 6-BED HOME BUILDING #606 | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
1955HVA1 | EXHAUST FAN REPLACEMENT | 1955 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #325 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0516HVA1 | EXHAUST FAN REPLACEMENT | 0516 | The existing exhaust fans that serve restroom and shower areas are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0325PLM1 | WATER HEATER REPLACEMENT | 0325 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0325ADA3 | ADA SIGNAGE | 0325 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0516PLM1 | WATER HEATER REPLACEMENT | 0516 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9981PLM2 | PLUMBING UPGRADES | 9981 | The domestic and irrigation water lines do not currently have separate meters to report usage. The City of Sparks calculates their sewer fees based on the amount of water used, but the meter is currently reporting domestic water and irrigation water. The fee should be based on only the domestic water use. This project would provide for installation of water meters on each building which will report domestic use separately from irrigation. The 2013 CIP includes a project to do this work. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
0320ENR1 | HVAC UPGRADE | 0320 | The existing HVAC system consists of natural gas fired furnaces and split system air conditioning units. This equipment is original to the building, has required excessive maintenance in recent years and replacement parts are no longer available. This project would provide for replacing the existing equipment with new energy efficient equipment. The current design does not provide return air ducting from the sleeping rooms. This issue should be analyzed by the mechanical engineer to determine whether these returns should be installed. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36420
0516ADA4 | ADA RESTROOM REMODEL | 0516 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0320ADA4 | ADA RESTROOM REMODEL | 0320 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of all 5 restrooms is necessary. This project would provide funding for construction of five unisex accessible restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, paint and demolition and construction of walls. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 75000
0516INT6 | INTERIOR FINISHES | 0516 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 12140
0320INT6 | INTERIOR FINISHES | 0320 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 12140
0516INT7 | FLOORING REPLACEMENT | 0516 | The painted concrete and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be repaired or replaced. This project would provide for stripping and re-painting the concrete with an elastomeric or other water resistant paint and removal and disposal of the carpet and installation of heavy duty commercial grade carpet in the next 4-5 years. | SRC ICF/MR DUAL DIAGNOSIS, BUILDING #335 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 19424
0320INT7 | FLOORING REPLACEMENT | 0320 | The painted concrete and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be repaired or replaced. This project would provide for stripping and re-painting the concrete with an elastomeric or other water resistant paint and removal and disposal of the carpet and installation of heavy duty commercial grade carpet in the next 4-5 years. | SRC ICF/MR DUAL DIAGNOSIS BLDG #345 | 9981 | HHS | ADSD | SRC | Sparks | 1990 | 2428 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 19424
0325ADA2 | ADA DOOR HARDWARE REPLACEMENT | 0325 | The operable parts on the interior doors are round knobs which do not comply with ADA requirements. Section 309.4 of the ADA Standards for Accessible Design states that operable parts shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion thereof was previously recommended in the FCA reports dated 11/05/1999 and 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SRC BLDG #604, ICF/MR 2 6-BED HOME | 9981 | HHS | ADSD | SRC | Sparks | 1981 | 4829 | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
9981SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9981 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site-wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5-year cyclical basis to maintain the integrity of the paving and prevent premature failure. 150,000 square feet of asphalt area was used to generate this estimate. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
9981HVA1 | DIRECT DIGITAL CONTROL SYSTEM FOR HVAC SYSTEMS | 9981 | Presently the site has no DDC supervisory control or automated energy management control programs. Future HVAC considerations should include installation of appropriate hardware to connect any new buildings to the campus energy management network while maintaining local control logic. The new system should allow starting of equipment, monitoring of status, monitoring of space temperatures, monitoring and control of hot and chilled water temperatures, and similar typical centrally controlled elements. Detailed control of the individual elements of the buildings systems can yield tremendous benefits based upon the reported operating hours coupled with varying occupancy loads. The system should include a microprocessor control center which monitors and manages all components of the buildings HVAC systems. The DDC should also have the capability of controlling other building systems (such as lighting, alarms, etc.) and communicating with the central management system for the campus. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0345EXT1 | EXTERIOR FINISHES | 0345 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | MAINTENANCE SHOP 2 | 9981 | HHS | ADSD | SRC | Sparks | 1988 | 720 | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
9981SIT3 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9981 | There are nine existing light poles throughout the site. The poles are rusted and damaged and are reaching the end of their useful life. The system is problematic and replacement parts are no longer available. This project would provide for the removal and the disposal of the existing light fixtures, poles and bases and the installation of 12 new solar powered LED exterior light fixtures, 20’ poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58500
9981ENV1 | BACKFLOW PREVENTION | 9981 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. Building #600-601 does not have any type of backflow prevention between the water main and the building. This project provides for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 25000
9981ADA2 | ADA SITE UPGRADES | 9981 | Many sidewalk sections serving the buildings and parking areas are deteriorated and failing. In some areas the concrete is spalling considerably and other areas are heaving and settling due to either expansive soils or tree roots. This project addresses the removal and the replacement of the existing sidewalks as needed. 1,250 SF of 4" thick concrete sidewalk was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 12500
2693EXT2 | EXTERIOR FINISHES | 2693 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WEST STORAGE #2 | 9981 | HHS | ADSD | SRC | Sparks | 2003 | 264 | 2017-10-19 | Four to Ten Years | Long-Term Needs | 3 | 1320
9981ADA1 | ADA SIGNAGE | 9981 | The ADA provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project would provide funding for the purchase and the installation of ADA signage to include updated parking signage and directional signage from the accessible parking spaces to the accessible building entrances. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/04/1999, 08/24/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/21/2012. | SIERRA REGIONAL CENTER SITE | 9981 | HHS | ADSD | SRC | Sparks |  |  | 2017-10-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0288EXT1 | EXTERIOR FINISHES | 0288 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building including the roof is in poor shape and should be weather sealed and caulked to prevent further damage. It is recommended that this project be done within the next two years. | PUMP HOUSE | 9982 | Correct | Farm |  | Carson City | 1965 | 120 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
0288EXT2 | EXTERIOR DOOR REPLACEMENT | 0288 | The existing exterior metal door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | PUMP HOUSE | 9982 | Correct | Farm |  | Carson City | 1965 | 120 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0293EXT1 | EXTERIOR FINISHES | 0293 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 840
0293INT1 | INTERIOR FINISHES | 0293 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 840
0293EXT2 | ROOF REPLACEMENT | 0293 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2520
1447EXT1 | EXTERIOR FINISHES | 1447 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | CALVING BARN | 9982 | Correct | Farm |  | Carson City | 1998 | 1200 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2915SFT3 | FIRE ALARM INSTALLATION | 2915 | This building is not equipped with an automatic fire detection and alarm system. It is recommended that an automatic fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 10800
2915SFT2 | INSTALL EXIT SIGNS AND EGRESS LIGHTING | 2915 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency exit lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 1500
2915SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2915 | Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.910 states, that every new building owned by the State that is intended for occupancy must be equipped with an automatic fire suppression system. This project would provide funding for the installation of an automatic fire suppression system and backflow prevention. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 50400
2915INT1 | INTERIOR FINISHES | 2915 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 3600
2915EXT1 | EXTERIOR FINISHES | 2915 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | MAINTENANCE SHOP | 9982 | Correct | Farm |  | Carson City | 2004 | 3600 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 10800
1450EXT2 | WINDOW REPLACEMENT | 1450 | The windows are original, single pane construction in a metal frame. These older windows are drafty, not energy efficient and one is broken. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1450EXT1 | EXTERIOR FINISHES | 1450 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1448EXT2 | ROOF REPLACEMENT | 1448 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
1448STR1 | STRUCTURAL ASSESSMEMT | 1448 | The building was constructed in 1916 out of unreinforced masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. This project should coincide with the preservation project. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1444EXT2 | ROOF REPLACEMENT | 1444 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. This project should coincide with any projects that may be recommended by the structural assessment report project. | OLD DAIRY BARN/HAY STORAGE | 9982 | Correct | Farm |  | Carson City | 1916 | 5125 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76875
2916EXT1 | EXTERIOR FINISHES | 2916 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | A. I. BUILDING | 9982 | Correct | Farm |  | Carson City | 0 | 400 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1448EXT1 | EXTERIOR FINISHES | 1448 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1450EXT3 | EXTERIOR DOOR REPLACEMENT | 1450 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1446EXT4 | ROOF REPLACEMENT | 1446 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76545
1446STR1 | STRUCTURAL ASSESSMEMT | 1446 | The building was constructed in 1916 out of unreinforced sandstone masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1446EXT3 | WINDOW REPLACEMENT | 1446 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1446EXT2 | EXTERIOR DOOR REPLACEMENT | 1446 | The existing exterior wood doors on the carpenter shop portion appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with two new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 1000
1446EXT1 | EXTERIOR FINISHES | 1446 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | EQUIPMENT SHED | 9982 | Correct | Farm |  | Carson City | 1916 | 5103 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25515
1443EXT4 | EXTERIOR DOOR REPLACEMENT | 1443 | The building has 3 exterior metal doors and 6 exterior wood doors that have reached the end of their expected life. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 9 new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 22500
1443HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1443 | There are 2 existing wall mounted evaporative coolers that service this building. The units are not energy efficient and are approaching the end of their expected life. This project would provide for the removal of the existing coolers and replacement with one central roof top evaporative cooling unit including connections to utilities and existing duct work. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1443INT3 | FLOORING REPLACEMENT - LAB | 1443 | The VCT (vinyl composite tile) flooring in the lab room is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the existing VCT and installation of new 12x12 VCT with a 6" base. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2700
1443EXT5 | CONCRETE APRON REPLACEMENT | 1443 | The exterior concrete apron outside of the processing room has extensive cracking and is due for replacement. This project would provide for the installation of a new 120 square foot 4" thick concrete slab-on-grade apron. Removal and disposal of the existing concrete is included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1443SFT1 | FIRE ALARM INSTALLATION | 1443 | This building is not equipped with an automatic fire detection and alarm system. It is recommended that an automatic fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 7998
1448SEC1 | CONSERVE AND PROTECT BUILDING | 1448 | The building was constructed in 1916 out of unreinforced sandstone masonry. It is currently used for incidental storage and has been vandalized. The broken windows in the buildings have allowed pigeons, bats and other pests access to the building, with related health hazards and permitted rain to enter the building. The second floor is unusable due to instability of the floor/ ceiling assembly. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the buildings to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure. Roofing is addressed in a separate project. | RANCH HOUSE | 9982 | Correct | Farm |  | Carson City | 1916 | 3000 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 30000
2919ENR1 | LIGHTING UPGRADE | 2919 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | WILD HORSE OFFICE | 9982 | Correct | Farm |  | Carson City | 0 | 480 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
1444STR1 | STRUCTURAL ASSESSMEMT | 1444 | The building was constructed in 1916 out of unreinforced masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. | OLD DAIRY BARN/HAY STORAGE | 9982 | Correct | Farm |  | Carson City | 1916 | 5125 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1444EXT1 | EXTERIOR FINISHES | 1444 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | OLD DAIRY BARN/HAY STORAGE | 9982 | Correct | Farm |  | Carson City | 1916 | 5125 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25625
1450INT1 | INTERIOR FINISHES | 1450 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | YARD OFFICE | 9982 | Correct | Farm |  | Carson City | 1970 | 100 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1443ENR1 | LIGHTING UPGRADE | 1443 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7998
2919INT1 | INTERIOR FINISHES | 2919 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WILD HORSE OFFICE | 9982 | Correct | Farm |  | Carson City | 0 | 480 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2919EXT1 | EXTERIOR FINISHES | 2919 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | WILD HORSE OFFICE | 9982 | Correct | Farm |  | Carson City | 0 | 480 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2918ENR1 | LIGHTING UPGRADE | 2918 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | WILD HORSE ARENA | 9982 | Correct | Farm |  | Carson City | 0 | 10000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1443INT2 | CEILING SYSTEM UPGRADE - PROCESSING ROOM | 1443 | The processing room in this building has a suspended acoustical tile ceiling system. The t-bar framing is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
2918INT1 | INTERIOR FINISHES | 2918 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4 to 5 years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WILD HORSE ARENA | 9982 | Correct | Farm |  | Carson City | 0 | 10000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2918EXT1 | EXTERIOR FINISHES | 2918 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | WILD HORSE ARENA | 9982 | Correct | Farm |  | Carson City | 0 | 10000 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2917EXT1 | EXTERIOR FINISHES | 2917 | It is important to maintain the finish, weather resistance and appearance of the steel structure. This project would provide for painting of the steel structure and should be done on a cyclical basis based on environmental conditions. | FREE STALL BARN | 9982 | Correct | Farm |  | Carson City | 2005 | 12000 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 12000
1443EXT3 | WINDOW REPLACEMENT | 1443 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 18 units. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0293ENR1 | LIGHTING UPGRADE | 0293 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 336
9982ELE1 | ELECTRICAL DISTRIBUTION SYSTEM UPGRADE | 9982 | The electrical service was adequate for the original buildings for the site. With additional buildings and anticipated needs, the service is approaching available capacity. This project recommends upgrading the system, providing separate services and disconnects for each of the buildings, replacing the switchgear and providing additional capacity for future growth. This project or a portion thereof was previously recommended in the FCA report dated 09/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/02/2008. | NORTHERN NEVADA DAIRY FARM | 9982 | Correct | Farm |  | Carson City |  |  | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
1443EXT2 | ROOF REPLACEMENT | 1443 | The single-ply roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new single-ply roofing system. The small pop-outs around the building are covered by asphalt composition roofing shingles. These areas should be replaced as well. This estimate includes removal and disposal of the old roofing. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39990
1443INT1 | INTERIOR FINISHES | 1443 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13330
1443EXT1 | EXTERIOR FINISHES | 1443 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | DAIRY BARN | 9982 | Correct | Farm |  | Carson City | 1970 | 2666 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26660
1442EXT1 | DEMOLISH STRUCTURE | 1442 | The Chicken House is an unused wood framed structure that is in poor shape. This project would provide for the demolition of the structure including debris removal. | CHICKEN HOUSE | 9982 | Correct | Farm |  | Carson City |  | 144 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
1440EXT1 | EXTERIOR FINISHES | 1440 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | BULL BARN | 9982 | Correct | Farm |  | Carson City | 1930 | 1050 | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
0293EXT3 | EXTERIOR DOOR REPLACEMENT | 0293 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with two new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | BREAK ROOM | 9982 | Correct | Farm |  | Carson City | 1970 | 168 | 2008-09-02 | Four to Ten Years | Long-Term Needs | 3 | 1000
1440STR1 | STRUCTURAL ASSESSMEMT | 1440 | The building was constructed in 1916 out of unreinforced sandstone masonry. The walls are showing signs of failure including cracking, settling and crumbling. This project would provide for an investigation and assessment to be done by a licensed Structural Engineer to identify possible deficiencies and problems in the building and provide a report outlining issues and resolutions. Future projects may result from this report and are not included in this estimate. | BULL BARN | 9982 | Correct | Farm |  | Carson City | 1930 | 1050 | 2008-09-02 | Immediate to Two Years | Currently Critical | 1 | 5000
9982SIT2 | WELL EVALUATION AND ABANDONMENT | 9982 | There are wells on this site that are no longer in use. The Division of Water Resources (DRW) requires that these wells be plugged as not to allow a conduit for ground water contamination. The costs to plug the wells depend on the depth of the wells and the casing size. Preliminary estimates run around $45.00 per foot to plug the wells estimating that it around 200 feet deep. NAC 534.427 was referenced for this project. Three wells with 8" casings were used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/02/2008. | NORTHERN NEVADA DAIRY FARM | 9982 | Correct | Farm |  | Carson City |  |  | 2008-09-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
2007INT3 | INTERIOR FINISHES | 2007 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9375
2007HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2007 | This building is cooled by two evaporative coolers, one on grade on the north side and one on the roof. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Four to Ten Years | Long-Term Needs | 3 | 8000
2007EXT2 | EXTERIOR FINISHES | 2007 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Four to Ten Years | Long-Term Needs | 3 | 18750
2007EXT1 | REPLACE ROOF | 2007 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/12/2008. | NDF ADMINISTRATION BUILDING | 9984 | CNR | Forestry |  | Carson City | 1994 | 1875 | 2008-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
9984SIT2 | LANDSCAPE IMPROVEMENTS | 9984 | A large portion of the site is not covered by vegetation or rock and is a constant maintenance problem. The wind and water causes the dirt to erode which then must be replaced once a year in order to maintain the grade and protect the buildings. This project recommends covering the dirt areas with grass including an irrigation system. Another alternative could include planting of shrubs as a wind break. Xeriscaping may be another method but due to security concerns, having cobblestone or other objects in the landscaping may pose a risk to inmates and staff. | STEWART CONSERVATION CAMP | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2014HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2014 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2015INT4 | INTERIOR FINISHES | 2015 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2015EXT2 | EXTERIOR FINISHES | 2015 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2015ADA2 | RESTROOM REMODEL | 2015 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2834EXT1 | EXTERIOR FINISHES | 2834 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | PHONE RAMADA | 9984 | Correct | SCC |  | Carson City | 2000 | 170 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 340
9984HVA1 | UPDATE WATER TREATMENT SYSTEM | 9984 | The chemical water treatment and water softener systems throughout the camp are in good condition, but some were not operating and others did not receive regular maintenance. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $15,000 fee is suggested. | STEWART CONSERVATION CAMP | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 15000
2013ADA1 | RESTROOM REMODEL | 2013 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
9984SFT1 | FIRE SPRINKLER SUPPLY LINE REPLACEMENT | 9984 | The main fire sprinkler supply line servicing the campus has rusted and is due for replacement. Staff reported that they recently replaced a portion of the buried piping and visual inspection revealed that the entire line is beginning to fail. This project would provide funds to remove the existing piping and replace it with a new line. The estimate includes disposal of the existing materials, excavation, backfill, etc.. Backflow prevention replacement is included in this estimate. | STEWART CONSERVATION CAMP | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 225000
2013EXT2 | EXTERIOR FINISHES | 2013 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2015HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2015 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2014ADA1 | RESTROOM REMODEL | 2014 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2013INT3 | INTERIOR FINISHES | 2013 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2010EXT2 | EXTERIOR FINISHES | 2010 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 37500
2008SFT1 | REPLACE STAIR HANDRAILS | 2008 | There is a set of stairs which lead to an upper level storage area in the NDF portion of the building. The existing wood framed handrails at the stairs do not meet the requirements of the 2006 IBC. This project would provide for the installation of handrails in accordance with the 2006 IBC Chapter 10, Section 1012. | MULTI-USE BUILDING | 9984 | Correct | SCC |  | Carson City | 1994 | 7000 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 1200
2010ELE2 | MISCELLANEOUS ELECTRICAL REPAIRS | 2010 | The electrical subpanel has some broken circuit breaker safety caps and is not properly labeled. There is an electrical cord from the walk-in coolers ran through the wall into a damaged duplex outlet located in the dry storage room. This project would provide the repairs necessary to bring these items into compliance with codes and adopted standards. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 500
2010ELE1 | REPLACE WALL MOUNTED ELECTRICAL HEATER | 2010 | The existing wall mounted electric baseboard heater is damaged and inoperable. This project would provide for the removal and replacement of the heater. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 1000
2008INT3 | INTERIOR FINISHES | 2008 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-USE BUILDING | 9984 | Correct | SCC |  | Carson City | 1994 | 7000 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2008EXT2 | EXTERIOR FINISHES | 2008 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | MULTI-USE BUILDING | 9984 | Correct | SCC |  | Carson City | 1994 | 7000 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 70000
2009HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2009 | This building is cooled by an evaporative cooler located on grade on the south side of the building. This unit will reach the end of its expected life in the next 8 to 10 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 4000
2009INT3 | INTERIOR FINISHES | 2009 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9375
2009EXT2 | EXTERIOR FINISHES | 2009 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 18750
2010HVA2 | HVAC SYSTEM REPLACEMENT | 2010 | The building is heated by two roof-top furnaces and cooled by one air conditioner on grade. One of the heating units has been decommissioned in order to provide parts for the other unit. In turn, the ducting has been re-routed to accommodate for the loss of one unit. This equipment is original to the building and has reached the end of its expected life. This project recommends replacing the roof-top heaters, the air conditioning condenser unit and routing the ductwork back to the original design. The estimate includes removal and disposal of the existing equipment. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 120000
2010ADA1 | ADA RESTROOM UPGRADE | 2010 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restroom, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 25000
2010INT4 | KITCHEN EQUIPMENT UPGRADE | 2010 | The kitchen cooking equipment is original to the building and is reaching the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next two to three years, including the Baxter oven, refrigerator and freezer equipment and the Mars Air Door unit on the back door. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. This estimate is a lump some for budgeting purposes. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9984SFT3 | FIRE ALARM INSPECTION | 9984 | The fire alarm system was not operating at the time of the survey. The reason for the malfunction was not known at the time of the survey and the maintenance staff explained that there is no funding to repair the system. This project would provide funding for an inspection of the system by a certified fire alarm equipment inspector to determine the cause of the problem. Any future projects would come from report recommendations. | STEWART CONSERVATION CAMP | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
2010INT1 | INTERIOR FINISHES | 2010 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
2010INT5 | REPLACE VINYL COMPOSITION TILE | 2010 | The existing vinyl composition tile (VCT) in the dining, corridors and storage areas is extremely worn, damaged and should be replaced. This project would provide for the removal and replacement of the VCT. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15400
2011HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2011 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2011ADA1 | RESTROOM REMODEL | 2011 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2011INT2 | INTERIOR FINISHES | 2011 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2011EXT2 | EXTERIOR FINISHES | 2011 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2012HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2012 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2012ADA1 | RESTROOM REMODEL | 2012 | The restroom and shower room are in overall poor condition. The countertops in each room show signs of wear and deterioration. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. The tile on the floors and walls of the bathrooms are damaged and worn and should be replaced. This project provides for a complete remodel of the restroom and shower room which should include an ADA compliant toilet stall, shower and sink with all ADA complaint fixtures. The existing exhaust fans are undersized and should be replaced with commercial grade exhaust fans. The removal and disposal of the old fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 275000
2012INT3 | INTERIOR FINISHES | 2012 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2012EXT2 | EXTERIOR FINISHES | 2012 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2013HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2013 | This building is cooled by three roof mounted evaporative coolers. This equipment will reach the end of its expected life in the next 5 to 6 years and should be scheduled for replacement in that time frame. The estimate includes removal and disposal of the existing equipment. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 12000
2014INT3 | INTERIOR FINISHES | 2014 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19600
2014EXT2 | EXTERIOR FINISHES | 2014 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Four to Ten Years | Long-Term Needs | 3 | 39200
2010INT3 | SUSPENDED ACOUSTICAL CEILING TILE REPLACEMENT | 2010 | The Dining space in this building has a suspended acoustical ceiling tile system. The system is original to the building and has reached the end of its expected life. The metal frame is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project recommends replacing the suspended acoustical ceiling tile system including the tiles. Removal and disposal of the existing ceiling system is included in this estimate. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2012EXT1 | REPLACE ROOF | 2012 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 02 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2015EXT1 | REPLACE ROOF | 2015 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2014EXT1 | REPLACE ROOF | 2014 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 04 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2013EXT1 | REPLACE ROOF | 2013 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 03 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2011EXT1 | REPLACE ROOF | 2011 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | HOUSING UNIT 01 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39200
2010EXT1 | REPLACE ROOF | 2010 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | CULINARY/DINING | 9984 | Correct | SCC |  | Carson City | 1994 | 3750 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
9984SIT1 | SLURRY SEAL ASPHALT PAVING | 9984 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 80,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | STEWART CONSERVATION CAMP | 9984 | Correct | SCC |  | Carson City | 1994 | 0 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
2015ADA1 | REMOVE WATER FOUNTAIN | 2015 | This building has a water fountain which is not ADA accessible, damaged and is very rarely used. This project recommends permanently removing the water fountain. | HOUSING UNIT 05 | 9984 | Correct | SCC |  | Carson City | 1994 | 3920 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2009EXT1 | REPLACE ROOF | 2009 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. This project or a portion thereof was previously recommended in the FCA report dated 8/22/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2008. | CONTROL ROOM | 9984 | Correct | SCC |  | Carson City | 1994 | 1875 | 2008-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
0340INT2 | INTERIOR FINISHES | 0340 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 6-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 129195
0347ELE1 | ELECTRICAL EQUIPMENT REPLACEMENT | 0347 | The main electrical switchgear in the building is over 30 years old and should be scheduled for replacement. Staff noted at the time of the survey that the equipment will cost between $250,000 and $500,000 to replace. The equipment was working at the time of the survey, but it is vital to the needs of the campus and therefore should be scheduled for replacement. This project would replace the main switchgear and associated electrical equipment in the building. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
0352EXT2 | EXTERIOR FINISHES | 0352 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the wood panels, soffits and eaves and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27415
0353SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0353 | The building is a B and S-2 occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 100996
0326ADA10 | ELEVATOR INSTALLATION | 0326 | There is no elevator in the building to provide an accessible path of travel to the 2nd floor. This building is required to have an accessible path of travel to the 2nd floor if an employee with disabilities is stationed on the 2nd floor per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible elevator to be installed to access the 2nd floor of the building. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 250000
0353EXT3 | GUTTER AND DOWNSPOUT INSTALLATION | 0353 | The building only has gutters over entrances and those gutters are damaged and not functioning properly. Currently, the water sheet drain off of the single ply and metal roofing causing erosion to the asphalt and concrete at grade. There are also areas where the runoff pools up near the building causing premature deterioration to the building and creating slip and fall areas during inclement weather. This project would provide funding for the installation of a seamless gutter and downspout system for the building which ties into the site storm system. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0353ENR3 | WATER HEATER REPLACEMENT | 0353 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed for more efficient use of energy. This estimate includes: 50 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0353ENR2 | COOLING EQUIPMENT REPLACEMENT | 0353 | The building is cooled by a combination of roof mounted and wall mounted evaporative coolers and wall mounted air conditioners. All of these units are older and not energy efficient. This project would provide for replacing all of this equipment with new, more energy efficient roof mounted cooling equipment and installing new ducting to non-conditioned spaces. The estimate includes removal and disposal of the old equipment. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0353ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0353 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0353ADA3 | ADA SIGNAGE | 0353 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
0328ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0328 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
1958EXT2 | EXTERIOR FINISHES | 1958 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, sanding, priming and painting the wood soffits and fascia and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7620
0340EXT3 | EXTERIOR FINISHES | 0340 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the painted finishes and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129195
2449INT1 | INTERIOR FINISHES | 2449 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DINI-TOWNSEND HOSPITAL- BUILDING #25 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2000 | 59040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 295200
0340ENR2 | WINDOW REPLACEMENT | 0340 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 85 units. Removal and disposal of the existing windows is included in this estimate. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
9985ELE1 | SITE ELECTRICAL UPGRADE | 9985 | The site's electrical distribution system is a mix of old direct buried 4180 volt cable and newer 4180 volt cable in conduit where remodels or upgrades have occurred over the years. The main switchgear and transformers at the emergency generator have reached the end of there useful life and are in need of replacement. This project would provide for a complete upgrade and replacement of 4180 volt cable in conduit where direct buried cable is present from the main switchgear including new transformers, switchgear, trenching and backfill, new conduit to all existing buildings on site. Removal of the old existing cable and equipment is included in this estimate. Individual building electrical upgrades are not included in this estimate. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1850000
0327EXT3 | EXTERIOR FINISHES | 0327 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49195
0327EXT4 | SOFFIT REPLACEMENT | 0327 | The exterior soffits around the building are weather beaten, broken and are showing signs of considerable wear. It appears that this type of suspended ceiling soffit is not holding up well against the inclement weather in this climate. This project would provide funding to replace the soffits with a more durable system. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0327EXT5 | ROOF REPLACEMENT | 0327 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed over 20 years ago. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118068
0327INT2 | JANITORS CLOSET REPAIRS | 0327 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0327PLM1 | WATER HEATER REPLACEMENT | 0327 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 3750
0328ADA5 | LEVER HARDWARE INSTALLATION | 0328 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0328ENR2 | HVAC EQUIPMENT REPLACEMENT | 0328 | The roof mounted HVAC unit was installed in 1999 and should be scheduled for replacement. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC unit and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 83835
0343ADA3 | ADA RESTROOM REMODEL | 0343 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0328ADA3 | ADA SIGNAGE | 0328 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0328ADA2 | ADA RESTROOM UPGRADE | 0328 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0328INT3 | CEILING SYSTEM REPLACEMENT | 0328 | The Meeting Room on the north side of the building has a suspended acoustical tile ceiling system that is old and should be scheduled for replacement. The t-bar framing is bent in some areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0328ENR1 | WINDOW REPLACEMENT | 0328 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 20 units. Removal and disposal of the existing windows is included in this estimate. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0328INT2 | INTERIOR FINISHES | 0328 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27945
0328EXT5 | EXTERIOR FINISHES | 0328 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 27945
0331ADA6 | ADA SIGNAGE | 0331 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
0331ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0331 | This building contains a water fountain on each floor. The 1st and 2nd floor drinking fountains are not accessible. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of two new accessible fixed high/ low ADA drinking fountains for the 1st and 2nd floor. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0329INT4 | CEILING SYSTEM REPLACEMENT | 0329 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144000
0329EXT8 | EXTERIOR FINISHES | 0329 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and concrete accents and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 96625
0353ADA2 | ADA RESTROOM UPGRADE | 0353 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 20000
0343INT1 | FLOORING REPLACEMENT | 0343 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12702
0340ADA2 | ADA RESTROOM UPGRADE | 0340 | The Adolescent Services section of the building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0343EXT1 | EXTERIOR FINISHES | 0343 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the unpainted walls, painting the painted walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10585
0326ADA9 | ADA SIGNAGE | 0326 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1958ADA1 | ADA UPGRADES | 1958 | The building does not have an accessible entrance and restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements and a complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom and an ADA accessible ramp and entrance door / hardware. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 25000
0347EXT2 | EXTERIOR FINISHES | 0347 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8820
0348ADA1 | ADA RESTROOM UPGRADE | 0348 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0348ENR1 | WINDOW REPLACEMENT | 0348 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0348EXT3 | EXTERIOR FINISHES | 0348 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48210
0352ENR1 | HVAC EQUIPMENT REPLACEMENT | 0352 | The HVAC system has been converted from the central plant steam system to a temporary boiler and chiller with a cooling tower. Funding has been approved to replace the existing chiller and cooling tower, but had not been done at the time of the most recent survey. The large air handler in the basement is also scheduled to be replaced, but was still there in 2012. This project recommends installing a new HVAC system for the building with more energy efficient equipment controlled by an energy management system. The estimate includes removal and disposal of the existing HVAC units and all required connections to utilities. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0352PLM1 | WATER HEATER REPLACEMENT | 0352 | There is a 50 gallon electric water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 50 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 3750
0352INT3 | INTERIOR FINISHES | 0352 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 27415
0326INT8 | JANITORS CLOSET REPAIRS | 0326 | The mop sink in the Janitors Closet in Room 119 is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0329EXT7 | EXTERIOR DOOR REPLACEMENT | 0329 | There are six exterior metal doors that are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of six metal door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. The storefront door and window systems are not included in this project. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0326ADA8 | DRINKING FOUNTAIN REPLACEMENT | 0326 | This building contains water fountains on each floor that are not ADA compliant. The 2006 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0334INT2 | KITCHEN REMODEL | 0334 | The two kitchens are in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0333EXT5 | SKYLIGHT REPLACEMENT | 0333 | There are two 8’x8’ acrylic sky-lights located on the roof. Both units have cracks in them that are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of two acrylic skylight units. Minor roof repairs are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0330ENR2 | WINDOW REPLACEMENT | 0330 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 40 units. Removal and disposal of the existing windows is included in this estimate. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0340EXT4 | EXTERIOR DOOR REPLACEMENT | 0340 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of all of the exterior metal man door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0330ADA1 | ADA RESTROOM REMODEL | 0330 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0326INT6 | RESTROOM REMODEL | 0326 | The eight restrooms in the north and south wings of the building are over 30 years old and in overall poor condition. The finishes, fixtures, cabinets, partitions, toilets and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
0333INT2 | KITCHEN REMODEL | 0333 | The two kitchens are in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0326ADA7 | BREAK ROOM REMODEL | 0326 | The kitchenette and associated cabinets in the four employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 16000
0330EXT5 | EXTERIOR FINISHES | 0330 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 26185
9985PLM1 | SITE DOMESTIC WATER LINE REPLACEMENT | 9985 | The existing domestic water supply lines and main feeding the campus are aged and should be scheduled for replacement. there have been numerous leaks and the system has been problematic due to age. This project would provide for the complete replacement of the domestic water supply system including trenching, backfill, grading and required backflow prevention. to each occupied building on site. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2100000
0331EXT6 | EXTERIOR FINISHES | 0331 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and concrete accents and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76720
0331EXT7 | EXTERIOR DOOR REPLACEMENT | 0331 | There are four exterior metal doors that are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of four metal door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. The storefront door and window systems are not included in this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0331INT2 | FLOORING REPLACEMENT | 0331 | The VCT (vinyl composite tile), sheet vinyl and ceramic tile in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. Asbestos testing and abatement is NOT included in this estimate if required. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 122752
0331INT3 | CEILING SYSTEM REPLACEMENT | 0331 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
0331ADA2 | ADA RESTROOM UPGRADE | 0331 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling one Men's and one Women's restrooms into ADA compliant restrooms. The items to be addressed may include sinks, toilets, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 60000
0326INT7 | SHOWER ROOM REMODEL | 0326 | The Men's and Women's shower rooms on the 2nd floor are over 30 years old and in overall poor condition. The finishes, fixtures and exhaust fans are showing signs of severe wear and deterioration. This project would provide for a complete remodel of the shower rooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. If it is deemed unnecessary to provide shower facilities in the building, it is recommended to remove the showers and remodel the rooms into storage rooms or offices. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0326EXT4 | EXTERIOR FINISHES | 0326 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and concrete accents and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 136870
0334ENR2 | WINDOW REPLACEMENT | 0334 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 40 units. Removal and disposal of the existing windows is included in this estimate. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0343SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0343 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0334EXT5 | EXTERIOR FINISHES | 0334 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 26185
0340PLM1 | WATER HEATER REPLACEMENT | 0340 | There are two 80 gallon gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that two new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0340ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0340 | The Adolescent Services section of the building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0326EXT5 | EXTERIOR DOOR REPLACEMENT | 0326 | The storefront system at the entrance and the exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the storefront system and all of the metal man doors except the new ADA door on the east side of the building with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0334ADA1 | ADA RESTROOM REMODEL | 0334 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0333EXT4 | EXTERIOR FINISHES | 0333 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0326INT5 | INTERIOR DOOR REPLACEMENT | 0326 | Five of the interior doors in this building are damaged and do not operate properly. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 5 interior doors was used in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0326ADA6 | ADA RESTROOM UPGRADE | 0326 | The staff restrooms near the Lobby do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0333ENR2 | WINDOW REPLACEMENT | 0333 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 40 units. Removal and disposal of the existing windows is included in this estimate. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0333ADA5 | ADA RESTROOM REMODEL | 0333 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
0330INT2 | KITCHEN REMODEL | 0330 | The two kitchens are in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0331ADA4 | ELEVATOR REPAIRS | 0331 | This building has an elevator, but it has been out of service for some time, and it does not comply with ADA standards. This project would provide funding to repair the elevator to improve maintenance, facilitate control of this building and comply with the ICC/ANSI A117.1998 Section 407. These repairs are to include but not limited to updating the control panel, door reversing light beams, call button, hall station upgrades, and a hands-free telephone. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0340INT3 | CARPET REPLACEMENT | 0340 | The carpet in the Adolescent Services section of the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. The estimate is based on replacing approximately 6,000 square feet of carpet. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0326INT4 | CEILING SYSTEM REPLACEMENT | 0326 | The 2nd floor of this building has a suspended acoustical tile ceiling system. The t-bar framing is bent and damaged in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104000
0326EXT1 | ROOF REPLACEMENT | 0326 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed over 20 years ago. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 168000
0327INT3 | INTERIOR FINISHES | 0327 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49195
9985SIT3 | CONCRETE AND PAVING UPGRADE SITEWIDE | 9985 | The site has a mix of PC concrete and asphalt concrete roads, parking lots and pedestrian paths. Many areas are damaged and have settled which have created incorrect slopes and trip hazards. There are limited ADA parking spaces and accessible routes to the public entrances. Some buildings have been recently demolished and may be ideal locations for new parking lots, circulation roads or accessible paths of travel. Additional parking is also necessary to accommodate growing outpatient caseloads and staff. This project would provide for repairing or replacing existing paving and installing new paving including all necessary accessibility upgrades based on a professionally designed sitewide plan. This project should be implemented concurrently with the LANDSCAPE UPGRADES project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 850000
0352SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0352 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MEDICATION CLINIC - BUILDING #5 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1967 | 5483 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
0329HVA1 | HVAC EQUIPMENT REPLACEMENT | 0329 | The HVAC system was installed over 30 years ago and should be scheduled for replacement. It consists of roof mounted heat pumps which cause consistent maintenance problems. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 386500
0329ADA3 | ADA UPGRADES | 0329 | Restrooms are present in this building. They do not fully meet the Americans with Disabilities Act (ADA) regulations. One existing restroom is designated as an ADA restroom but it does not comply. The minimum turning radius required cannot be achieved in the current configuration. The staff restroom should be converted to an ADA accessible unisex restroom with all new fixtures. This would be the most economical. The second level Men's and Women's restrooms do not comply and either do the showers. These restrooms should be remodeled for compliance to ADA accessibility requirements. This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. It is recommended this fountain be replaced. Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be replaced and/or relocated to comply with ADA requirements. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 150000
0329SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0329 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0331SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0331 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0326HVA1 | HVAC EQUIPMENT REPLACEMENT | 0326 | The four HVAC roof top units were installed over 25 years ago. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of four new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 410610
0331INT1 | INTERIOR FINISHES | 0331 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76720
0343ENR1 | HVAC EQUIPMENT REPLACEMENT | 0343 | The existing HVAC system consists of wall mounted hydronic heaters and window mounted evaporative coolers. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas-fired heating as well as air conditioning. Ducting and vents will need to be installed in either the attic or the crawlspace as well. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1958SFT1 | SMOKE DETECTOR INSTALLATION | 1958 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0340ELE1 | LIGHTING UPGRADE | 0340 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 10/28/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2006. Project complete. | BUILDING #8 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1958 | 25839 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
1958ENR2 | HVAC EQUIPMENT REPLACEMENT | 1958 | The existing HVAC system consists of wall mounted hydronic heaters and window mounted evaporative coolers. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas-fired heating as well as air conditioning. Ducting and vents will need to be installed in either the attic or the crawlspace as well. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0326SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0326 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7000
0326EXT2 | WINDOW REPLACEMENT | 0326 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 250 units. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0328SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0328 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
0343INT2 | INTERIOR FINISHES | 0343 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10585
0353SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0353 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 3607
0327SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0327 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0327INT4 | FLOORING REPLACEMENT | 0327 | The sheet vinyl flooring in the gymnasium is damaged and reaching the end of its useful life. The gymnasium is the main indoor recreational facility on the site. It is a multi-purpose room where games can be played or different types of gatherings may occur. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0343ADA1 | ADA INTERIOR UPGRADE | 0343 | The family room in this building is accessed by stepping down two steps. A physically challenged person cannot access the kitchen or living room from the family room. It is recommended that an ADA compliant ramp be installed in place of the steps. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 10000
0329EXT1 | WINDOW REPLACEMENT | 0329 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. Staff reported that these windows are difficult to open and do not seal properly. Several windows allow water to penetrate to the interior. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 100 units including costs associated with a two story structure. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0329INT3 | JANITORS CLOSET REPAIRS | 0329 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2800
0326ELE2 | ELECTRICAL UPGRADE | 0326 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. Numerous safety issues including non-GFCI outlets in restrooms or near sinks, missing duplex covers and painted receptacles are present. It is recommended the entire system be upgraded to meet the evolving needs of the building including a comprehensive rewiring and replacement of outdated and failing outlets, switches and panels, and adding additional capacity for anticipated needs. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2004 and 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 547480
2725ADA1 | ADA RESTROOM UPGRADES | 2725 | The designated Men's and Women's ADA accessible restrooms are not fully compliant with the adopted codes. The toilet seat cover dispensers are not in the correct location, the men's toilet seat handle is on the wrong side and the toilet seats do not have the required open-front and elongated shape. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | CENTRAL KITCHEN - BUILDING #26 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2007 | 4626 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
2725EXT1 | EXTERIOR FINISHES | 2725 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CENTRAL KITCHEN - BUILDING #26 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2007 | 4626 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23130
2725INT1 | INTERIOR FINISHES | 2725 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CENTRAL KITCHEN - BUILDING #26 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2007 | 4626 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 23130
2449EXT3 | EXTERIOR FINISHES | 2449 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing the exterior, priming and painting the stucco, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DINI-TOWNSEND HOSPITAL- BUILDING #25 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2000 | 59040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 295200
0347SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0347 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0330ADA4 | ADA SIGNAGE | 0330 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
0347SIT1 | BOLLARD INSTALLATION | 0347 | There is a 2,000 gallon diesel tank above ground with no bollards for protection. This project would provide funding for 4 eight inch diameter bollards filled with concrete to be located on each corner of the tank. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0348SFT2 | EGRESS DOOR HARDWARE UPGRADE | 0348 | The egress door located on north west side of the building was locked shut from the inside with deadbolt hardware. IBC 2006 section 1008.1.8.4 prohibits manually operated flush bolts or surface bolts on egress doors. This project would provide for the purchase and installation of emergency panic hardware to be installed on the door and removing the deadbolt locking hardware. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
0330ADA3 | LEVER HARDWARE INSTALLATION | 0330 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project would provide for the purchase and installation of 15 lever action hardware to be placed on all the interior doors. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0330HVA3 | HVAC EQUIPMENT REPLACEMENT | 0330 | The HVAC system was installed in 1999 and should be scheduled for replacement. It consists of roof mounted packaged units and window mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. Also, the air conditioner compressor is not functioning. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 78555
0330EXT4 | SKYLIGHT REPLACEMENT | 0330 | There are two 8’x8’ acrylic sky-lights located on the roof. Both units have cracks in them that are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of two acrylic skylight units. Minor roof repairs are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0330EXT2 | ROOF CLEANING / REPAIRS | 0330 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. This project applies to the single-ply membrane portion of the roof. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
0353ELE2 | ELECTRICAL UPGRADE | 0353 | This building was constructed before the high demand for electrical services were needed for computers, shop tools, life safety equipment and other electrical devices. As time has progressed, the buildings electrical demand has changed and numerous alterations and additions have been made to the existing electrical system. There are also numerous outlets and switches which are broken or missing proper covers. It is recommended the entire system be upgraded to meet the evolving needs of the building and to bring all components of the system up to current codes. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144280
0328EXT4 | ROOF REPLACEMENT | 0328 | The single ply membrane roof and the wood shingle roof on this building were in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single ply membrane and a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LIBRARY/MEETING ROOMS - BUILDING #2A | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5589 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67068
0327ELE2 | ELECTRICAL UPGRADE | 0327 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. Numerous safety issues, missing duplex covers, and painted receptacles are present. It is recommended the entire system be upgraded to meet the evolving needs of the building including a comprehensive rewiring and replacement of outdated and failing outlets, switches and panels, and adding additional capacity for anticipated needs. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 196780
2449EXT2 | ROOF REPLACEMENT | 2449 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average single-ply roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that this buildings single-ply roofing be replaced in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. This project does not apply to the asphalt composition shingle roofing. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | DINI-TOWNSEND HOSPITAL- BUILDING #25 | 9985 | HHS | DPBH | NNAMHS | Sparks | 2000 | 59040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
1958STR2 | PATIO STRUCTURE REPLACEMENT | 1958 | There is a wood framed patio structure attached to the east side of the house. The wood structure, especially the roof framing is deteriorating and is showing signs of sagging and dry rot. The 4x4 wood posts are also deteriorating, particularly at the connection to the concrete foundation. This project would provide for the removal and replacement of this patio cover including a new asphalt composition roof to match the main home. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1958ENR1 | WINDOW REPLACEMENT | 1958 | The windows are older dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12100
0329EXT6 | ROOF CLEANING / REPAIRS | 0329 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
0353EXT2 | OVERHEAD DOOR REPLACEMENT | 0353 | The existing overhead coiling doors, (2) 10' X 10', (1) 7' X10 and (1) 8' X 7', are original to the building. They are all damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish and some minor collisions have occurred. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20800
0329INT2 | FLOORING REPLACEMENT | 0329 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. Additional costs are included for the possibility of asbestos abatement. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 193250
0327HVA3 | HVAC REPLACEMENT | 0327 | The roof top air handlers are more than 30 years old. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new multi-zone air handling units and two new single-zone air handling units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This work is currently recommended for the 2013 Capitol Improvement Program. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | CANTEEN - DROP-IN CENTER - BUILDING #2 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 11828 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0348EXT2 | ROOF REPLACEMENT | 0348 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115704
2678EXT1 | EXTERIOR FINISHES | 2678 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining of the wood structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | KIOSK | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 36 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180
9985SIT4 | SANITARY SEWER LINE REPLACEMENT | 9985 | The sanitary wastewater system is showing signs of deterioration. Because of the deterioration, the system is not working to its full potential. Some of the lines are original to the site and are in fair to poor condition. The passage of time and constant heavy use are contributing factors to problems that arise. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. This project would provide for the complete replacement of the sanitary sewer system on site from the city connection to each occupied building on site. This project or a portion there of was previously recommended in the FCA report dated 11/03/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/26/2006. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500000
0521EXT3 | DEMOLISH STRUCTURE | 0521 | The Gazebo Restroom building is dilapidated and deteriorating and has reached the end of its useful life. It has been locked up and not used for several years and is no longer useful since the Dini-Townsend Hospital was built. This project would provide funding for the demolition of the building. | GAZEBO RESTROOM - BUILDING #27 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1976 | 160 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
0331ELE2 | ELECTRICAL UPGRADE | 0331 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. The electrical system within the building has been retrofitted and rewired as the needs of the agency have changed over the years. There are numerous safety issues, missing duplex covers, and painted receptacles that need to be repaired. It is recommended the entire system be upgraded to meet the evolving needs of the building including rewiring, replacing switches and panels and adding additional capacity. This project or a portion thereof was previously recommended in the FCA reports dated 10/2701999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 383600
0353ENR1 | WINDOW REPLACEMENT | 0353 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0330EXT3 | ROOF HATCH | 0330 | The roof hatch is broken and needs to be replaced. This project would provide for the purchase and installation of a new roof hatch. This estimate includes removal and disposal of the existing damaged hatch and any patching and / or repairs to the roof membrane. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0333ADA3 | LEVER HARDWARE INSTALLATION | 0333 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project would provide for the purchase and installation of 15 lever action hardware to be placed on all the interior doors. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0333HVA2 | HVAC EQUIPMENT REPLACEMENT | 0333 | The HVAC system was installed in 1999 and should be scheduled for replacement. It consists of roof mounted packaged units and window mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52237
0331EXT4 | ROOF CLEANING / REPAIRS | 0331 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. This project applies to the single-ply membrane portion of the roof. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
1958INT1 | INTERIOR FINISHES | 1958 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #14 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1951 | 1524 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7620
0347LGT1 | LONG TERM NEEDS | 0347 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement Projects related to maintenance and is based on a 10 year planning cycle. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project or a portion there of was previously recommended in the FCA report dated 10/29/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/29/2006. Reassigned to more specific projects. | GENERATOR BUILDING - BUILDING #20 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 1764 | 2017-10-18 | Four to Ten Years | Long-Term Needs | 3 | 18000
9985SIT1 | LANDSCAPE UPGRADES | 9985 | The landscaping sitewide is in fair condition, but there are several areas that are due for upgrades. The existing galvanized landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. This old piping breaks often and very likely has underground leaks that are unknown at this point. There are concrete benches and planters around the site that have deteriorated, some to the point of exposing the metal rebar, which should be repaired or replaced. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines and repair or replacement of the damaged concrete benches and planters. 6,000 linear feet of irrigation piping was used to generate this estimate. This project should be implemented concurrently with the CONCRETE AND PAVING UPGRADE SITEWIDE project. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0348INT1 | INTERIOR FINISHES | 0348 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | WAREHOUSE/PURCHASING - BUILDING #21 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1971 | 9642 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0326ADA2 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0326 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports at three separate flights of stairs. Removal and disposal of the existing railing is included. NRS 338.180, 2006 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 25000
0331EXT5 | WINDOW REPLACEMENT | 0331 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. Staff reported that these windows are difficult to open and do not seal properly. Several windows allow water to penetrate to the interior. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 100 units including costs associated with a two story structure. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | LAB/PHARMACY - BUILDING #3 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1925 | 15344 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0329INT1 | INTERIOR FINISHES | 0329 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/27/1999 and 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | BUILDING #4 (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1961 | 19325 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 96625
0330INT1 | INTERIOR FINISHES | 0330 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8A | 9985 | HHS | DCFS | NNCAS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0343SFT1 | SMOKE DETECTOR INSTALLATION | 0343 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0343ENR2 | WINDOW REPLACEMENT | 0343 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. Some of the windows have broken seals and are difficult to operate. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 17 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/05/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
0333INT1 | INTERIOR FINISHES | 0333 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0353INT1 | INTERIOR FINISHES | 0353 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 11/02/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/29/2006. | MAINTENANCE/HOUSEKEEPING BUILDING #22 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1959 | 8040 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36070
0333EXT3 | ROOF HATCH | 0333 | The roof hatch is broken and needs to be replaced. This project would provide for the purchase and installation of a new roof hatch. This estimate includes removal and disposal of the existing damaged hatch and any patching and / or repairs to the roof membrane. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2677EXT1 | EXTERIOR FINISHES | 2677 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | PARKING RAMADA | 9985 | HHS | DPBH | NNAMHS | Sparks | 1980 | 512 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1024
0334INT1 | INTERIOR FINISHES | 0334 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 10/29/1999 and 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26185
0343ADA2 | ACCESSIBLE BUILDING ENTRANCE | 0343 | The building has steps leading into the main entrance which do not comply with accessibility requirements and are missing handrails. The entry door has a threshold and hardware that do not meet the requirements for accessibility. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building, handrails, curbing, and replacement of the door hardware and threshold to meet the ADA Accessibility Guidelines. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #15 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1949 | 2117 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 35000
0334HVA3 | HVAC EQUIPMENT REPLACEMENT | 0334 | The HVAC system was installed in 1999 and should be scheduled for replacement. It consists of roof mounted packaged units and window mounted evaporative coolers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52370
0334ADA3 | LEVER HARDWARE INSTALLATION | 0334 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project would provide for the purchase and installation of 15 lever action hardware to be placed on all the interior doors. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0334ADA4 | ADA SIGNAGE | 0334 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
2059EXT3 | EXTERIOR FINISHES | 2059 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building as needed. Included in the cost is repairing any cracks and sealing the stone masonry as well as caulking the windows and other penetrations. It is recommended that the building envelope be sealed and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDING #12 - HISTORICAL (VACANT) | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 | 4076 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20380
0334EXT3 | ROOF HATCH | 0334 | The roof hatch is broken and needs to be replaced. This project would provide for the purchase and installation of a new roof hatch. This estimate includes removal and disposal of the existing damaged hatch and any patching and / or repairs to the roof membrane. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9985SFT1 | FIRE ALARM SYSTEM UPGRADE | 9985 | The existing wireless portion of the fire alarm system is over 25 years old and has reached its useful life. Certification of the system is costly, parts are no longer available and the system is routinely failing. A common occurrence is that the Fire Department is notified of an alarm, but the system reports the alarm in the wrong building. This can cause vital time loss to control the fire, protect the building and ensure the life safety of the occupants. The wireless annunciation system consists of a repeater panel in each of the 20 buildings and a master control panel that is currently located near Building #12. This project would provide for replacing the repeater in each building, replacing the master control panel and relocating it to Building #25 and providing miscellaneous work to ensure that each buildings alarm system is functioning properly. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
0333EXT2 | ROOF CLEANING / REPAIRS | 0333 | The roof on this building was in fair condition at the time of the survey. The roof has a few seams that need to be sealed and miscellaneous debris and dirt though out. This project would provide funding to seal the seams and clean off the dirt and debris from the roof. The removal of debris and cleaning must be in conformance with the roofing manufacture's specifications so as not to void the warranty. This project applies to the single-ply membrane portion of the roof. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 500
0333ADA4 | ADA SIGNAGE | 0333 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8B | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
9985HVA1 | DIRECT DIGITAL CONTROL SYSTEM FOR HVAC SYSTEMS | 9985 | Presently the site has no direct digital control (DDC) supervisory control or automated energy management control programs. Future HVAC considerations should include installation of appropriate hardware to connect any new buildings to the campus energy management network while maintaining local control logic. The new system should allow starting of equipment, monitoring of status, monitoring of space temperatures, monitoring and control of hot and chilled water temperatures, and similar typical centrally controlled elements. For the sake of retention of the relatively new pneumatic equipment, the application of a DDC/pneumatic hybrid system is strongly recommended. Detailed control of the individual elements of the system buildings can yield tremendous benefits based upon the reported operating hours coupled with varying occupancy loads. The system should include a microprocessor control center which monitors and manages all components of the building HVAC system. The system should also have the capability of controlling other building systems (such as lighting, alarms, etc.) and of communicating with the central management system for the campus. This project or a portion thereof was previously recommended in the FCA report dated 06/29/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. Did not use this project. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
0334EXT4 | SKYLIGHT REPLACEMENT | 0334 | There are two 8’x8’ acrylic sky-lights located on the roof. Both units have cracks in them that are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of two acrylic skylight units. Minor roof repairs are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/28/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | GROUP HOME - BUILDING #8C | 9985 | HHS | DPBH | NNAMHS | Sparks | 1977 | 5237 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
0326ADA4 | LEVER HARDWARE INSTALLATION | 0326 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed on approximately 45 interior doors to meet these guidelines. This project or a portion thereof was previously recommended in the FCA report dated 06/27/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | ADMINISTRATION - BUILDING #1 | 9985 | HHS | DPBH | NNAMHS | Sparks | 1920 | 32933 | 2017-10-18 | Immediate to Two Years | Currently Critical | 1 | 22500
0976EXT3 | EXTERIOR FINISHES | 0976 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO | 9985 | HHS | DPBH | NNAMHS | Sparks | 1976 | 1194 | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2388
9985SIT5 | FENCE REPAIR | 9985 | There is a fence surrounding the back yard of Building #8C. The fence is constructed of 2"x 6" x 5’ dog eared redwood fence planks and 4"x4" redwood posts. It is due for staining and some boards and posts are broken. This project would provide for the repair and/ or replacement of damaged areas of the fence and staining of the entire fence. This project or a portion thereof was previously recommended in the FCA report dated 06/26/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/05/2012. | NNAMHS SITE | 9985 | HHS | DPBH | NNAMHS | Sparks | 1882 |  | 2017-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1352EXT1 | EXTERIOR FINISHES | 1352 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | WELL HOUSE(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 168 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 1680
2689EXT1 | EXTERIOR FINISHES | 2689 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. | TOOL SHED(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 0 | 120 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 600
1352INT1 | INTERIOR FINISHES | 1352 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | WELL HOUSE(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 168 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 840
1896INT3 | INTERIOR FINISHES | 1896 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 24510
1896PLM1 | REPLACE WATER HEATERS | 1896 | The existing water heaters are old and have reached the end of their expected life. This project would provide for the removal, disposal, and replacement of two 25 gallon gas fired water heaters including all required connections to utilities. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1896STR1 | STRUCTURAL ASSESSMENT | 1896 | An upper level storage mezzanine has been constructed inside of the Building. The 2003 IBC has a minimum requirement of 125p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and it could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 5000
1895INT2 | INTERIOR FINISHES | 1895 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 20750
2690EXT1 | EXTERIOR FINISHES | 2690 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior of the water tank, other than the roof, including painting, staining, or other applied finishes, and caulking penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. | WATER TOWER | 9986 | Correct | SSCC |  | Silver Springs | 0 | 1134 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 10000
2029INT1 | INTERIOR FINISHES | 2029 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. | GENERATOR BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 725 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 3625
1895ELE1 | LIGHTING UPGRADE | 1895 | Existing building lighting fixtures, T-12s, are older fluorescent type and are not energy efficient. This project will upgrade lighting fixtures to T-8s, with electronic ballasts resulting in increased efficiency and reduced costs associated with illumination. | CULINARY/DINING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14525
0711ADA1 | ADA PROJECTS | 0711 | ADA legislation pertaining to building access has established signage criteria for all permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria and should be installed. No accessible shower stall is present in the inmate housing area. ADA accessibility to at least one shower stall is recommended. Removing two existing showers and adding one accessible would be the most cost effective in one of the housing wings. Plumbing modifications are included in this estimate. The same situation exists in the toilet rooms; an accessible toilet is required in each wing. It is recommended to remove two existing toilet stalls and add one accessible stall. Plumbing modifications are included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 60000
0711HVA2 | BOILER REPLACEMENT | 0711 | There are 4 existing gas fired boilers which provide heat for the entire building. They were installed in 1991 and are original to the housing unit. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. This project would provide for the removal and replacement of the 4 boilers with 4 new 765 MBH gas fired boilers. This project should be requested in a CIP in about 8 to 10 years. This project does not address any piping replacement, only connections to existing systems. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 68000
0711INT1 | BATHROOM AND SHOWER ROOM RENOVATION | 0711 | The countertops in the restrooms and shower rooms in each wing show signs of wear, deterioration and are damaged. There are three wings with restrooms. Extensive use, combined with repetitive water being spilled, has caused the laminate top to separate from the wooden underlayment and should be replaced. A problem exists with the drain system in the shower rooms. The drains clog frequently, possibly due to improper installation or debris. Because the floor is a concrete slab, the work to repair this problem is extensive. This portion of the project provides for an inspection of the waste lines with a video camera to determine the extent of the problem. Future projects may result from the findings and are not included in this estimate. This project also includes remodeling of the existing showers, with includes at a minimum removal of all tile and plumbing fixtures, gypsum board repair and installation of new stainless steel shower units. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 180000
2029EXT1 | EXTERIOR FINISHES | 2029 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. | GENERATOR BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 725 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 3625
0711ELE1 | LIGHTING UPGRADE | 0711 | Existing building lighting fixtures, T-12s, are older fluorescent type and are not energy efficient. This project will upgrade lighting fixtures to T-8s, with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39347
1896EXT1 | REPAIR / REPLACE DOORS & GLAZING | 1896 | Per 2003 IBC 2406.3, safety glass is required when a fixed window is located within two feet of the door. This project recommends replacement of the two windows on the south side and one on the west side with safety glazing. The doors in the building have damaged or missing hardware. This project would replace the door hardware on all of the doors. The wall and overhead door in the gymnasium area have been damaged. The extent of the damage within the wall is not known. The door should be replaced and the wall framing members should be exposed to inspect and repair as necessary. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 17000
1896INT1 | LAUNDRY ROOM REMODEL | 1896 | The laundry room is not vented and an exhaust fan should be installed. Combustion-air ducts are needed for the laundry room from the exterior of the building. There is some damage to the gypsum board from moisture and this project includes funds for repair of the gypsum board and installation of FRP on the walls adjacent to the washers and dryers. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
1896ELE1 | LIGHTING UPGRADE | 1896 | Existing building lighting fixtures, T-12s, are older fluorescent type and are not energy efficient. This project will upgrade lighting fixtures to T-8s, with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28595
1895EXT1 | DOOR AND WINDOW MODIFICATIONS | 1895 | The exterior door to the loading dock is too small for the use intended; it is a single three-foot-wide door. A set of double doors will provide easier access to transport freight into the storage area. This project would provide for a new 6'-0"x7'-0" set of doors including frame, painting and hardware. Modifications to the structure are included in this estimate. Two windows in the dining area have seals broken and moisture stains, which makes visibility difficult. The broken seal reduces the insulation factor of these windows. New replacements are recommended. These are located on the east side. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1895HVA1 | TYPE 2 HOOD INSTALLATION FOR DISHWASHER | 1895 | The Uniform Mechanical Code, Section 508.1, requires exhaust hoods be installed above commercial grade dishwashing machines. This dishwasher does not have an exhaust hood. This project would provide for the installation of a Type II exhaust hood to be mounted over the dishwasher including all required ducting to the roof, cutting the roof penetration and sealing of all roof penetrations. Connections to utility systems is also included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 18500
1895ADA1 | ADA SIGNAGE | 1895 | The ADA has established signage criteria for all permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria and should be replaced. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 12349.698
0711EXT1 | EXTERIOR FINISHES | 0711 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This structure should be painted every five to seven years to maintain it's integrity. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 56210
9986SFT1 | INSTALL SEISMIC GAS SHUT OFF VALVE | 9986 | Agreements reached between the Nevada Risk Management Office and the State of Nevada's Insurance Underwriter require Seismic Gas Shutoff Valves (SGSV's) on all gas services to all State buildings. This project would install a SGSV to the gas main line serving the buildings on site. | SILVER SPRINGS CONSERVATION CAMP SITE | 9986 | Correct | SSCC |  | Silver Springs | 1991 |  | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 4500
0711HVA1 | REPLACE BATHROOM EXHAUST FANS | 0711 | The exhaust fans in the shower room and bathrooms do not operate properly or do not work at all. This project would provide for the removal and replacement of the exhaust fans including connections to existing utilities. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 9000
1895EXT2 | EXTERIOR FINISHES | 1895 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building is a metal sided building and required mostly caulking and sealing of doors windows, penetrations, etc. This project should be done on an as needed basis with at least a once a year inspection of the exterior with special attention paid to the south and west sides of the structure. This estimate is for a one time complete exterior inspection, caulk and seal which may be used for future operating budget requests by the using agency. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | CULINARY/DINING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 4150 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 6225
0711INT2 | INTERIOR FINISHES | 0711 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This structure should be painted every five to seven years to maintain it's integrity. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 56210
1896EXT2 | EXTERIOR FINISHES | 1896 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building is a metal sided building and required mostly caulking and sealing of doors windows, penetrations, etc. This project should be done on an as needed basis with at least a once a year inspection of the exterior with special attention paid to the south and west sides of the structure. This estimate is for a one time complete exterior inspection, caulk and seal which may be used for future operating budget requests by the using agency. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Four to Ten Years | Long-Term Needs | 3 | 12255
1896ADA1 | ADA / RESTROOM REMODEL PROJECT | 1896 | The Americans With Disabilities Act (ADA) requires complying drinking fountains in the building. An estimate for an ADA compliant drinking fountain is included with this project. ADA legislation pertaining to building access has established signage criteria for all permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project provides funds for ADA signage. The water closet and lavatories in the restroom adjacent to the gym are worn from years of use. It is recommended that the fixtures in all the bathrooms be replaced. This estimate includes the removal and replacement of the toilet and two sinks including faucets. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | MULTI-PURPOSE BUILDING(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 8170 | 2006-08-17 | Immediate to Two Years | Currently Critical | 1 | 15000
0711SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0711 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Emergency exit lighting should be installed and/or replaced to provide illumination along the egress route. This project or a portion there of was previously recommended in the FCA report dated 5/4/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/17/2006. | HOUSING UNIT(VACANT) | 9986 | Correct | SSCC |  | Silver Springs | 1991 | 11242 | 2006-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22484
0115ADA6 | ACCESSIBLE ENTRANCE RAMP | 0115 | This facility has an ADA accessible ramp located on the north side of the building at the main entrance. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have proper slopes, landings or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 35000
9988SIT7 | ASPHALT PAVING INSTALLATION | 9988 | There is no asphalt paving connecting Building #1 to the access road between Housing Unit #2 and the Multi-Purpose building. This project would provide asphalt cement paving for a 20' wide access road from the existing paving to the back side of Unit #1. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | WARM SPRINGS CORRECTIONAL CENTER | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9988ADA1 | ADA PARKING UPGRADES | 9988 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking spaces and path of travel to the entrance of the building do not meet the requirements of the code. The slopes are out of compliance, the configuration of the spaces, loading zones and path of travel to the entrance are not compliant. This project provides funding to bring the existing ADA parking space up to code including removal of the asphalt and replacement with P.C. concrete, installing a concrete path of travel to the entrance, updated signage, re-striping, re-grading and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | WARM SPRINGS CORRECTIONAL CENTER | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 45000
0115ADA2 | ADA SIGNAGE | 0115 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 1500
0115EXT2 | EXTERIOR FINISHES | 0115 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97210
0115INT4 | INTERIOR FINISHES | 0115 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97210
0115EXT4 | EXTERIOR DOOR REPLACEMENT | 0115 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 14 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
9988SIT6 | CRACK FILL & SEAL ASPHALT PAVING | 9988 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and exercise yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 180,000 square feet of asphalt area was used to generate this estimate. | WARM SPRINGS CORRECTIONAL CENTER | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
0118ADA2 | ADA SIGNAGE | 0118 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 22500
2034ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 2034 | There is an electrical duplex outlet under the sink in each restroom which is not GFCI protected. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of two GFCI duplex outlets for the safety of the occupants. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 600
2034PLM1 | WATER HEATER REPLACEMENT | 2034 | There are two 5 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new on-demand electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2034EXT2 | SLIDING GLASS DOOR REPLACEMENT | 2034 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2034EXT1 | EXTERIOR FINISHES | 2034 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2003ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 2003 | There is an electrical duplex outlet under the sink which is not GFCI protected. This outlet should be changed to a GFCI type outlet per the NEC. This project would provide for the purchase and installation of a GFCI duplex outlet for the safety of the occupants. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 300
2003EXT2 | SLIDING GLASS DOOR REPLACEMENT | 2003 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2003EXT1 | EXTERIOR FINISHES | 2003 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0118HVA3 | HYDRONIC HEATER REPLACEMENT | 0118 | The building is partially heated by two roof-mounted hydronic heaters. They are original to the building and have reached the end of their useful life. This project provides for disposal of the existing units and replacement with two new roof-mounted units including connections to utilities. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0118ADA3 | ADA BREAK ROOM REMODEL | 0118 | There are two small Employee Lounges in the building and a Lab Room with cabinets and a sink. The kitchenettes and associated cabinets are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 45000
0118INT6 | VCT FLOORING REPLACEMENT | 0118 | The VCT (vinyl composite tile) flooring in the Dining Room is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16200
0115ADA5 | ADA ACCESSIBLE COUNTER | 0115 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The security counter at the entrance of the building does not meet current ADA requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 1500
0118EXT3 | EXTERIOR FINISHES | 0118 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
0115INT5 | INTERIOR WINDOW REPLACEMENT | 0115 | There are two interior windows near the entrance that are cracked and should be replaced. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0117ENR1 | HVAC EQUIPMENT REPLACEMENT | 0117 | The HVAC system was installed in 1998 and is original to the building. It consists of two natural gas-fired boilers, rooftop air-conditioners and rooftop air handlers. The system is not energy efficient and will reach the end of its expected and useful life in the next 5-8 years. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Four to Ten Years | Long-Term Needs | 3 | 690000
0117INT1 | INTERIOR FINISHES | 0117 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 230000
0117EXT2 | EXTERIOR FINISHES | 0117 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 92000
0116ENR1 | HVAC REPLACEMENT | 0116 | The HVAC system was installed in 1977 and is original to the building. It consists of a natural gas-fired boiler, a chiller and several fan coil units. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project is funded under CIP 13-M18 and the estimate is based off of that project. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0116PLM2 | WATER HEATER REPLACEMENT | 0116 | There are two 100 gallon natural gas-fired water heaters in the building. One of them is currently not operational. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0116SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0116 | The existing control panel appeared to be operating properly but technology has changed, replacement parts are hard to find for performing routine and emergency maintenance and it is reaching the end of its expected life. The current electronic controls do not cover all of the cell doors which are currently on a key system. This project would provide a new electronic touch screen door control system for 54 cell doors in this unit. All doors and frames on inmate cells would require replacement to accommodate the electric locks; conduit and conductors would have to be run to all cells. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000000
0116EXT4 | WINDOW REPLACEMENT | 0116 | The louvered windows are original, single pane construction in metal frames. These older windows are drafty, not energy efficient and the louver mechanisms are problematic. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 66 units. Removal and disposal of the existing windows is included in this estimate. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 79200
0116INT3 | INTERIOR FINISHES | 0116 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57775
0116EXT3 | EXTERIOR FINISHES | 0116 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57775
0115EXT3 | WINDOW REPLACEMENT | 0115 | The exterior windows are original, dual pane construction in metal frames. These older windows are not insulated and not energy efficient. This project recommends replacing the windows with dual pane security rated window systems. This estimate is for the replacement of 124 units. Removal and disposal of the existing windows is included in this estimate. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 148800
0118INT5 | INTERIOR FINISHES | 0118 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108000
0115ADA3 | ADA RESTROOM REMODEL | 0115 | There are several staff and inmate restroom throughout the building. Some of them have accessible elements, but none are fully compliant. They do not meet the current Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0118SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0118 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10800
0116PLM1 | WATER CLOSET AND LAVATORY REPLACEMENT | 0116 | The existing water closets and lavatories in 45 of the inmate cells are made of vitreous china. These types of fixtures are damaged and broken frequently and weapons can be made from the broken pieces which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project would provide for replacing the existing water closets and lavatories with a stainless steel combination water closet with lavatory unit that is suicide resistant. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 232500
0115ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0115 | This building contains 3 water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of six drinking fountains to meet the ADA requirements, a high and low fountain in each of the three separate secured areas. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 12000
0118ADA1 | ADA RESTROOM UPGRADE | 0118 | The staff restroom and inmate shower in the Medical area are not ADA compliant. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom and remodeling the shower. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 35000
0115INT2 | FLOORING REPLACEMENT | 0115 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175000
0116HVA1 | EXHAUST FAN REPLACEMENT | 0116 | The existing exhaust fans that serve the restrooms and showers are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2003INT1 | INTERIOR FINISHES | 2003 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0116SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0116 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5776
0121EXT3 | EXTERIOR FINISHES | 0121 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #4 | 9988 | Correct | WSCC |  | Carson City | 1957 | 576 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0116ADA3 | ADA SHOWER REMODEL | 0116 | The building has a shower/ bathing room in each of the three wings. The ceramic tiles, fixtures, and drains are broken and failing. None of the shower stalls are ADA accessible or compliant. This project would provide for a complete remodel of all three shower rooms. One of the showers should be an ADA compliant stainless steel shower cabinet complete with accessible plumbing fixtures, seat, etc. Included in this estimate is removal and replacement of the fixtures and finishes in all three shower rooms. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0119EXT3 | EXTERIOR FINISHES | 0119 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #2 | 9988 | Correct | WSCC |  | Carson City | 1957 | 576 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0116EXT2 | EXTERIOR DOOR REPLACEMENT | 0116 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the purchase and installation of 10 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0115SEC1 | CELL DOORS, LOCKS AND MECHANISMS REPLACEMENT | 0115 | The existing control panel appeared to be operating properly but technology has changed, replacement parts are hard to find for performing routine and emergency maintenance and it is reaching the end of its expected life. The current electronic controls do not cover the cell doors which are currently on a key system. This project would provide a new electronic touch screen door control system for the sally ports and 60 cell doors in this unit. All doors and frames on inmate cells would require replacement to accommodate the electric locks; conduit and conductors would have to be run to all cells. This project is in design under CIP 11-M14 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 1244200
0118EXT2 | CLEAN ROOF DEBRIS | 0118 | The roof on this building was in fair condition at the time of the survey but debris was observed in certain areas. The roof has grease from the culinary exhaust fan leaking on the roof and dead birds and other items in the roof drains. This project would provide for the cleaning of the roof membrane using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | MULTI-PURPOSE/CULINARY/INFIRMARY | 9988 | Correct | WSCC |  | Carson City | 1980 | 21600 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 500
0115ADA4 | ADA SHOWER REMODELS | 0115 | The inmate housing portion of this building has showers in each wing. None of the shower stalls are ADA accessible or compliant. The shower stalls are all showing signs of age, deterioration and inmate abuse. This project would provide for remodeling all of the showers including one ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is removal and replacement of the existing shower stalls and installation of stainless steel shower units. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 500000
0122EXT3 | EXTERIOR FINISHES | 0122 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #5 | 9988 | Correct | WSCC |  | Carson City | 1957 | 480 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2034INT1 | INTERIOR FINISHES | 2034 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/07/1999 and 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
0117EXT3 | ROOF REPLACEMENT | 0117 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT 4 | 9988 | Correct | WSCC |  | Carson City | 1998 | 44600 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 552000
2034HVA1 | HVAC EQUIPMENT REPLACEMENT | 2034 | The packaged HVAC unit is more than 15 years old and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | GUARD TOWER 2 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0115SFT2 | EXTERIOR STAIR REPLACEMENT | 0115 | There are two sets of stairs coming out of the building that are not code compliant and are due for replacement. The exterior concrete stairway that leads out from the Administration area is deteriorating and missing proper handrails. Spalling and cracking have occurred to the point of exposing rebar and causing a tripping hazard. It has only one handrail and does not have a proper landing at the bottom of the stairway. It appears these stairs are original to the building. The exterior steel stairway that leads out of "C" Wing does not have a compliant landing from the exit door and is missing a handrail. This project recommends the removal and replacement of the stairways and handrails in accordance with IBC Sections 1009 and 1012. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | ADMINISTRATION/GATEHOUSE/UNIT 1 | 9988 | Correct | WSCC |  | Carson City | 1962 | 19442 | 2014-05-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0097EXT3 | EXTERIOR FINISHES | 0097 | It is important to maintain the finish, weather resistance and appearance of the building which is over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and re-pointed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | COTTAGE #6 | 9988 | Correct | WSCC |  | Carson City | 1957 | 576 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
9988SEC1 | VIDEO SURVEILLANCE SYSTEM INSTALLATION | 9988 | There are no security cameras or recording systems for the prison site except for a few isolated areas and in Housing Unit 4. This is a safety issue as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide funding for the installation of a site wide surveillance camera and recording system and all required connections to utility systems. This project is a lump sum estimate for budgeting purposes. Final design of the system and amount of cameras would be determined by an in depth site survey and programming and may affect the final proposed cost estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/18/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/13/2014. | WARM SPRINGS CORRECTIONAL CENTER | 9988 | Correct | WSCC |  | Carson City | 1962 |  | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 650000
2003HVA1 | HVAC EQUIPMENT REPLACEMENT | 2003 | The packaged HVAC unit is more than 15 years old and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | GUARD TOWER 1 | 9988 | Correct | WSCC |  | Carson City | 1998 | 402 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0116EXT5 | ROOF REPLACEMENT | 0116 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1992. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT 2 | 9988 | Correct | WSCC |  | Carson City | 1977 | 11555 | 2014-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 138660
1401INT2 | INTERIOR FINISHES | 1401 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 39005
0107SFT3 | INSTALL FIRE ALARM SYSTEM | 0107 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0108SFT3 | INSTALL FIRE ALARM SYSTEM | 0108 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0109SFT3 | INSTALL FIRE ALARM SYSTEM | 0109 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0110SFT3 | INSTALL FIRE ALARM SYSTEM | 0110 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
0107SEC5 | WINDOW REPLACEMENT | 0107 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0108SEC5 | WINDOW REPLACEMENT | 0108 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0110SEC5 | WINDOW REPLACEMENT | 0110 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
1401SFT3 | INSTALL FIRE ALARM SYSTEM | 1401 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
1401SEC5 | REPLACE CELL DOORS | 1401 | Housing Unit No. 6 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0107EXT2 | REPLACE ROOF | 0107 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0108EXT2 | REPLACE ROOF | 0108 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0109EXT2 | REPLACE ROOF | 0109 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0110EXT3 | REPLACE ROOF | 0110 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
1401EXT2 | REPLACE ROOF | 1401 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
0094STR1 | SEISMIC RETROFIT AND TENANT IMPROVEMENT | 0094 | This building is constructed of sandstone masonry walls on the exterior and poured in place concrete columns, floors and roof deck which are keyed into the stone except for Housing Unit 5 and the third level which contains the third level addition known as Unit 2. The majority of this structure was constructed around 1925. This project would provide for a seismic retrofit of a portion of the structure. Included in this estimate is a cost for tenant improvements to relocate and or remodel offices, restrooms, control room, entrance lobby, and associated programs to provide ADA accessibility and efficient use of space mainly at the first floor of the building. Final design and scope of this project may impact the cost of this project. 45,000 square feet of floor area was used to generate this cost estimate. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5297500
0109SEC5 | WINDOW REPLACEMENT | 0109 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
1405EXT5 | DEMOLISH STRUCTURE | 1405 | The Guard Tower #5 sways substantially during high winds and its structural integrity is suspect. The structure is also approaching 30 years of age and should be replaced. It is recommended that this structure be demolished and a new guard tower be built in its place. The cost estimate includes capping existing utilities and removal of possible asbestos containing materials. The "New Guard Tower" project should be implemented immediately following this project. | GUARD TOWER #4 SOUTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
1401SEC4 | WINDOW REPLACEMENT | 1401 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0106EXT2 | REPLACE ROOF | 0106 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 02/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2006. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 156020
1404EXT4 | REPLACE GUARD TOWER | 1404 | This project would provide for the construction of a new guard tower in place of the existing Guard Tower #3 Northeast. This project should be implemented immediately following the "Demolish Structure" project which will eliminate the existing guard tower. The cost estimate is based on the proposed Prison 8 Guard Tower design at Indian Springs. | GUARD TOWER #3 NORTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 560000
0106SFT3 | INSTALL FIRE ALARM SYSTEM | 0106 | The Housing unit has a smoke detector located in the bottom portion of the existing HVAC ducting system at each duct chase which provides the only fire protection system in the structure. There is no fire alarm or sprinkler system. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54607
1404EXT5 | DEMOLISH STRUCTURE | 1404 | The Guard Tower #3 sways substantially during high winds and its structural integrity is suspect. The structure is also approaching 30 years of age and should be replaced. It is recommended that this structure be demolished and a new guard tower be built in its place. The cost estimate includes capping existing utilities and removal of possible asbestos containing materials. The "New Guard Tower" project should be implemented immediately following this project. | GUARD TOWER #3 NORTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
1406EXT4 | NEW GUARD TOWER | 1406 | This project would provide for the construction of a new guard tower in place of the existing Guard Tower #3 Northeast. This project should be implemented immediately following the "Demolish Structure" project which will eliminate the existing guard tower. The cost estimate is based on the proposed Prison 8 Guard Tower design at Southern Desert Correctional Center. | GUARD TOWER #5 SOUTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 256 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 560000
1406EXT5 | DEMOLISH STRUCTURE | 1406 | The Guard Tower #5 sways substantially during high winds and its structural integrity is suspect. The structure is also approaching 30 years of age and should be replaced. It is recommended that this structure be demolished and a new guard tower be built in its place. The cost estimate includes capping existing utilities and removal of possible asbestos containing materials. The "New Guard Tower" project should be implemented immediately following this project. | GUARD TOWER #5 SOUTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 256 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0106SEC5 | WINDOW REPLACEMENT | 0106 | The existing operable windows in the housing unit cells are original and have been damaged by inmate abuse and are no longer working as intended. This project would provide for the removal and replacement of the windows in the housing unit cells. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
9989SIT5 | REPLACE DAMAGED SEWER WASTE LINE | 9989 | The existing sewer waste line from the Culinary building to just west of the Courthouse has had numerous failures and is in need of replacement. This project would provide for the replacement of about 200 lineal feet of 4" sewer waste line. Excavation, backfill and boring under the existing structure is included in this estimate. A lump sum of $5,000 was used for the boring portion of this estimate. This project should be done concurrently with the sewer grinder installation project for the Culinary / Dining facility. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 18000
9989ADA1 | ADA PROGRAM SITE ACCESSIBILITY | 9989 | The Nevada State Prison site currently does not have any ADA program accessibility for staff and inmates. There is also a visitation room at Housing Unit 12 in the north east area of the site. This project would provide for ADA program accessibility improvements to the prison site which may include a route of travel from the Administration / Visitation area to the Culinary / Dining facility, educational programs located in building 0094 Administration / Cell Blocks, the Gymnasium and Infirmary. This project includes new walks, ramps, stairs, handrails on existing and new stairs and other improvements which will provide ADA program accessibility and building code compliance in the lower yard and to Housing Unit 12. Also included is an ADA accessible walkway with a ramp and handrails for access into Housing Unit 12. This project should be done concurrent with the tenant improvement project in the Administration / Cell Block building which will relocate programs to the lower level of this building. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500000
1405EXT4 | NEW GUARD TOWER | 1405 | This project would provide for the construction of a new guard tower in place of the existing Guard Tower #3 Northeast. This project should be implemented immediately following the "Demolish Structure" project which will eliminate the existing guard tower. The cost estimate is based on the proposed Prison 8 Guard Tower design at Indian Springs. | GUARD TOWER #4 SOUTHEAST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 144 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 560000
0107PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0107 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0099INT1 | INTERIOR FINISHES | 0099 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 13440
0099ELE1 | LIGHTING UPGRADE | 0099 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20160
0099EXT3 | REPLACE CONCRETE STEPS | 0099 | The IBC 2006 section 1008.1.5 requires landings shall have a width not less than the width of the stairway or the door, which is the greater. The landing and stairs have been saw cut and partially removed. This situation could create a slip and fall hazard. This project would provide funding for the removal of the existing concrete and the installation of a concrete landing, stairs and handrail as required. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5000
0107ENR1 | LIGHTING UPGRADE | 0107 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0103EXT1 | EXTERIOR FINISHES | 0103 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is the sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 113340
0103INT1 | INTERIOR FINISHES | 0103 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56670
0096INT1 | INTERIOR FINISHES | 0096 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39900
0110INT1 | REPLACE FLOORING IN GUN POST #5 | 0110 | Attached to the roof of this housing unit is Gun Post #5. The flooring is vinyl composition tile (VCT) and has deteriorated from constant use, weather and the passage of time. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0110EXT1 | REPLACE WINDOWS AND DOORS IN GUN POST 5 | 0110 | The gun post contains two doors and four windows. The seals are broken on several of the windows. Because of the broken seals, condensation occurs and the windows become fogged between the panes of glass. It is difficult to see through this fogging. This is a structure that observes inmates, so it is important that the officer has a clear line of site. A high probability exists that this situation will occur with the remaining windows also. This project would provide funding for the purchase and installation of new security/safety glazed windows. The two doors are also showing signs of wear and deterioration. The hardware on one door is damaged from constant use. This project would provide funding for the purchase and installation of new doors and associated hardware. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0106SEC3 | REPLACE CELL DOORS | 0106 | Housing Unit No. 6 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0106PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0106 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0105INT1 | INTERIOR FINISHES | 0105 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 39655
0105EXT2 | EXTERIOR FINISHES | 0105 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for the painting of the exterior of the building. Included in the cost estimate is the sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations that may be required. This building should be painted within the next five to seven years. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 79310
0105ELE1 | LIGHTING UPGRADE | 0105 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59482
0099SFT1 | EXIT SIGN & EGRESS LIGHTING INSTALLATION | 0099 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1700
0106SEC2 | EXTERIOR DOOR REPLACEMENT | 0106 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0110SEC3 | REPLACE CELL DOORS | 0110 | Housing Unit No. 10 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0110SEC2 | EXTERIOR DOOR REPLACEMENT | 0110 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0110SEC1 | REPLACE SECURITY GLAZING | 0110 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0110ENR1 | LIGHTING UPGRADE | 0110 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0109SEC2 | EXTERIOR DOOR REPLACEMENT | 0109 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0109SEC1 | REPLACE SECURITY GLAZING | 0109 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0109PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0109 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0098SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0098 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 1998 Section 7. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 28959
0094INT1 | REPLACE ADMINISTRATION OFFICE DOORS | 0094 | The front office doors in the administration portion of the building are showing signs of heavy use. The bottom of the doors have become warped and damaged over the years. this project would provide funding for the purchase and installation of new hollow metal offices doors, frames, lever action door handles, hardware and painting of doors and frames. Removal and disposal of existing damaged doors and frames is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009.. This estimate is for the removal and replacement of 15 doors. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 52500
1401SEC2 | EXTERIOR DOOR REPLACEMENT | 1401 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0108SEC3 | REPLACE CELL DOORS | 0108 | Housing Unit No. 8 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0108SEC2 | EXTERIOR DOOR REPLACEMENT | 0108 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0108SEC1 | REPLACE SECURITY GLAZING | 0108 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0108PLM3 | REPLACE WATERCLOSETS AND LAVATORIES | 0108 | The existing lavatories and water closets in this housing unit are made of vitreous china. These types of fixtures are damaged and broken frequently; weapons can be made from the broken pieces, which creates a security risk. Stainless steel units are more durable and are recommended to be installed. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 144000
0108ENR1 | LIGHTING UPGRADE | 0108 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0022SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0022 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2250
0022SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0022 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 41552
0109ENR1 | LIGHTING UPGRADE | 0109 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0109EXT1 | EXTERIOR FINISHES | 0109 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0098INT2 | STRUCTURAL ASSESSMEMT | 0098 | An upper level storage mezzanine has been constructed inside of the Bindery Building. The 2006 IBC has a minimum requirement of 125p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. This project was listed as "BEAM INSTALLATION" in the FCA report dated 09/15/1999 and was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
0107SEC1 | REPLACE SECURITY GLAZING | 0107 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0098SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0098 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/15/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3400
0106HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0106 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0094ADA1 | ADA RESTROOM REMODEL | 0094 | The Administration Offices do not have an accessible restroom. The existing bathroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 30000
1401EXT1 | EXTERIOR FINISHES | 1401 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0110INT2 | INTERIOR FINISHES | 0110 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
1401ELE1 | LIGHTING UPGRADE | 1401 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0109INT1 | INTERIOR FINISHES | 0109 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
1401SEC1 | REPLACE SECURITY GLAZING | 1401 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0108INT1 | INTERIOR FINISHES | 0108 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0108EXT1 | EXTERIOR FINISHES | 0108 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0107INT1 | INTERIOR FINISHES | 0107 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0107EXT1 | EXTERIOR FINISHES | 0107 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0112INT1 | REPLACE VINYL/ ASBESTOS TILE FLOOR | 0112 | The existing building is used as an armory. The floor tiles contain asbestos and have reached the end of their useful life. When cabinets or files are moved around, asbestos fiber becomes air-borne, this is harmful to anyone inside the building. This project would provide funding for the removal and disposal of the asbestos tile and the installation of vinyl floor tiles to be installed. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29750
0106SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0106 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0098SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0098 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 57918
0099EXT1 | EXTERIOR FINISHES | 0099 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26880
0110EXT2 | EXTERIOR FINISHES | 0110 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior paint is peeling and the caulking around the windows, flashing, fixtures and other penetrations is failing. This project would provide for the painting of the exterior of the building. Included in the cost estimate is the sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations that may be required. This building should be painted within the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/17/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 78010
0110SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0110 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0108HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0108 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
1408ELE1 | LIGHTING UPGRADE | 1408 | Existing building lighting fixtures in the rooms adjacent to the housing area use T-12 technology, and are older fluorescent types and are not energy efficient. The existing lighting in the housing areas are provided by high bay sodium type, large round fixtures. This project will upgrade the lighting fixtures in the area adjacent to the housing units with T-8 lamps and electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. It is also recommended that the sodium lights be replaced with new more energy efficient high-pressure sodium lights. These types of lights will provide better illumination and energy savings. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89160
1408SFT1 | EXIT SIGN LIGHTING UPGRADE | 1408 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2500
9989SIT1 | REPAVE DAMAGED ASPHALT AND RESEAL ROADWAY | 9989 | Asphalt walkways have been constructed to many of the facilities, including the guard towers; most of these walkways are in fair condition. Some of the driveways and parking areas throughout the site have damage. Numerous cracks, potholes, and general deterioration are present. Snow accumulations, frost and rain, etc. are contributing factors. This is typical wear over time. It was noted that under the main parking lot a geothermal area exists. This is the main cause of accelerated deterioration from heat rising through the road surface. The areas for replacement are all non-foot traffic areas. The asphalt leading to the housing units will only need to be sealed. 145,233 square feet was used to generate this estimate. An access road around the perimeter of the fence has been constructed. It is in good condition. For proper routine maintenance it is recommended the entire roadway be resealed. This type of application will extend the life of the asphalt. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480000
1401SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1401 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0110SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0110 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0109SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0109 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0108SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0108 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0094ELE1 | UPGRADE ELECTRICAL SYSTEM | 0094 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time progressed the building's electrical demand and system has been changed. It is utilized to its current maximum potential. The electrical panels and receptacles are older types and are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including switchgear, main panels and subpanels located in the utility chases and basement areas. Electrical fixtures are addressed in another project. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1912518
1401SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1401 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0094ELE2 | LIGHTING REPLACEMENT / UPGRADE | 0094 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. The majority of the light fixtures are not the security type fixtures with the enclosed housing. This project would provide funding for the purchase of new security type fixtures with T-8 lamps and electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Security lighting fixtures shall be installed in inmate areas. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. This project should be done concurrently with the other electrical related projects which may help reduce the costs. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 796882
0109SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0109 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0108SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0108 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 08 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0107SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0107 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
1408PLM1 | REMOVE AND REPLACE EXISTING WATER HEATER | 1408 | Two 100-gallon gas-fired water heaters supply domestic hot water. One has been replaced and the other is original to the building. The average life span of a typical gas/oil or electric water heater is eight to ten years. With the passage of time and constant use, the one unit is showing signs of wear. It is reaching the end of its expected life. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6500
0114SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0114 | This building does not have an automatic fire suppression system. We are recommending installation of fire sprinklers in critical need buildings within the prison enclosure. This project will include a backflow prevention device as required by state law. State law regulates connections between public water systems and sources of contaminants which can enter the system by back pressure or siphonage. Public water systems include supplies, systems for pumping, storage and treatment and distribution systems. The NAC 477.915 requires a fire sprinkler system to be installed: (c) If the building: (1) Is designated as a B occupancy; (2) Regardless of occupancy designation, has a floor area which exceeds 12,000 square feet on any floor or 24,000 square feet on all floors, including any mezzanines; or (3) Is an R-1 or R-2 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building. This building contains a B occupancy. Water purveyors require service backflow prevention immediately after the meter, which isolates the customer's water system from the distribution system. If fire water or irrigation systems tap directly into the public system, backflow devices would be necessary on both domestic, irrigation and fire water services. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 54750
1401HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 1401 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 11 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0110HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0110 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 10/GUN POST #5 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0099SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0099 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 37632
0107SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0107 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0094ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0094 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 10000
0096ELE1 | LIGHTING UPGRADE | 0096 | Existing building lighting fixtures in the rooms adjacent to the gymnasium are T-12s, and are older fluorescent types and are not energy efficient. The existing lighting in the gymnasium is provided by high bay metal halide type fixtures. This project will upgrade the lighting fixtures in the area adjacent to the gymnasium to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. It is recommended that the metal-halide lights be replaced with high pressure sodium lights. These types of lights will provide better illumination as well as energy savings. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59850
0095SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0095 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2550
0095HVA2 | REPLACE EXHAUST FANS IN SCREENING ROOM | 0095 | There are two exhaust fans in the silk screening room to remove fumes. The fans are noisy and have reached the end of their expected service life. This project would provide funding for the replacement of the exhaust fans. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0095PLM1 | REPLACE WATER HEATER | 0095 | The water heater tank is showing signs of wear and deterioration and is not seismic anchored. It appears this appliance is original to the building. This project would provide funding for the purchase and installation of a new natural gas unit and seismic anchoring. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 3500
0094EXT2 | REPLACE EXISTING ROOF | 0094 | The roof on this building was in fair condition at the time of the survey. The single-ply system is spongy along the walkways, and is especially noticeable at the bottom of the stairs from the third story to the fourth story and there is an old built-up roofing system with concrete pavers on top which should be replaced. It appears that a roof coating has been applied on the unit 3 section of the building. One portion of the roof was redone in 1989. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 840000
0094SFT4 | INSTALL SECOND MEANS OF EGRESS IN VISITORS CENTER | 0094 | The visitor center has only one means of egress. The maximum posted occupancy of this room is 76. The 2006 International Building Code (IBC), table 1018.1 requires the occupant load 1-500 to have a minimum of 2 exits. This project would provide for the labor and material necessary to install a second means of egress. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
0094SFT3 | FIRE ALARM SYSTEM UPGRADE | 0094 | This building is equipped with an automatic fire detection and alarm system, but the system is old, does not meet current code requirements and is missing in some locations. It is recommended that the fire detection and alarm system be upgraded to a fully monitored. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements and building codes. This project should be coordinated with the fire sprinkler upgrade project. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 743757
0095HVA1 | REPLACE EVAPORATIVE COOLERS | 0095 | There are currently four evaporative coolers mounted on the side of the building. They are severely scaled and have reached the end of their serviceable life. This project would provide for four new evaporative coolers to be installed. Project includes removal and disposal of the old coolers and utility connections to the new units. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9989SIT3 | REPLACE STAIRS TO CULINARY | 9989 | The exterior stairs that lead to the main entrance and culinary appears to be part of the original construction. Deterioration, spalling and cracking has occurred, mainly from exposure to the weather and freeze / thaw conditions. This project would provide funding for the removal and disposal of the old concrete and the installation of new concrete steps including handrails. This project should be done concurrently with ADA accessible route improvement project proposed for the lower yard. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1402SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1402 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20650
0107HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0107 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0094SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0094 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways throughout the building. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0120SFT1 | REPLACE VINYL/ ASBESTOS TILE FLOOR | 0120 | The existing building is used as an armory. The floor tiles contain asbestos and have reached the end of their useful life. When cabinets or files are moved around, asbestos fiber becomes air-borne, this is harmful to anyone inside the building. This project would provide funding for the removal and disposal of the asbestos tile and the installation of vinyl floor tiles to be installed. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31605
0120HVA1 | HVAC INSTALLATION | 0120 | The building is currently used as an Armory. It is important to maintain temperature and humidity. The heater appears to be original to the building. It is not energy efficient and has reached the end of its useful life. There is no air-conditioning or way of controlling humidity. This project would provide funding for the purchase and installation of a new HVAC and humidity control unit. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27900
0120ELE1 | LIGHTING UPGRADE | 0120 | The existing building lighting fixtures are older luminescent type and are not energy efficient. If this building would be used for anything other than storage, it is recommended a lighting upgrade be done. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 3255
0112HVA1 | REPLACE HEATER, INSTALL EVAPORATIVE COOLER | 0112 | The building is currently used for storage files. It is important to maintain temperature. The heater appears to be original to the building. It is not energy efficient and has reached the end of its useful life. There is no air-conditioning or ways of cooling the building. This project would provide funding for the design, purchase and installation of a new HVAC system. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25500
1410EXT3 | EXTERIOR FINISHES | 1410 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
0094SFT1 | FIRE SPRINKLER INSTALLATION UPGRADE | 0094 | The administration offices, visiting area, education, laundry, infirmary, mattress factory, housing units, and canteen are located in this building. Most of the building does not have fire sprinklers. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. Also, NAC 477.915 Existing buildings owned by State: Requirements; reporting of fires; smoke detectors; penalty for violation of section. (NRS 477.030) 1. Every existing building owned by the State of Nevada must: (a) Comply with the provisions of NRS 477.100 to 477.170, inclusive; (b) Meet the requirements of the building code in effect when the building was constructed; (c) If the building: (1) Is designated as a B occupancy; (2) Regardless of occupancy designation, has a floor area which exceeds 12,000 square feet on any floor or 24,000 square feet on all floors, including any mezzanines; or (3) Is an R-1 or R-2 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building; This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1487514
0094SEC1 | REPLACE CELL BLOCK DOOR CONTROL PANELS AND MOTORS | 0094 | Problems exist with the door control panel and cell door motor systems in the cell blocks. It is believed the systems are original equipment. Repairs to the control systems and motors are difficult because replacement parts are not being manufactured for the units. It was noted that at one time, some of the controls were operated by an electric motor however most of them have become defective. Some of the systems are now operated manually. This type of operation is more difficult and could create a possible security risk. It is recommended that the door control and cell door motor systems be replaced in the cell blocks. This estimate is for 5 door control systems and 300 cell door motors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2250000
0095ELE1 | LIGHTING UPGRADE | 0095 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55965
0096SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0096 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 111720
0109HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0109 | The air handler, fan coils and related equipment are original to the building, 1981. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 09 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 468060
0114PLM2 | INSTALL 40 GALLON GAS WATER HEATERS | 0114 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3750
0114ELE2 | ELECTRICAL UPGRADE | 0114 | This building was constructed before the high demand for new types of electrical devices were needed. As time progressed the buildings electrical demand has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77500
0114PLM1 | REPLACE DOMESTIC AND WASTE WATER SYSTEMS | 0114 | The sanitary wastewater system is showing signs of deterioration. It was noted that the drains operate adequately. Because of the deterioration, the system is not working to its full potential. Some of the lines are original to the building and are in fair condition. The passage of time and constant heavy use is a contributing factor to problems that arise. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. It is recommended the entire wastewater system be replaced. The domestic water that is supplied to the facility has a high mineral content. This has a detrimental effect on the system. Pipe deterioration is accelerated. Deposits within these pipes restrict water flow as well. It is recommended this system be replaced concurrently with the drain system. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 46000
0114SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0114 | This building is equipped with an automatic fire detection and alarm system, but the system is antiquated. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 1998 Section 7. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6570
0114ELE1 | LIGHTING UPGRADE | 0114 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8760
0103SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0103 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3400
0103ELE1 | LIGHTING UPGRADE | 0103 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85005
0103INT2 | REPAIR FLOORING IN DINING ROOM | 0103 | The painted floor in the dining area needs to be repaired and resealed. A significant amount of foot traffic goes though this building daily and deterioration is occurring. It is showing signs of wear from constant use. This project would provide for the floor to be repaired, patched and resealed with an epoxy floor covering for ongoing upkeep and maintenance. This estimate includes two 5 foot by 5 foot concrete areas to be saw cut removed and replaced at areas that are the most damaged.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45900
0105SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0105 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5100
0114HVA1 | REPLACE AIR CONDITIONERS WITH EVAPORATIVE COOLERS | 0114 | Each separate section is cooled by window-mounted air-conditioners. The units are reaching the end of useful live. With the use and/or occupancy of the each section either being storage, welding or small repairs, an evaporative cooler would operate more efficient. This project would provide funding for the purchase and installation of three evaporative coolers including all required connections to utilities. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0094INT4 | REFURBISH GUN POSTS | 0094 | Disney Films constructed the gun post at this building while making a movie at the prison. It is constructed of wood, sitting atop a non-combustible building. It needs complete refurbishing including flooring, windows, doors and electrical. The soffits and walls are peeling and deteriorating. The gun post is not heated or cooled. The other two gun posts also will need to be refurbished. They are constructed of concrete. Only one of the gun posts has a restroom. They use radiator-heating units, which are inadequate in colder weather. Gun post three has a window-mounted air conditioning unit and an electric resistance-heating unit. The windows are tilt-out metal frame and should be replaced. The roof-mounted spotlights will need to be replaced also. The escape hatches located in the floor, are too small and need to be enlarged. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0022SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0022 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20776
0094EXT3 | REPLACE WINDOWS | 0094 | Some of the existing windows open inward which protrudes into the walkways and are original to the building. Some of the units are cracked or damaged, seals are broken, are difficult to operate and they have reached the end of their useful life. This project would provide funding to replace the window units with new security window units. A total of 352 units was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1056000
0094INT3 | REPLACE FLOORING ADMINISTRATION / VISITATION | 0094 | The floor coverings in this building are in generally poor condition and have reached the end of their serviceable life. The carpeted areas are showing signs of traffic wear and the 12"x12" VCT is loose and separating from the substrate creating a potential tripping hazard. This project would provide funding for the replacement of these floor coverings in the administration and visitation areas. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0096SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0096 | The exit signs in this building are older types or are missing. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 7650
0094INT2 | INTERIOR FINISHES | 0094 | The interior walls, ceilings and cells of this building should have a new application of paint in the next two to four years for proper upkeep and maintenance. Prior to painting, all surfaces should be repaired, and additional funds have been included to address the extensive wall repairs. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 743757
0099HVA1 | HVAC UPGRADE | 0099 | The air handler, fan coils and related equipment have reached the end of their expected life. The building does not have a cooling system. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80640
0107SEC3 | REPLACE CELL DOORS | 0107 | Housing Unit No. 7 was constructed in 1981. The cell doors are original construction. They are damaged from inmate abuse and constant use and could become a security concern for staff and inmates. This project would provide for the replacement of the cell doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192000
0105ADA1 | ADA PROJECTS / RESTROOM REMODEL | 0105 | A separate public and inmate visitation restroom is present in this building. They does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with ICC/ANSI A117.1-2002 Sections 603 - 604 and 2006 IBC Chapter 11. Given the current configuration of the restrooms, the work will include the installation of a new water closet, a urinal, sink, and stall; grab bars, faucets, mirrors, dispensers and hardware. Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be replaced and/or relocated to comply with ADA requirements. This housing unit is a lockdown unit which does not have ADA compliant cells and shower. This project also includes funding for retrofitting 2 cells into ADA compliant cells and remodeling one shower unit into an ADA compliant shower unit. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 80000
1410ENR1 | LIGHTING UPGRADE | 1410 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project also includes the replacement of spot lights on the exterior of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3375
0112ELE1 | LIGHTING UPGRADE | 0112 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2975
1414EXT1 | DEMOLISH MAINTENANCE WAREHOUSE 2 | 1414 | The maintenance warehouse 2 contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE WAREHOUSE 2 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1950 | 1288 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
1407EXT1 | DOG KENNEL DEMOLITION | 1407 | The Dog Kennel contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. It has not been occupied for years. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. The existing stone was quarried on the prison site and it is suggested that the stone be salvaged for future use at the discretion of the Department of Corrections. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | DOG KENNEL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1200 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 12000
0101EXT2 | DEMOLISH WATER TANK | 0101 | The existing water tank is not used for water storage, but it is used for maintenance storage. This was a quick remedy for needed storage space. This building contains numerous code and safety issues including but limit to rodent infestation and improper ventilation. The tank is dilapidated and deteriorating and has reached the end of its useful like. This project would provide funding for the demolition of the water tank. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | WATER TANK STORAGE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1969 | 2375 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 23750
0114SFT3 | CONSTRUCT OCCUPANCY SEPARATION WALLS | 0114 | The building has low hazard storage adjacent to the welding shop. The low hazard storage areas are S-2 occupancy. The welding shop is H-4 occupancy. The 2003 IBC table 302.3.2 states that where these occupancies are adjacent to each other a 1-hour occupancy separation wall is required. This project would provide for the construction of a 1-hour occupancy separation walls be constructed on either side of the welding shop. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20000
1408INT1 | INTERIOR FINISHES | 1408 | The interior finishes are in fair to poor condition. It is recommended that the interior walls be painted in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59440
1403EXT3 | EXTERIOR FINISHES | 1403 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finishes are faded and damaged to a point where the concrete is showing wear and deterioration. This project would provide funding for the exterior building envelope other than the roof, including painting, staining, or other applied finishes and caulking around windows, flashing, fixtures and other penetrations. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9360
1410PLM1 | REPLACE PLUMBING SYSTEM AND INSTALL WATER HEATER | 1410 | The building's sanitary wastewater system is showing signs of deterioration. It was noted that the drains operate slowly. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. It is recommended the wastewater system be replaced. The building's domestic water that is supplied to the facility has a high mineral content. This has a detrimental effect on the system. Pipe deterioration is accelerated. Deposits within these pipes restrict water flow as well. It is recommended this system be replaced concurrently with the drain system. The water closet and lavatory are reaching the end of their useful life. It is recommended these fixtures be replaced. For sanitation purposes, it is recommended a water heater be installed in this guard tower. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0114SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0114 | The exit signs in this building are older types. Illuminated exit signs shall be marked per 2003 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/19/2006. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4000
1410HVA1 | HVAC UPGRADE/INSTALLATION | 1410 | The heating unit appears to be original to the building. The unit is a forced-air-gas-type. The building is cooled by an evaporator cooler which is severely scared and has reached its normal life cycle. This project would provide for a complete HVAC system to be installed in the building including air handlers, duct work, connections to existing utilities, seismic bracing and an energy managements system. Design of the system is not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0107SEC2 | EXTERIOR DOOR REPLACEMENT | 0107 | The existing exterior doors to the housing unit are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors were used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 07 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 39000
0102EXT2 | DEMOLISH OLD BUTCHERS SHOP | 0102 | The Old Butchers Shop contains numerous code and safety issues including but not limited to rodent infestation, missing windows and doors, and possible structural deficiencies. Also, the building is located outside of the secure area of the prison and could be accessed by the public. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. The sandstone masonry has historic value and should be salvaged for future renovations. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD BUTCHERS SHOP (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 300 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3000
0103INT3 | REPAIR WALLS IN DISHWASHING AREA | 0103 | The dishwashing area has a large room where carts and other large items are washed. The walls are CMU and the ceiling is gypsum board. This room is severely damage and deteriorating from moisture and water overspray. This project would provide for the installation of fiberglass reinforced panels (FRP) on the walls, and an epoxy based paint on the ceiling. Prior to painting all damaged surfaces should be repaired and prepped for paint as required. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 9000
0112SFT1 | SEISMIC GAS SHUT OFF | 0112 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #1 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 850 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
0113EXT2 | DISCONTINUE BUILDING USE | 0113 | The existing Warden’s House is dilapidated and deteriorating. It contains numerous code and safety issues including, but not limited to an upper level exterior door without a deck or stairway, rodent infestation, broken or missing doors and windows, possible asbestos contamination and broken or missing electrical fixtures. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the buildings to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure The public/personnel should not be allowed to enter or use this building. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INVESTIGATION/OLD WARDENS HOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1957 | 2880 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0114EXT1 | STONE RE-POINTING | 0114 | The existing building exterior is unreinforced natural stone that was quarried directly from the correctional facility site. Some portions of this structure are over 50 years old. There are numerous areas where the mortar is failing, missing and not sealed properly due the age, settling and exposure to the weather. This project would provide for the cleaning, repair and re-pointing of the exterior stone work. | STORAGE & MAINTENANCE OFFICE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1952 | 2190 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21900
0120SFT2 | SEISMIC GAS SHUT OFF | 0120 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COTTAGE #3 (NSP) LOCATED AT WSCC(VACANT) | 9989 | Correct | NSP |  | Carson City | 1953 | 930 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
1403INT1 | INTERIOR FINISHES | 1403 | The interior finishes are in poor condition. The interior finishes are faded and damaged to a point where the concrete is showing wear and deterioration. This project would provide funding for the interior walls and ceiling to be painted. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3120
1403ELE1 | LIGHTING UPGRADE | 1403 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project also includes the replacement of spot lights on the exterior of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4680
1410INT1 | INTERIOR FINISHES | 1410 | The interior wall, floor and ceiling finishes are in poor condition. The interior finishes are faded and damaged to a point where the concrete walls and floors are showing wear and deterioration. This project would provide funding for the interior walls, floors and ceilings to be painted on the lower and upper levels. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5400
0096SFT3 | STAIRWAY HANDRAIL INSTALLATION | 0096 | The existing concrete exterior stairs at the entry are lacking handrails as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for tubular steel framed handrails to be installed. Painting is included in this estimate. This project should be coordinated with the ADA ramp project. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 5000
0096EXT2 | EXTERIOR FINISHES | 0096 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the protection of the exterior of the building. Included in the cost is sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the project be completed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 15960
0105SFT2 | INSTALL FIRE ALARM SYSTEM | 0105 | The fire alarm system is original to the building and is due for an upgrade. This project would provide for the installation of a fully monitored fire alarm system in the housing unit. When completed, the new system will provide visual, as well as audible notification. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 55517
1402INT4 | SUSPENDED CEILING REPLACEMENT | 1402 | The building has a suspended acoustical tile ceiling system. The t-bar framing is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14750
1402SFT3 | SEISMIC RETROFIT | 1402 | This building is constructed of sandstone masonry walls on the exterior and wood framed interior walls and roof. The structure requires seismic strengthening to meet current life safety codes. This portion of the structure was built in the early 1900's and should be retrofitted to meet today's seismic codes. This project would provide for a seismic upgrade and retrofit to this facility. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 73750
1402EXT1 | EXTERIOR FINISHES | 1402 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 14750
1402INT3 | INTERIOR FINISHES | 1402 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7375
0098HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0098 | The air handler, fan coils and related equipment are original to the building, 1976. The building does not have a cooling system and the equipment is has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 124110
0022INT2 | REPLACE EXISTING FLOORING | 0022 | The floor coverings in this building are in generally poor condition and have reached the end of their serviceable life. The carpeted areas are showing signs of traffic wear and the 12"x12" vinyl composition tile (VCT) is loose and separating from the substrate creating a potential tripping hazard. In April of 1989 an asbestos survey was conducted. It was reported that in some areas of the buildings asbestos was present. This project would provide for the replacement of these floor coverings with new VCT. This project includes removal and disposal of the asbestos. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29680
0098EXT2 | REPLACE ROOF | 0098 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next one to two years with a new single-ply roofing system to be installed over the existing metal roofing system. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 82740
0098ADA2 | ADA RESTROOM PROJECT | 0098 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucet, mirror, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0098EXT1 | EXTERIOR FINISHES | 0098 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the protection of the exterior of the building. Included in the cost is sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the project be completed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 8274
0022ADA2 | ADA RESTROOM REMODEL | 0022 | The existing restroom is not ADA compliant. This project would provide for the remodeling of the restroom into a unisex ADA compliant facility including a sink, toilet, grab bars, mirror, plumbing jacket and signage as indicated in the 2006 IBC Chapter 11, Section 1109.2.1. Minor plumbing modifications and room reconfiguration may be required and this cost estimate includes funds for minor modifications including new vinyl composition flooring, and a new 3'-0" wide door with lever action door handles. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 30000
0098ELE1 | LIGHTING UPGRADE | 0098 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31027
0098INT1 | INTERIOR FINISHES | 0098 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20685
1402ELE1 | LIGHTING UPGRADE | 1402 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11062
1402INT2 | REPLACE CARPET | 1402 | The interior floor covering is mostly carpet and is showing signs of extreme wear. Several areas are worn out and tears are evident throughout the carpeted areas causing a tripping hazard. This project would replace the existing broad loom carpet with carpet tile. Carpet tile would allow for future replacement of only those sections of carpet that are worn or damaged without the need to remove the entire carpeted area. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 14750
0106SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0106 | This building does not have an automatic fire suppression system. The 2006 IBC Chapter 903.2.5 states that "An automatic sprinkler system shall be provided throughout buildings with a Group I fire area". This building is an I-3 occupancy with sleeping quarters. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 109214
0094ENV1 | ENVIRONMENTAL HAZARDS SURVEY | 0094 | An inspection was performed on this building in 1989 for asbestos containing materials (ACM). Not included in the previous testing was lead paint and other possible environmental hazards. This project would provide funding to complete a building survey of potential environmental hazards located inside the building and on the roofing system. Future projects and their associated costs that may arise from the results of the survey are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0022EXT1 | EXTERIOR FINISHES | 0022 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 29680
0096EXT1 | REPLACE ROOF | 0096 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next one to two years with a new single-ply roofing system to be installed over the existing metal roofing system. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 159600
0106SEC1 | REPLACE SECURITY GLAZING | 0106 | This housing unit is a tiered structure. It house inmates on two floors. One entrance door accesses the building. To enter the cellblock, inmates pass through a central assembly area. Four sets of double security doors are used to access the inmate rooms. The glazing in these doors gets broken and damaged frequently and should be replaced with security glazing. Security glazing is also located in the partition wall between the sally port and the guard station. These windows also experience damage and should be replaced with safety glazing. This project would provide funding for the purchase and installation of safety glazing. It is recommended that this project be implemented in the next two years. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 32000
0022ELE1 | LIGHTING UPGRADE | 0022 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22260
1402ADA1 | ADA PROJECTS | 1402 | The building is lacking ADA compliant entry access, signage and restrooms. The restroom adjacent to the courtroom is not accessible. Grab bars and proper paper dispensers are necessary to make it comply. Currently the mirror height in this restroom is 49" above the finished floor. ICC/ANSI A117.1 - 2003 Section 603.3 states: "Mirrors shall be mounted with the bottom edge of the reflecting surface 40 inches maximum above the floor or ground". The existing railing on the accessible ramp that leads to the front door of the courthouse does not have proper extensions and is too low at 29 1/2". ICCANSI A117.1 - 2003 Section 505.4 states: "Top of gripping surfaces of handrails shall be 34" minimum and 38" maximum vertically above stair nosing and ramp surfaces." The existing doors in this facility have locking knob-type door hardware. ICC/ANSI A117.2003 section 404.2.6 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. The exterior door and entrance used by the inmates is not ADA compliant. This project would provide for an ADA complaint inmate entrance including door and hardware and floor modifications. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 was referenced for this project. This project would provide funding to bring the building into ADA compliance. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 60000
0022INT1 | INTERIOR FINISHES | 0022 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14840
0106EXT1 | EXTERIOR FINISHES | 0106 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 78010
0106INT1 | INTERIOR FINISHES | 0106 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39005
0106ENR1 | LIGHTING UPGRADE | 0106 | Existing building lighting fixtures, T-12s, are older fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8s with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | HOUSING UNIT 06 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1981 | 7801 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58507
0096HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0096 | The air handler, fan coils and related equipment are original to the building, 1976. The building does not have a cooling system and the equipment has reached it's expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation equipment, exhaust fans and installation of a cooling system. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 239400
1402SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1402 | The exit signs in this building are older types or painted on the walls. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups along all of the required exit pathways. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1700
1410SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 1410 | There is inadequate security camera coverage and insufficient recording equipment in the Guard Tower. This is a safety issue for the public, staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of additional surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 20000
2573INT1 | INTERIOR FINISHES | 2573 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOBBY CRAFT STORE | 9989 | Correct | NSP |  | Carson City | 0 | 320 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
2545EXT1 | EXTERIOR FINISHES | 2545 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 16800
2573EXT1 | EXTERIOR FINISHES | 2573 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOBBY CRAFT STORE | 9989 | Correct | NSP |  | Carson City | 0 | 320 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 3200
0096SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0096 | There is no security camera or recording system in the Gymnasium. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 95000
2569EXT1 | EXTERIOR FINISHES | 2569 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is priming and painting as well as caulking flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOILER ROOM STORAGE SHED (VACANT) | 9989 | Correct | NSP |  | Carson City | 0 | 80 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 160
0103SFT0 | UPGRADE FIRE ALARM SYSTEM | 0103 | This building has an automatic fire detection and alarm system but it appears to be original to the facility. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 79338
0098SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0098 | There is no security camera or recording system in the Book Bindery. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 75000
0029EXT2 | EXTERIOR FINISHES | 0029 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is repairing any cracks and sealing the stone masonry as well as caulking the windows and other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD PUMPHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 64 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 320
0103SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0103 | There is no security camera or recording system in the Culinary/ Dining Hall. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
1402HVA1 | REPLACE HVAC SYSTEM | 1402 | The Courthouse has a roof top packaged HVAC unit which appears to be more than 20 years old. This project would provide for installation of a new roof mounted packaged HVAC unit to be installed. It is recommended that this project be implemented in the next two to three years to avoid possible failure and emergency funding for replacement. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36875
1402SFT4 | INSTALL FIRE ALARM SYSTEM | 1402 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 10325
9989ELE2 | REPLACE ELECTRICAL SWITCH GEAR | 9989 | The main electrical switch gear for the site is located east of the Boiler Plant and is approximately 30 years old. The equipment has reached the end of its expected life and should be scheduled for replacement. This project would provide for removal and replacement of the existing switch gear and includes connection to the emergency generator. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
1402SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 1402 | There is no security camera or recording system in the Courthouse. This is a safety issue for the public, staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire courthouse and all required connections to existing utility systems. | COURTHOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 1475 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
9989SIT4 | REPLACE SALLY PORT GATES | 9989 | There are three 16’ high motorize gates used at the prison. One is located near the Main Gate / Tower #1 and two are located at Tower #2. The gates are problematic and are having difficulty opening and closing. When the gates are inoperable this creates security issues for the inmates and staff. This project would provide for the replacement of the three motorized gate assemblies. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0095SFT2 | INSTALL FIRE ALARM SYSTEM | 0095 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 52234
0094PLM2 | REPLACE SEWER / WASTE WATER LINES | 0094 | The sewer / waste water infrastructure in the building is over 50 years old except for some small areas that have been repaired or replaced over the years as needed. Some of the sanitary sewer pipe, hangers, connectors and couplers have or are deteriorating to a point where raw sewage may be leaking in some areas. The waste vents in the cell block chases are too close to the exhaust vents on the roof and in unit 5, some have been damaged and to not vent properly. The waste lines in unit 2 have failed. This may be a potential health hazard. This project would provide for the removal and installation a new sewer / waste water infrastructure in the building including all connections, supports, anchoring. Some of the waste lines have been upgraded in the Sagebrush basement area in a past Capital Improvement Project. 8,000 lineal feet of cast iron pipe was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800000
0094PLM3 | REPLACE DOMESTIC WATER DISTRIBUTION SYSTEM | 0094 | The majority of the domestic water supply lines in the building are over 50 years old. At the time of the 2009 survey, all of unit 5 and some of unit 3 were having problems and the system was not 100 percent operational. Some of the pipe, hangers, connectors and couplers are deteriorating and water leaks are developing. Dielectric corrosion is occurring between different types of pipe metals, internal corrosion is occurring on the 4" pipe and compression clamps are located in areas where leaks have occurred. Other small repairs have been done over time as needed to keep system operational. A break in the pipe has the potential to short out the power supply, alarm system, flood the lowest levels of the building and presents a safety hazard. This project would provide funding for the removal and installation a new domestic water supply piping system, check and mixing valves and isolation valves. 8,000 lineal feet of steel piping was used in this estimate. If copper pipe is used, the price could double. Removal and/or abandonment of the existing system is included in this estimate. A project for replacing the utilities in the "Sagebrush" basement area was completed in 2001. This project number was 95-M27. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 800000
0094HVA3 | REPLACE HVAC SYSTEM | 0094 | The building is heated by low pressure steam. The steam pipes are deteriorating, leaking under the concrete has occurred, and other areas of the steam piping system has had leaks. There is a steam leak currently in unit 5. The Administration portion of the building is cooled by a central air-conditioning system. This section also requires evaporative coolers and windows air-conditioners to supplement the cooling. The cell block areas have roof and wall mounted evaporative coolers which are old and inefficient. The air distribution system in this facility is reaching the end of its useful life or is non-existent. The exhaust system in the chase ways no longer operates properly. There is not adequate fresh air supply in the cell areas as required in the IMC table 403.3. These systems appear to be over 25 years old and no longer energy efficient and some do not function. This project would provide funding for the design and engineering of a total renovation of the heating, air-conditioning and ventilation system. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4781295
0094ELE3 | CELL BLOCK LIGHTING CONTROL SYSTEM | 0094 | The lights for cell block units' 3 and 5 are controlled in the hallway by switches. The maintenance staff has installed lock boxes to protect them from inmate abuse. However the inmates have broken all of the lighting controls. This is a safety issue as the correctional officers need to be able to control the lighting. This project would provide for the design, purchase and installation of a lighting control unit to be located in the correctional offices room. This project should be coordinated with the electrical system upgrade project which may reduce the cost estimate if done simultaneously. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
0094EXT4 | STONE MASONRY RE-POINTING | 0094 | The existing building exterior is natural sandstone that was quarried directly from the correctional facility site. Some portions of this structure are over 100 years old. There are numerous areas where the mortar is failing, missing and not sealed properly due the age and exposure to the weather. This project would provide for the cleaning, repair and re-pointing of the exterior stone work. Due to the vertical nature of the building, scaffolding will be required to accomplish this project and is included in this estimate. This project does not include the exterior stairway on the southwest side of the building. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 531255
0095INT1 | INTERIOR FINISHES | 0095 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37310
0094SEC2 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0094 | There is no security camera or recording system for this building except for a few isolated areas like the visitation area. This is a safety issue for staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire building and all required connections to existing utility systems. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500000
2171INT1 | INTERIOR FINISHES | 2171 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0022SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0022 | There is no security camera or recording system in the Chapel/ Six Post. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
1408EXT3 | EXTERIOR FINISHES | 1408 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 59440
0098ADA1 | INSTALL LEVER ACTION DOOR HARDWARE | 0098 | The existing doors in this facility have locking knob-type door hardware and do not meet the requirements for ADA accessibility. ICC/ANSI A117.1-1998 section 404.2.7 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. This project would provide for the purchase and installation of lever action door hardware to be placed on all the interior doors. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOOK BINDERY (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 4137 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 7500
1409SIT1 | EXTERIOR STAIRS | 1409 | The 2006 IBC Chapter 1009.5.1 requires the horizontal slope of stair treads in any direction not to exceed 2 percent. Chapter 1009.10 requires handrails be installed and a landing is required at the top and bottom of the stairs. There is an existing concrete stairway that provides access between the street and the building that is not within these required code parameters and is showing signs of settling and separation. This project would provide for the rebuilding of the concrete stairway to meet the 2006 IBC code requirements. Two handrails, one on each side of the stairway are included in this cost estimate. This project or a portion there of was previously recommended in the FCA report from July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | PROPERTY WAREHOUSE 1/OLD ARMORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1950 | 1800 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 7500
2171SFT3 | HANDRAIL INSTALLATION | 2171 | The 2006 International Building Code 1009.11 requires handrails on each side of stairways. The building has a set of stairs to access the offices on the mezzanine above the cafeteria and restrooms. The stairway has only one handrail. This project would provide for the installation of another handrail on the stairway to match the existing handrail. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 2500
2171SFT2 | JANITOR CLOSET WALL PROTECTION | 2171 | The mop sinks in the Janitor's Closets are mounted adjacent to gypsum board that is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54 inches above the floor finish. This project includes FRP on both Janitor's Closets that currently do not have wall protection. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2171SFT1 | SEISMIC GAS SHUT OFF VALVE | 2171 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3500
2545SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2545 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 23520
2568SFT1 | STAIRWAY / HANDRAIL REPAIRS | 2568 | The existing stairs on the east side are constructed of wood, which have deteriorated to point where they are unsafe to use and do not meet current building codes. Also, the hand rails do not meet the requirements in the 2012 IBC section 1009.11. This project would provide for the removal and disposal of the existing stairs and construction of a new wood framed set of stairs and handrails. The door swings outward, therefore, a three foot wide landing will be required at the top of the stairs and is included in this estimate. | CHEMICAL STORAGE BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 0 | 308 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4500
0041INT1 | INTERIOR FINISHES | 0041 | The interior finishes are in fair to poor condition. It is recommended that the interior walls be painted at least once in the next two years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD 5TH STREET TOWER (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 100 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1000
9989SIT6 | SITE DRAINAGE STUDY | 9989 | The Nevada State Prison site has many areas with steep slopes, stone terraces, and paved areas that do not drain properly during a heavy precipitation event. There are no storm drains or designated channels for water to flow. This has caused areas of erosion around some of the structures and pavement. This project would provide for a site drainage study to be performed by a civil engineer to address the above mentioned items. Future projects may arise from the findings contained in the report which are not included in this estimate. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0022ADA1 | INSTALL LEVER ACTION DOOR HARDWARE | 0022 | The existing doors in this facility have locking knob-type door hardware and do not meet the requirements for ADA accessibility. ICC/ANSI A117.1-1998 section 404.2.7 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. This project would provide for the purchase and installation of lever action hardware to be placed on all the interior doors. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6750
9989SIT7 | TELECOMMUNICATION / SECURITY SYSTEM INFRASTRUCTURE | 9989 | There are projects proposed for adding a fully monitored fire alarm, security and telecommunications system for the entire institution. This project would provide for the underground infrastructure improvements site wide excluding the buildings including excavation, conduit installation, backfill, and pull boxes as required for the systems. | NEVADA STATE PRISON SITE | 9989 | Correct | NSP |  | Carson City | 1868 |  | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 975000
0041EXT2 | EXTERIOR FINISHES | 0041 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior paint is peeling; the caulking around the windows, flashing, fixtures and other penetrations is failing. This project would provide funding for the painting of the exterior of the building. Including in the cost is the sanding, priming, filling in the crack, caulking of the windows, flashing, fixtures and all other penetrations. This project should be completed in the next two years. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | OLD 5TH STREET TOWER (VACANT) | 9989 | Correct | NSP |  | Carson City | 1868 | 100 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1500
1412EXT1 | EXTERIOR FINISHES | 1412 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing of the exterior of the building. Included in the cost is sealing, caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | PUMP HOUSE (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 308 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 1540
0103INT4 | RESURFACE KITCHEN FLOOR | 0103 | The painted concrete floor in the kitchen is worn and damaged and should be resurfaced. This project would provide for the installation of an epoxy based floor covering suitable for food preparation areas and health department specifications. 5,000 square feet of floor area was used to generate this estimate. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
1409EXT2 | EXTERIOR FINISHES | 1409 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the exterior of the building. Included in the cost is sanding, priming, filling in the cracks, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PROPERTY WAREHOUSE 1/OLD ARMORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1950 | 1800 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 18000
0103HVA1 | REPLACE HVAC / VENTILATION SYSTEM | 0103 | The two rooftop packaged HVAC units, two evaporative coolers, two make-up air units and the exhaust fans appear to be more than 20 years old and are reaching the end of their useful life. This project recommends replacement of HVAC and make-up air equipment. It is recommended that this project be implemented in the next two years to avoid possible failure and emergency funding for replacement. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 340020
0105HVA1 | REPLACE HVAC SYSTEM | 0105 | The HVAC system consists of a boiler, air handler and a condenser. It is original equipment and should be scheduled for replacement in the next two to four years to mitigate possible emergency funding due to failure. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 237930
0103PLM1 | INSTALL SEWAGE GRINDER | 0103 | The grease interceptor to the west of the building is not currently operating correctly. The sewage pipes down the line from the interceptor have been clogged with grease and other waste from the kitchen. It is recommended that a sewage grinder be installed between the kitchen sewage lines and the grease interceptor to remedy this problem. This project would provide for the purchase and installation of a sewage grinder and connection to existing sewer system in the Culinary. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0096ADA2 | ACCESSIBLE ENTRANCE RAMP | 0096 | The gymnasium is lacking an accessible entrance into the building. The building is used to allow inmates to play basketball, table tennis and lift weights. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
0105SEC2 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 0105 | There is no security system for this building except for a few isolated cameras which are new according to staff. This is a safety issue for staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 12 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1982 | 7931 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 75000
0763EXT1 | EXTERIOR FINISHES | 0763 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the protection of the exterior of the building. Included in the cost is sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the project be completed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9989 | Correct | NSP |  | Carson City | 1999 | 900 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
0094SFT6 | INSTALL HANDRAILS AT ALL INTERIOR STAIRWAYS | 0094 | All of the existing stairways in the interior of the building do not meet current building codes. Some are missing and they do not have proper extensions or are not at proper heights. This project would provide for the installation of new tube steel handrails at all interior stairways including the housing units. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 50000
0094SFT5 | INSTALL STAIRS / HANDRAILS AT ADMINISTRATION | 0094 | The existing concrete stairs are showing signs of wear and deterioration. The handrails do not meet current building codes for ADA accessibility and handrail extensions and configurations. This project would provide for the removal and replacement of the concrete stairs and handrails. | ADMINISTRATION/CELL BLOCKS (VACANT) | 9989 | Correct | NSP |  | Carson City | 1925 | 106251 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 6500
1403SEC1 | FIRE ALARM SYSTEM INSTALLATION | 1403 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | GUARD TOWER #2 NORTH (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 624 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 4368
1410SEC2 | INSTALL FIRE ALARM SYSTEM | 1410 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MAIN GATE/TOWER #1, NORTHWEST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1963 | 450 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 3150
1411EXT3 | DISCONTINUE BUILDING USE | 1411 | The Old Electric Shop is dilapidated and deteriorating. It contains numerous code and safety issues including, but not limited to rodent infestation, broken or missing doors and windows, non code compliant entry stairs, possible asbestos contamination and broken or missing electrical fixtures. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the U. S. Department of Interior Recommended Guidelines in Preservation Brief 31. Costs related to providing drainage away from the buildings to prevent future water accumulation, pest control and removal of accumulated waste are included. Windows and doors will be secured or covered, and some will include louvers to permit ventilation of the structure The public/personnel should not be allowed to enter or use this building. | OLD ELECTRIC SHOP (VACANT) | 9989 | Correct | NSP |  | Carson City | 1900 | 1930 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 25000
2545SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2545 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. Illuminated exit signs shall be marked per 2006 IBC Section 1011.1. This project would provide funding to install self-illuminating or LED models with internal battery backups as well as emergency egress lighting to provide illumination along the egress route. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 1700
2545SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 2545 | There is no security camera or recording system in the Modular Education Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
2171EXT2 | EXTERIOR FINISHES | 2171 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Including in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE SHOP | 9989 | Correct | NSP |  | Carson City | 2004 | 4000 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 4000
1408SEC1 | SURVEILANCE / SECURITY SYSTEM INSTALLATION | 1408 | There is no security system for this building except for a few isolated cameras. This is a safety issue for staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 13 (VACANT) | 9989 | Correct | NSP |  | Carson City | 1988 | 11888 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 75000
0099PLM1 | BOILER MAINTENANCE | 0099 | The three steam boilers are functioning well and it is important to maintain the equipment including replacing worn parts. The maintenance staff indicated several specific parts that will be due for replacement in the next 2-3 years in order to ensure the equipment is functioning to its maximum potential. These parts include a valve for the Deaerator tank and a fan motor for Boiler #1. This project would provide for the purchase and installation of these parts and includes extra funds for other necessary maintenance. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0095EXT3 | REPLACE WINDOWS | 0095 | The windows are single pane, open inward which protrudes into the isles and are original to the building. Some of the units have several cracks, seals are broken, are difficult to operate and they have reached the end of their useful life. This project would provide funding to replace the window units with new double pane energy efficient units. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | INDUSTRIAL/LICENSE PLATE FACTORY(VACANT) | 9989 | Correct | NSP |  | Carson City | 1962 | 7462 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30250
0096SFT4 | FIRE ALARM SYSTEM UPGRADE | 0096 | This building is equipped with an automatic fire detection and alarm system, but the system is old, does not meet current code requirements and is missing in some locations. It is recommended that the fire detection and alarm system be upgraded to a fully monitored. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements and building codes. This project should be coordinated with the fire sprinkler install project. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 55860
0103EXT3 | EXTERIOR DOOR REPLACEMENT | 0103 | The existing exterior doors to the Culinary / Dining Hall are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 4 doors were used to generate this estimate. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
2545SFT2 | INSTALL FIRE ALARM SYSTEM | 2545 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 11760
2545INT1 | INTERIOR FINISHES | 2545 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MODULAR EDUCATION BUILDING (VACANT) | 9989 | Correct | NSP |  | Carson City | 2002 | 1680 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
0099SFT3 | INSTALL FIRE ALARM SYSTEM | 0099 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fully monitored fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2002 Section 7. | BOILER PLANT (VACANT) | 9989 | Correct | NSP |  | Carson City | 1958 | 2688 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 18816
0096ADA1 | ADA RESTROOM PROJECT | 0096 | The restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new shower stall, toilet, sink, shower, grab bars, faucet, mirror, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 30000
0096INT2 | RESEAL FLOORING | 0096 | The flooring system in the weight and shower area needs to be resealed. A significant amount of foot traffic goes though this building daily and deterioration is occurring. It is showing signs of wear from constant use and abuse. This project would provide for the existing floor to be ground, patched and resealed with an epoxy resin for ongoing upkeep and maintenance. This project or a portion there of was previously recommended in the FCA report dated 09/07/1999 and July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | GYMNASIUM (VACANT) | 9989 | Correct | NSP |  | Carson City | 1976 | 7980 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14700
0103EXT2 | REPLACE ROOF | 0103 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that this building be re-roofed in the next five years to be consistent with the roofing program and the end of the warranty period. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Four to Ten Years | Long-Term Needs | 3 | 226680
0022HVA1 | REPLACE HVAC SYSTEM | 0022 | The Chapel / Six Post currently has only ducted heat and evaporative cooling which is in need of replacement. This project would provide for a cooling system to be installed in the building. This project or a portion there of was previously recommended in the FCA report dated July 2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/10/2009. | CHAPEL/SIX POST (VACANT) | 9989 | Correct | NSP |  | Carson City | 1971 | 2968 | 2009-02-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89040
0103ADA1 | ADA ACCESSIBILITY PROJECTS | 0103 | The Culinary / Dining facility is lacking ADA compliant facilities. There is a restroom present inside which also does not meet ADA requirements. This project would provide for ADA improvements which include at a minimum remodeling the existing restroom into a new ADA compliant restroom, lever action door hardware, an ADA compliant dining table with proper clearances and adding an ADA accessible food service counter. The ADA accessible route into the building is addressed in the site portion of this report. | CULINARY/DINING HALL (VACANT) | 9989 | Correct | NSP |  | Carson City | 1966 | 11334 | 2009-02-10 | Immediate to Two Years | Currently Critical | 1 | 35000
2562EXT2 | ROOF REPLACEMENT | 2562 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 8-10 years to be consistent with the roofing program and the end of the warranty period. | MICROWAVE BUILDING | 9990 | Admin | PubWorks | B&G | Carson City | 2004 | 480 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 5760
2562EXT1 | EXTERIOR FINISHES | 2562 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the stone walls caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MICROWAVE BUILDING | 9990 | Admin | PubWorks | B&G | Carson City | 2004 | 480 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0127SFT4 | SPRAY FINISHING BOOTH UPGRADES | 0127 | There is a spray finishing booth in the building that does not meet the design and fire safety guidelines outlined in the International Fire Code (IFC) and the National Fire Protection Association (NFPA) standards. Section 2404 of the 2012 IFC includes design codes for spray finishing rooms including constructing the room with approved noncombustible materials, proper means of egress, installation of an approved automatic fire-extinguishing system, fire extinguishers and mechanical ventilation requirements. NFPA 33 outlines standards for spray application areas including electrical, ventilation and fire protection systems and rules for drying and curing processes, operations and maintenance. This project would provide for installation of a spray finishing room in the building that complies with the IFC and NFPA to ensure the safety of the occupants. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
0127INT3 | INTERIOR DOOR REPLACEMENT | 0127 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 12 doors. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0128EXT5 | ROOF REPLACEMENT | 0128 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1995 and is now 19 years old. The roof warranty for this roof expired on 5-8-2012. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0128EXT4 | EXTERIOR DOOR REPLACEMENT | 0128 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 11 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44000
0128INT2 | INTERIOR FINISHES | 0128 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0138ENV1 | ROOF CLEANUP | 0138 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0144EXT3 | ROOF REPLACEMENT | 0144 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
0128EXT3 | EXTERIOR FINISHES | 0128 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls, repairing and painting the stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0147EXT4 | ROOF REPLACEMENT | 0147 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
0126INT6 | JANITORS CLOSET REPAIRS | 0126 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0127EXT2 | EXTERIOR FINISHES | 0127 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls, repairing and painting the stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0127INT2 | INTERIOR FINISHES | 0127 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0127EXT3 | EXTERIOR DOOR REPLACEMENT | 0127 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 2 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0127EXT4 | OVERHEAD DOOR REPLACEMENT | 0127 | There are seven 8'x10' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0141ENV1 | ROOF CLEANUP | 0141 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0140ENV1 | ROOF CLEANUP | 0140 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0139ENV1 | ROOF CLEANUP | 0139 | The roof on this building was in fair condition at the time of the survey but pigeon debris had built up significantly in certain areas. Pigeon droppings, nests and dead pigeons have built up around the HVAC equipment and roof drains. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the pigeon debris by a licensed pest control business using cleaning materials approved by the roofing manufacturer. Using the proper cleaning agents per the roofing manufacturer should not void the warranty. The roof should be cleaned as soon as possible. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
2006EXT2 | ROOF REPLACEMENT | 2006 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | BIKE STORAGE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1963 | 384 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4608
1436EXT3 | ROOF REPLACEMENT | 1436 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1993 and is now 21 years old. The roof warranty for this roof expired on 9-27-2009. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 95640
0142EXT4 | ROOF REPLACEMENT | 0142 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 163692
0149EXT5 | ROOF REPLACEMENT | 0149 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 127608
0129EXT5 | ROOF REPLACEMENT | 0129 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1999 and is now 15 years old. The roof warranty for this roof expires on 8-8-2015. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 196248
0146EXT4 | ROOF REPLACEMENT | 0146 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10368
0145EXT4 | ROOF REPLACEMENT | 0145 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0143EXT5 | ROOF REPLACEMENT | 0143 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 2001 and is now 13 years old. The roof warranty for this roof expires on 2-27-2019. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 6600
0139EXT5 | ROOF REPLACEMENT | 0139 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 259032
0138EXT5 | ROOF REPLACEMENT | 0138 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 259032
0137EXT4 | ROOF REPLACEMENT | 0137 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 2001 and is now 13 years old. The roof warranty for this roof expired on 2-27-2019. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 7-8 years to be consistent with the roofing program. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 195672
0135EXT6 | ROOF REPLACEMENT | 0135 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1993 and is now 21 years old. The roof warranty for this roof expired on 9-27-2009. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57216
0133EXT5 | ROOF REPLACEMENT | 0133 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1991 and is now 23 years old. The roof warranty for this roof expired on 7-16-2008. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 215940
0132EXT4 | ROOF REPLACEMENT | 0132 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2352
0131EXT6 | ROOF REPLACEMENT | 0131 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126720
0130EXT3 | ROOF REPLACEMENT | 0130 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1999 and is now 15 years old. The roof warranty for this roof expires on 8-8-2015. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126720
0150EXT6 | ROOF REPLACEMENT | 0150 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1997 and is now 17 years old. The roof warranty for this roof expired on 12-15-2013. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39900
2004INT3 | JANITORS CLOSET REPAIRS | 2004 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0125EXT5 | ROOF REPLACEMENT | 0125 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110580
0150ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0150 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0150INT3 | JANITORS CLOSET REPAIRS | 0150 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0124EXT5 | ROOF REPLACEMENT | 0124 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1997 and is now 17 years old. The roof warranty for this roof expired on 12-15-2013. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
1436EXT2 | EXTERIOR FINISHES | 1436 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 38350
2004EXT3 | ROOF REPLACEMENT | 2004 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in the 1980's. It is recommended that the single-ply roof on the older half of the structure of this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
2004INT2 | INTERIOR FINISHES | 2004 | The interior finishes are in fair condition. Approximately 1/3 of the interior walls are painted. It is recommended to paint the interior walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2004EXT2 | EXTERIOR FINISHES | 2004 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is scraping, priming and painting the painted concrete and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63900
1673HVA1 | BOILER REPLACEMENT | 1673 | The hot water boilers servicing the building were installed more than 20 years ago and should be scheduled for replacement. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this older equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on two 1,145 MBH maximum output hot water boilers and associated equipment. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
0126EXT5 | ROOF REPLACEMENT | 0126 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43008
2785INT1 | INTERIOR FINISHES | 2785 | The interior finishes are in fair condition. About 10% of the interior walls are covered by painted gypsum board. It is recommended to paint the interior walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT #10 | 9990 | Correct | NNCC |  | Carson City | 2008 | 23780 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0127EXT5 | ROOF REPLACEMENT | 0127 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1997 and is now 17 years old. The roof warranty for this roof expired on 12-15-2013. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 126720
1673SEC1 | CELL DOOR LOCK REPLACEMENT | 1673 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1300000
1436INT4 | INTERIOR FINISHES | 1436 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38350
1436ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1436 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
1436ELE2 | ELECTRICAL UPGRADE | 1436 | This building was constructed before the high demand for electrical services were needed for maintenance equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115050
1648EXT3 | EXTERIOR FINISHES | 1648 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89000
0150PLM1 | WATER HEATER REPLACEMENT | 0150 | There is a 19 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1648INT3 | INTERIOR FINISHES | 1648 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 222500
0135SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0135 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
0150SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0150 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1700
0138SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0138 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10793
0139SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0139 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10793
0137SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0137 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0133SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0133 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5500
0131SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0131 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 3800
0130SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0130 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 3500
0137ADA1 | ADA RESTROOM UPGRADE | 0137 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restrooms in the gym and in the classroom hallway into ADA compliant restrooms. These items may include sinks, toilets, showers, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 90000
0128SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0128 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0126ADA1 | ADA RESTROOM UPGRADE | 0126 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0140SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0140 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10793
0127HVA1 | HVAC EQUIPMENT REPLACEMENT | 0127 | The existing HVAC system consists of fan coil units, hydronic heaters and evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0125INT1 | FLOORING REPLACEMENT | 0125 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. There is asbestos in the floor tile mastic that will need to be abated by a licensed abatement professional. It is recommended that the VCT and carpet be replaced. Additional monies are included in this project for asbestos removal and disposal. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 92150
0127SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0127 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 3500
9990ADA1 | ADA SITE UPGRADES | 9990 | The Command Post/ Operations/ Education building and the Education building are lacking an accessible entrance into the buildings from the yard. The buildings are used by the inmates and staff on a daily basis and are required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the buildings. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 70000
0125SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0125 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2004SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2004 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6000
0141EXT3 | EXTERIOR DOOR REPLACEMENT | 0141 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 9 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0142EXT2 | WINDOW REPLACEMENT | 0142 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110400
0127ADA1 | ADA RESTROOM UPGRADE | 0127 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0149SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0149 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
9990SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9990 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas, loading docks, exercise yards and the perimeter road. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 600,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0137ADA2 | ADA SIGNAGE | 0137 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0136INT1 | CEILING SYSTEM REPLACEMENT | 0136 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93040
0126SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0126 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0137INT1 | CEILING TILE REPLACEMENT | 0137 | The ceiling in the Gym portion of this building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and many have fallen off of the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. Additional costs would be required if there is asbestos in the tiles or adhesive. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
0149EXT2 | WINDOW REPLACEMENT | 0149 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
0143ELE1 | LIGHTING UPGRADE | 0143 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 825
0142SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0142 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6821
0141SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0141 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6821
0124ADA1 | ADA RESTROOM UPGRADE | 0124 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 30000
1648SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1648 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 6000
0125PLM1 | WATER HEATER REPLACEMENT | 0125 | There is a 120 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is missing proper seismic bracing and an expansion tank. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0129SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0129 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 7500
0131HVA1 | HVAC EQUIPMENT REPLACEMENT | 0131 | The existing HVAC system consists of 2 convectors, 10 hydronic unit heaters and 1 evaporative cooler. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0131ELE1 | ELECTRICAL UPGRADE | 0131 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0131SFT1 | INTERIOR STAIRWAY REPLACEMENT | 0131 | The stairs and handrails between the main floor and the storage loft do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The stairs to the area have become unstable and unsafe from years of use. This project would provide funding to remove and replace the stairway and handrail. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0129INT1 | CEILING REPLACEMENT | 0129 | The ceiling areas in this building are either acoustical tile or gypsum board in poor condition. The ceiling tiles are damaged and stained and some are coming loose from the substrate. The painted gypsum board in the kitchen is soiled and damaged in many areas. Due to their age and continuing deterioration, these ceilings should be scheduled for replacement. The ceiling finishes in food preparation areas shall be rated for food service applications as required by the health department which include but are not limited to a smooth, cleanable surface that is moisture resistant. Additional costs would be required if there is asbestos in the tiles or adhesive. This project or a portion thereof was previously recommended in the FCA report dated 01/12/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 114478
0128EXT1 | WINDOW REPLACEMENT | 0128 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 64800
0128ELE1 | ELECTRICAL UPGRADE | 0128 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
0149HVA1 | HVAC SYSTEM REPLACEMENT | 0149 | The existing HVAC system consists of older air handling units and hot water coils and a cooling tower that is 8 years old. The air handlers and coils are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 2 new air handling units and hot water coils, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 159510
0127SFT1 | INTERIOR STAIRWAY REPLACEMENT | 0127 | The stairs and handrails between the main floor and the storage loft do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The stairs to the area have become unstable and unsafe from years of use. This project would provide funding to remove and replace the stairway and handrail. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0141EXT2 | WINDOW REPLACEMENT | 0141 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 110400
0126ELE1 | ELECTRICAL UPGRADE | 0126 | This building was constructed before the high demand for electrical services were needed for maintenance equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53760
0133ENV1 | DUST COLLECTION SYSTEM REPLACEMENT | 0133 | The existing wood working equipment has partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project will provide for the replacement of several existing systems and installation of additional systems to minimize explosion hazard and disruption to production schedules. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0125EXT1 | WINDOW REPLACEMENT | 0125 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66600
0128HVA1 | HVAC EQUIPMENT REPLACEMENT | 0128 | The existing HVAC system consists of 2 fan coil units and 1 evaporative cooler. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
0124SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0124 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1000
0125ADA1 | ADA RESTROOM UPGRADE | 0125 | There are 9 restrooms in the building. None of these restrooms meet Americans with Disabilities Act (ADA) requirements. A complete retrofit of 3 of the restrooms is necessary. This project would provide funding for construction of a Men's and Women's restroom for staff and one restroom for inmates. These items may include demolition of several walls, new sinks, water closets, grab bars, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 45000
0124INT1 | CEILING TILE REPLACEMENT | 0124 | The ceiling in this building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. Additional costs would be required if there is asbestos in the tiles or adhesive. Given the location of HVAC equipment in the ceiling, this work could be performed concurrent with proposed HVAC equipment replacement. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0124HVA1 | HVAC EQUIPMENT REPLACEMENT | 0124 | The existing HVAC system consists of 4 unit heaters and window mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 4 new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0125HVA1 | HVAC EQUIPMENT REPLACEMENT | 0125 | The existing HVAC system consists of 4 air handling units connected to the central boiler, a chiller, 2 split system air conditioners and window mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 138225
0133HVA1 | HVAC EQUIPMENT REPLACEMENT | 0133 | The existing HVAC system consists of 2 large air handlers in the penthouse. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 269925
0130HVA1 | HVAC EQUIPMENT REPLACEMENT | 0130 | The existing HVAC system consists of a rooftop air handler. It is not energy efficient, insufficient for the spaces and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC unit, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 158400
0126HVA1 | HVAC EQUIPMENT REPLACEMENT | 0126 | The existing HVAC system consists of 2 four-ton condensing units and 2 original Fedderer furnaces. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53760
0142SEC3 | EXTERIOR DOOR REPLACEMENT | 0142 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 12 new security grade double metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0129HVA1 | HVAC EQUIPMENT REPLACEMENT | 0129 | The existing HVAC system consists of a rooftop air handler, 2 Futera hot water boilers, fan coil units and evaporative coolers. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 327080
0124INT2 | VCT FLOORING REPLACEMENT | 0124 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. There is asbestos in the floor tile mastic that will need to be abated by a licensed abatement professional. It is recommended that the VCT flooring be replaced. Additional monies are included in this project for asbestos removal and disposal. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0126INT1 | VCT FLOORING REPLACEMENT | 0126 | The VCT (vinyl composite tile) in the building is damaged and reaching the end of their useful life. There is asbestos in the floor tile mastic that will need to be abated by a licensed abatement professional. It is recommended that the VCT be replaced. Additional monies are included in this project for asbestos removal and disposal. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35840
1436HVA1 | HVAC EQUIPMENT REPLACEMENT | 1436 | The existing HVAC system consists of 8 rooftop evaporative coolers and several air handlers connected to the sitewide hot water loop. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115050
1436INT1 | CEILING TILE REPLACEMENT | 1436 | The ceiling in the building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. Additional costs would be required if there is asbestos in the tiles or adhesive. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38350
1436INT2 | FLOORING REPLACEMENT | 1436 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61360
0149EXT3 | EXTERIOR DOOR REPLACEMENT | 0149 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 8 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
1436ADA1 | ADA RESTROOM UPGRADE | 1436 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the staff restroom and the inmate restroom into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1963 | 7670 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
1648PLM1 | PLUMBING UPGRADES | 1648 | This building has a hose bib in each of the plumbing chases serving a pair of toilets on each floor. None of these hose bibs are equipped with a backflow prevention device. Additionally, every other plumbing chase has a floor drain in case the inmates clog the toilets and flood the cells. The existing drip-type trap primers have been extremely problematic, requiring frequent service and replacement. Without a functioning primer, the trap seal can dry out, permitting sewer gases to back into the building. This project addresses the installation of backflow prevention devices for each of the hose bibs and a flush-action trap primer for each of the floor drains. The flush action primers are activated each time the toilets are flushed. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1648HVA1 | HVAC EQUIPMENT REPLACEMENT | 1648 | The existing HVAC system consists of 4 unit heaters and window mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 4 new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project is recommended under CIP 13-M17. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 450000
1648ADA1 | ADA PROJECTS | 1648 | The existing accessible cells do not meet the Americans with Disabilities Act (ADA) requirements. The sinks have inadequate underside clearances and the mirrors are mounted too high. This project proposes providing new sinks and relocating the mirrors in each of the ADA accessible cells. The bank of phones does not have an accessible installation and is not equipped with hearing assisted equipment. This project provides an adaptive phone on each side of the housing unit. ADA requirements states that a threshold at an entrance door will not exceed 1/2 inch in height. The thresholds at the entrances to this building are about 1-1/4 inches high. It is recommended that a new accessible threshold and a door shoe be installed. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design This project or a portion there of was previously recommended in the FCA report dated 03/30/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 50000
0150HVA1 | HVAC EQUIPMENT REPLACEMENT | 0150 | The existing HVAC system consists of hydronic unit heaters and evaporative coolers. They are not energy efficient, insufficient for the spaces and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. This project includes the removal and disposal of approximately 50 asbestos mudded elbows on the hot water piping. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66500
2004ELE1 | SERVICE OUTLET INSTALLATION | 2004 | The NEC 2011 Section 210.63 requires a 125-volt, single-phase, 15 or 20 ampere-rated receptacle outlet to be located on the same level and within 25' of an HVAC unit. The rooftop HVAC units do not have a receptacle located near them and neither does the emergency generator. This project would provide funding to install two 125 volt receptacles, one for the HVAC units and the other for the emergency generator. This estimate includes an allowance for 100 feet of conduit and electrical wire. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0127ELE1 | ELECTRICAL UPGRADE | 0127 | This building was constructed before the high demand for electrical services were needed for maintenance equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING B | 9990 | Correct | NNCC |  | Carson City | 1967 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0128INT3 | DRYER REPLACEMENT | 0128 | The commercial tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the existing tumbler dryers and replacement with new units. A total of 7 dryers was used for this estimate. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0137ELE2 | ELECTRICAL UPGRADE | 0137 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 163060
0130INT2 | INTERIOR FINISHES | 0130 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0146PLM1 | PLUMBING SYSTEM UPGRADE | 0146 | The water supply and waste system is original to the building and in poor condition. There is not enough heating or insulation to prevent the pipes from freezing and repairs have been made frequently. This project recommends replacing all of the water and sewer lines in the building including sufficient insulation and heating to prevent freezing. This estimate includes removal and disposal of the existing system as required. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0130EXT2 | EXTERIOR FINISHES | 0130 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0145PLM1 | RESTROOM FIXTURE REPLACEMENT | 0145 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0145INT2 | INTERIOR FINISHES | 0145 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0144PLM2 | WATER HEATER REPLACEMENT | 0144 | There is an on-demand water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0130ELE2 | ELECTRICAL UPGRADE | 0130 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158400
0131EXT2 | EXTERIOR FINISHES | 0131 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0137INT4 | INTERIOR FINISHES | 0137 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 81530
0145EXT2 | WINDOW REPLACEMENT | 0145 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0129ADA1 | ADA RESTROOM REMODEL | 0129 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0139EXT4 | EXTERIOR FINISHES | 0139 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0137INT6 | FLOORING REPLACEMENT | 0137 | The various flooring materials in the building are damaged and reaching the end of their useful life. In the Law Library and corridor, the sheet vinyl is due for replacement as well as the carpeted Storage Rooms. The gymnasium floor is due for sanding and refinishing with a polyurethane or similar coating. It is recommended that the sheet vinyl and carpet be replaced and the gymnasium floor refinished. This project would provide for removal and disposal of the sheet vinyl, installation of new 12x12 VCT with a 6" base in its place and refinishing the gymnasium floor in the next 2-3 years. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130448
0129EXT4 | EXTERIOR DOOR REPLACEMENT | 0129 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 10 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0129EXT3 | WINDOW REPLACEMENT | 0129 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59400
0129INT3 | INTERIOR FINISHES | 0129 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81770
0129INT4 | CULINARY FLOOR REPLACEMENT | 0129 | This project recommends replacing 3,525 sq. ft. of flooring in the kitchen. The ceramic tile and substrate are damaged and failing. There are broken tiles throughout and water has infiltrated the substrate. This project would provide for removal and disposal of the existing flooring and installation of new quartz flooring in the next 1-2 years. Removal and reinstallation of kitchen equipment is also included in this estimate. This project is in design under CIP 13-M44 and the estimate is based off of that project. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 243225
0129INT5 | INTERIOR DOOR REPLACEMENT | 0129 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 28 doors. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
0129ELE2 | ELECTRICAL UPGRADE | 0129 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245310
0129EXT2 | EXTERIOR FINISHES | 0129 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81770
0138EXT4 | EXTERIOR FINISHES | 0138 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0137INT5 | INTERIOR DOOR REPLACEMENT | 0137 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 12 doors. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
0137EXT3 | EXTERIOR DOOR REPLACEMENT | 0137 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 9 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0129HVA2 | FREEZER COMPRESSOR REPLACEMENT | 0129 | There are 2 compressors for the freezer that will need to be replaced in the near future. They utilize older R-22 refrigerant and are original to the building. This project covers the recovery of the existing refrigerant and changing out the compressors with high efficiency units. If the existing compressor suffers a burnout and contaminates the refrigerant it will be more costly to change the unit out. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0129PLM3 | PLUMBING REPLACEMENT | 0129 | The cast iron waste and supply lines are older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. Excess moisture under the kitchen has contributed to the deterioration of the waste and supply piping. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | CULINARY/DINING | 9990 | Correct | NNCC |  | Carson City | 1987 | 16354 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0140EXT4 | EXTERIOR FINISHES | 0140 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0141EXT4 | EXTERIOR FINISHES | 0141 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 68205
0142EXT3 | EXTERIOR FINISHES | 0142 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 68205
0137SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0137 | The building has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 228284
0146EXT3 | SLIDING GLASS DOOR REPLACEMENT | 0146 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0147INT2 | FLOORING REPLACEMENT | 0147 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0147EXT3 | EXTERIOR DOOR REPLACEMENT | 0147 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0147EXT2 | WINDOW REPLACEMENT | 0147 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0147INT1 | INTERIOR FINISHES | 0147 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0147EXT1 | EXTERIOR FINISHES | 0147 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels, structural posts and stairs and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0146PLM3 | WATER HEATER REPLACEMENT | 0146 | There is a 15 gallon electric water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0140INT3 | JANITORS CLOSET REPAIRS | 0140 | The ceramic mop sink in the Janitors Closet is cracked and the paint on the CMU surround has peeled off. This project would provide for a new mop sink to be installed and applying an epoxy based paint to the surrounding CMU walls. The epoxy paint shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0146INT3 | FLOORING REPLACEMENT | 0146 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
0148EXT1 | EXTERIOR FINISHES | 0148 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. The estimate includes additional costs due to the difficulty of the work. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0146EXT2 | WINDOW REPLACEMENT | 0146 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0146INT2 | INTERIOR FINISHES | 0146 | The interior finishes are in fair to poor condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
0146EXT1 | EXTERIOR FINISHES | 0146 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0145PLM2 | WATER HEATER REPLACEMENT | 0145 | There is a 15 gallon electric water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0145INT3 | FLOORING REPLACEMENT | 0145 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0145EXT3 | EXTERIOR DOOR REPLACEMENT | 0145 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0133INT2 | INTERIOR FINISHES | 0133 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89975
0146PLM2 | RESTROOM FIXTURE UPGRADE | 0146 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 3 | 9990 | Correct | NNCC |  | Carson City | 1990 | 864 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0149EXT4 | EXTERIOR FINISHES | 0149 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53170
0150EXT5 | OVERHEAD DOOR REPLACEMENT | 0150 | There are three 16'x14' overhead coiling doors which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with three new motorized doors. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0150EXT4 | EXTERIOR DOOR REPLACEMENT | 0150 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 5 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0150EXT3 | WINDOW REPLACEMENT | 0150 | The existing exterior window units are original to the building and are damaged or broken and are not energy efficient. They present a safety and security issue due to their condition. This project would provide for the removal and replacement of the existing exterior window units with new institutional grade safety glazed window units. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0150INT2 | INTERIOR FINISHES | 0150 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16625
0150EXT2 | EXTERIOR FINISHES | 0150 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 16625
0149ADA3 | RESTROOM REMODEL | 0149 | The building does not have an accessible staff restroom. The existing staff restrooms have some accessible upgrades but they do not fully meet the Americans with Disabilities Act (ADA) requirements. A partial retrofit is necessary. This project would provide funding to bring the restrooms into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0149ADA2 | ADA RESTROOM UPGRADE | 0149 | The building does not have an accessible restroom. The existing restrooms in the staff area do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0147PLM1 | RESTROOM FIXTURE REPLACEMENT | 0147 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0149INT2 | INTERIOR FINISHES | 0149 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53170
0147PLM2 | WATER HEATER REPLACEMENT | 0147 | There is an on-demand water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 4 | 9990 | Correct | NNCC |  | Carson City | 1979 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0148PLM2 | WATER HEATER REPLACEMENT | 0148 | There is a 15 gallon electric water heater in the tower. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0148PLM1 | RESTROOM FIXTURE REPLACEMENT | 0148 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0148INT2 | FLOORING REPLACEMENT | 0148 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5340
0148EXT3 | EXTERIOR DOOR REPLACEMENT | 0148 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0148EXT2 | WINDOW REPLACEMENT | 0148 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0148INT1 | INTERIOR FINISHES | 0148 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 5 | 9990 | Correct | NNCC |  | Carson City | 1979 | 267 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2670
0137EXT2 | EXTERIOR FINISHES | 0137 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81530
0149ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0149 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0132EXT2 | EXTERIOR FINISHES | 0132 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 980
0133EXT4 | EXTERIOR DOOR REPLACEMENT | 0133 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 14 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0133EXT3 | WINDOWS REPLACEMENT | 0133 | The existing windows in this building are of single pane wire mesh construction. Many are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26400
0144PLM1 | RESTROOM FIXTURE REPLACEMENT | 0144 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including the water closet, lavatory and faucet. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0133ELE2 | ELECTRICAL UPGRADE | 0133 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 269925
0144INT2 | FLOORING REPLACEMENT | 0144 | The VCT (vinyl composite tile) flooring is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0133EXT2 | EXTERIOR FINISHES | 0133 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89975
0143EXT2 | EXTERIOR FINISHES | 0143 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2750
0132INT2 | INTERIOR FINISHES | 0132 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 980
0133PLM1 | WATER HEATER REPLACEMENT | 0133 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0131EXT5 | EXTERIOR DOOR REPLACEMENT | 0131 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 8 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0131EXT4 | OVERHEAD DOOR REPLACEMENT | 0131 | Two out of the seven 10'x14' overhead coiling doors are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0131INT2 | INTERIOR FINISHES | 0131 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52800
0142INT2 | INTERIOR FINISHES | 0142 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81705
0141INT2 | INTERIOR FINISHES | 0141 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 81705
0140INT2 | INTERIOR FINISHES | 0140 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0139INT2 | INTERIOR FINISHES | 0139 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0132EXT3 | EXTERIOR DOOR REPLACEMENT | 0132 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 2 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | TV DISTRIBUTION BUILDING | 9990 | Correct | NNCC |  | Carson City |  | 196 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0136EXT2 | EXTERIOR FINISHES | 0136 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 46520
0137ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0137 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MULTI-PURPOSE/GYM/CHAPEL | 9990 | Correct | NNCC |  | Carson City | 1968 | 16306 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0136SIT2 | SIDEWALK REPLACEMENT | 0136 | The sidewalks serving the building between the parking lot and the entrances are deteriorated and failing. It is spalling and cracking in all areas and should be scheduled for replacement. This project addresses removal and replacement of existing sidewalks as needed. 1,500 SF of 4" thick concrete sidewalk was used for this estimate. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0136INT5 | JANITORS CLOSET REPAIRS | 0136 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 1400
0136ELE2 | ELECTRICAL UPGRADE | 0136 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 139560
0136ADA3 | BREAK ROOM REMODEL | 0136 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0136INT4 | CARPET REPLACEMENT | 0136 | The carpet in the Conference Room is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0136EXT4 | WINDOW WALL SYSTEM REPLACEMENT | 0136 | There are six exterior aluminum window wall systems around the building that appear to be original to the building. They are damaged from age and general wear and tear and are a constant maintenance problem. The windows are single pane construction and the metal frames are rusted and damaged. This project would provide for the replacement of 203 linear feet of exterior aluminum window walls including dual pane, thermally broke windows, ADA compliant doors and hardware. Removal and disposal of the existing walls is included in this estimate. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 203000
0133INT3 | JANITORS CLOSET REPAIRS | 0133 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0136INT3 | INTERIOR FINISHES | 0136 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46520
0133INT4 | RESTROOM REMODEL | 0133 | The restroom in the Property Room was in overall poor condition at the time of the survey. It was not designed according to the building code. For example, the water closet seat is 34" above the finish floor and the walls and partitions do not fully enclose the restroom. This project would provide for a complete remodel of the restroom fixtures, hardware, doors, walls, floor and wall finishes. The removal and disposal of the existing fixtures and finishes is included in this estimate. | PRISON INDUSTRY/CANTEEN BUILDING A | 9990 | Correct | NNCC |  | Carson City | 1967 | 17995 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0135PLM1 | WATER HEATER REPLACEMENT | 0135 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0135ELE2 | ELECTRICAL UPGRADE | 0135 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71520
0135EXT5 | EXTERIOR DOOR REPLACEMENT | 0135 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 4 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0135EXT4 | WINDOW WALL SYSTEM REPLACEMENT | 0135 | There are two exterior window wall systems on the north and west exteriors of the building that appear to be original to the building. They are damaged from age and general wear and tear and are a constant maintenance problem. The windows are single pane construction and the metal frames are rusted and damaged. This project would provide for the replacement of 104 linear feet of exterior aluminum window walls including dual pane, thermally broke windows, ADA compliant doors and hardware. Removal and disposal of the existing walls is included in this estimate. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 104000
0135INT3 | INTERIOR FINISHES | 0135 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23840
0135EXT3 | EXTERIOR FINISHES | 0135 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and storefront systems and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | VISITORS CENTER II | 9990 | Correct | NNCC |  | Carson City | 1974 | 4768 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23840
0138INT2 | INTERIOR FINISHES | 0138 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 107930
0136EXT3 | ROOF REPLACEMENT | 0136 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The current roofing system was installed in 1993 and is now 21 years old. The roof warranty for this roof expired on 9-27-2009. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program. | ADMINISTRATION/VISITING I | 9990 | Correct | NNCC |  | Carson City | 1974 | 9304 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111648
0125ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0125 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
1673ENV1 | PEST CONTROL | 1673 | The roof, roof cap flashing, and exterior lights have become a roosting place for birds. The roof and exterior lights are covered in bird droppings. This project would provide for the removal and cleaning of the bird droppings from the above mentioned areas. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1673INT3 | ACOUSTICAL CEILING TILE REPLACEMENT | 1673 | The existing ceiling is covered by 12"x 12" interlocking acoustical tiles. They do not appear to be a hospital-grade product and many of the tiles are damaged and stained and need to be replaced. There is also a need for a tamper-proof tile in the inmate areas and access panels for HVAC equipment servicing. This project would provide for the replacement of the damaged, staining and missing ceiling tiles and installation of six 12"x12" one- hour rated access panels at HVAC equipment locations. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1673INT1 | INTERIOR FINISHES | 1673 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 305690
2005LGT1 | ROOF REPLACEMENT | 2005 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0126EXT4 | EXTERIOR DOOR REPLACEMENT | 0126 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 5 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0126EXT3 | WINDOW REPLACEMENT | 0126 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16200
0126INT3 | INTERIOR FINISHES | 0126 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 17920
0126EXT2 | EXTERIOR FINISHES | 0126 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 17920
0126ADA2 | ADA DOOR & THRESHOLD REPLACEMENT | 0126 | The existing exterior entrance door and threshold to the building is not accessible. It is missing a lever action door handle and the threshold is too tall. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4500
0125INT5 | JANITORS CLOSET REPAIRS | 0125 | The mop sink in the Janitors Closets is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0125INT4 | INTERIOR DOOR REPLACEMENT | 0125 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 75 doors. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0125EXT4 | EXTERIOR DOOR REPLACEMENT | 0125 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 17 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 68000
9990SIT3 | ASPHALT PAVING INSTALLATION | 9990 | The Prison Industries buildings do not have paved access roads around them and the drainage in this area is problematic. The unpaved areas make it difficult to transport materials and supplies between the buildings especially during and after inclement weather. The dirt areas do not provide proper drainage and graded areas are easily damaged by rain, snow and ice which exacerbates the problem. This project would provide asphalt cement paving for a 20' wide access road between and around the Prison Industries buildings. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0125EXT3 | EXTERIOR FINISHES | 0125 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 46075
2785EXT1 | EXTERIOR FINISHES | 2785 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9990 | Correct | NNCC |  | Carson City | 2008 | 23780 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118900
9990ADA2 | ADA PATH OF TRAVEL | 9990 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete path of travel to the recreation yards and religious group area are necessary to comply with ADA accessibility requirements. This project would provide for concrete walkways from the housing units to the recreation and religious areas to the north. This will require regrading, placement of P.C. concrete, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 4,000 square feet of concrete was used for this estimate. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0124INT6 | JANITORS CLOSET REPAIRS | 0124 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0124INT5 | INTERIOR DOOR REPLACEMENT | 0124 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 10 doors. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0124EXT4 | EXTERIOR DOOR REPLACEMENT | 0124 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 4 new security grade metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0124INT4 | INTERIOR FINISHES | 0124 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
0124EXT3 | EXTERIOR FINISHES | 0124 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 11000
0124ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0124 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
9990SIT6 | DRAINAGE IMPROVEMENTS | 9990 | The site has several areas with inadequate drainage due to deteriorated asphalt, clogged drains or insufficient sloping. The standing water causes premature deterioration of the paving and other site improvements. The grade does not slope properly near the entrance to the Maintenance Building. The drain at the Sally Port cannot handle the large volume of water coming from the parking lot which results in standing water around the Sally Port and Education building. This project would create positive flow away from the Maintenance Building, Education Building and Sally Port by regrading, paving, installing additional drainage swales or storm drains as needed. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9990PLM1 | ISOLATION VALVE INSTALLATION | 9990 | There are no isolation valves for the individual building's water lines. The main water line that serves each of the buildings on the site is in need of an isolation valve. This will allow the maintenance staff to do repairs and maintenance to the plumbing without shutting down the whole site. More importantly, a leak in the building can be shut down quickly minimizing damage in an emergency. This estimate provides for a 2-1/2" gate valve to be installed at each of 20 separate buildings. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9990SIT5 | CONCRETE CURB REPLACEMENT | 9990 | The concrete curbing in the parking lot has been damaged and is failing in many areas. There is extensive cracking, crumbling and failure due to vehicles colliding with the curbs. Due to the high traffic volume and high percentage of large commercial vehicles in this parking lot, it is recommended to replace the curbs with a system with a longer lifespan. This project would provide for the installation of concrete curbing with a deeper footing throughout and a high strength concrete mix to ensure a longer life cycle of the new curbing. Removal and disposal of the existing curbing is included in this estimate. This project should be implemented concurrently with the Crack Fill and Seal Asphalt Paving project. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9990HVA1 | BOILER PLANT AND DISTRIBUTION SYSTEM UPGRADE | 9990 | The hot water and steam boilers and hot water distribution piping has reached the end of its useful life and is due for replacement. The boilers were installed in 1978 and 1982 and are over 30 years old. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. This project would provide for the removal and disposal of the existing boilers, controls, piping and valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on (4) 5,000 MBH hot water boilers, (2) 100 hp steam boilers, heat exchangers, pumps, 12,500 linear feet of pre-insulated piping and temperature controls. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. Planning for this project is recommended under CIP 15-5289. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500000
9990ENR1 | HIGH MAST LIGHTING UPGRADE | 9990 | There are 15 high mast security light poles throughout the facility that have 9 security lamps each. The current lamps are an older, less efficient style and should be replaced with LED lamps. This project provides for the purchase and installation of 135 LED lamps for the high mast light poles. The cost includes removal and disposal of the existing lamps. | NORTHERN NEVADA CORRECTIONAL CENTER | 9990 | Correct | NNCC |  | Carson City | 1963 |  | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270000
0125INT3 | INTERIOR FINISHES | 0125 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMMAND POST/OPERATIONS/EDUCATION | 9990 | Correct | NNCC |  | Carson City | 1976 | 9215 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 46075
2004SFT1 | INTERIOR STAIRWAY REPLACEMENT | 2004 | The wood stairs and handrails in the north side of the original warehouse do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The landing at the top is not large enough and the handrails are not structurally adequate. This project would provide funding to remove and replace the stairway and handrail. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0145EXT1 | EXTERIOR FINISHES | 0145 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels, structural posts and stairs and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0145STR1 | STRUCTURAL ASSESSMENT | 0145 | The Guard Tower #2 sways substantially during high winds. This project recommends that a licensed engineer perform a structural investigation to assess the swaying of the metal guard tower. Future projects would be based on this report. | GUARD TOWER 2 | 9990 | Correct | NNCC |  | Carson City | 1974 | 75 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0144EXT2 | EXTERIOR DOOR REPLACEMENT | 0144 | The existing exterior metal door and frame appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new security grade metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0150SIT1 | SAND/ OIL INTERCEPTOR | 0150 | There is no sand/ oil interceptor for the repair garage. It is recommended that a sand/ oil interceptor be installed and connected to the sewer drain to prevent oils and solids from entering the city sewer lines. This project would provide funding for the purchase and installation of a 50 GPM sand/ oil interceptor with a high oil alarm. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0150ELE2 | ELECTRICAL UPGRADE | 0150 | This building was constructed before the high demand for electrical services were needed for equipment, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | AUTO SHOP | 9990 | Correct | NNCC |  | Carson City | 1974 | 3325 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49875
0126ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0126 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0126INT5 | INTERIOR DOOR REPLACEMENT | 0126 | The interior doors are original to the building. Many are damaged, difficult to lock and operate and do not have lever action handles. This project would provide for the removal of the existing doors and the purchase and installation of new metal security grade doors and frames. All hardware and painting is included in this estimate. Hardware to include security keys and fusible locks. This estimate is for 8 doors. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0124EXT2 | WINDOW REPLACEMENT | 0124 | The existing windows in this building are of single pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAIN GATE HOUSE | 9990 | Correct | NNCC |  | Carson City | 1963 | 1440 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0126INT4 | CEILING SYSTEM REPLACEMENT | 0126 | The office side of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in many areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1648SFT3 | GLAZING REPLACEMENT | 1648 | The 2 control rooms are located on the upper level of each wing. The flooring in these rooms contains structural glass block vision panels of which two are damaged and many are scratched and cloudy. This project would provide for the removal and replacement of 74 8"x8" structural glass blocks to ensure that the guards have clear vision below them. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 7 | 9990 | Correct | NNCC |  | Carson City | 1990 | 44500 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37000
2004ENR1 | LIGHTING UPGRADE | 2004 | The existing lighting fixtures in the refrigerators and freezers are not performing well in the cold temperatures. The T-8 lamps are slow to start, work intermittently and burn out prematurely. This project will upgrade the T-8 lamps to LED's or another fixture appropriate for the cold temperatures. Any electrical wiring upgrades are not included in this estimate. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2004HVA1 | HVAC EQUIPMENT REPLACEMENT | 2004 | The existing HVAC system consists of 2 roof mounted evaporative coolers and an original oil fired boiler. They are not energy efficient and have reached the end of their expected and useful life. The cooling is insufficient and does not provide a comfortable work environment in the summer. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 127800
1673INT4 | CABINET AND BREAK ROOM UPGRADES | 1673 | The cabinets and countertops in the building are showing signs of wear and tear and the break rooms are not ADA compliant. The countertops are delaminating and failing particularly at the Formica edges and corners. This condition is prevalent throughout the building including staff desks and 3 staff break rooms. This project recommends the replacement of the existing damaged laminate on the counters and cabinets with heavy duty, quality finishes. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing accessible sinks. This project would provide funding for the removal and replacement of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2004PLM1 | WATER HEATER REPLACEMENT | 2004 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0126SFT4 | SAFETY CABINETS | 0126 | The Maintenance Building contains many different paints, stains, pesticides and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2005EXT2 | EXTERIOR FINISHES | 2005 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 2000
2005INT2 | INTERIOR FINISHES | 2005 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 2000
2005EXT3 | WINDOW REPLACEMENT | 2005 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2005EXT4 | EXTERIOR DOOR REPLACEMENT | 2005 | The 2 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | INMATE CLOTHING STORE | 9990 | Correct | NNCC |  | Carson City |  | 400 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2006EXT1 | EXTERIOR FINISHES | 2006 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | BIKE STORAGE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1963 | 384 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2557EXT1 | EXTERIOR FINISHES | 2557 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE STORAGE | 9990 | Correct | NNCC |  | Carson City | 2004 | 3000 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0131SFT4 | SAFETY CABINETS | 0131 | The building contains many different paints, stains, printing chemicals and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING C | 9990 | Correct | NNCC |  | Carson City | 1974 | 10560 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0130SFT3 | WELDING VENTILATION INSTALLATION | 0130 | The building has insufficient ventilation for welding under OSHA Chapter 1926.353. If welding operations continue in this building, either general mechanical ventilation or local exhaust ventilation shall be provided. This project would provide for the installation of a mechanical ventilation system for the safety of the employees. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | PRISON INDUSTRY BUILDING D | 9990 | Correct | NNCC |  | Carson City | 1965 | 10560 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0128PLM2 | WATER STORAGE TANK REPLACEMENT | 0128 | There is a 860 gallon water storage tank in the building. The average life span of a water storage tank is forty to fifty years. The tank was installed in 1978. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. This project would provide for a new water storage tank to be installed including connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | LAUNDRY/CENTRAL PLANT | 9990 | Correct | NNCC |  | Carson City | 1968 | 7000 | 2014-05-01 | Four to Ten Years | Long-Term Needs | 3 | 3500
0126PLM2 | WATER HEATER REPLACEMENT | 0126 | There is a 120 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2784EXT1 | EXTERIOR FINISHES | 2784 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | NNCC BIOMASS PLANT | 9990 | Correct | NNCC |  | Carson City | 2006 | 6853 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6853
0126SFT3 | WELDING VENTILATION INSTALLATION | 0126 | The building has insufficient ventilation for welding under OSHA Chapter 1926.353. If welding operations continue in this building, either general mechanical ventilation or local exhaust ventilation shall be provided. This project would provide for the installation of a mechanical ventilation system for the safety of the employees. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | MAINTENANCE BUILDING | 9990 | Correct | NNCC |  | Carson City | 1969 | 3584 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 15000
2004EXT4 | OVERHEAD DOOR REPLACEMENT | 2004 | There are two 10'x10' overhead coiling doors in the original portion of the warehouse. One of them has been replaced, the other has not and is damaged and does not function properly. Exposure and wind have caused the door to bend, crack and lose its finish. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the motorized overhead coiling door and replacement with a new motorized overhead coiling door including remote operation, safety controls and connection to existing utilities. | CENTRAL WAREHOUSE | 9990 | Correct | NNCC |  | Carson City | 1972 | 25298 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0144EXT1 | EXTERIOR FINISHES | 0144 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels, structural posts and stairs and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1673EXT2 | EXTERIOR FINISHES | 1673 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | REGIONAL MEDICAL FACILITY UNIT 8 | 9990 | Correct | NNCC |  | Carson City | 1993 | 61138 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 305690
0141SEC1 | CELL DOOR LOCK REPLACEMENT | 0141 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 4 | 9990 | Correct | NNCC |  | Carson City | 1974 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0142SEC1 | CELL DOOR LOCK REPLACEMENT | 0142 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 5 | 9990 | Correct | NNCC |  | Carson City | 1977 | 13641 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0143EXT3 | EXTERIOR DOOR REPLACEMENT | 0143 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the louvered double metal door assembly and the 2 single metal man door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0149SEC1 | CELL DOOR LOCK REPLACEMENT | 0149 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 6 | 9990 | Correct | NNCC |  | Carson City | 1981 | 10634 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 250000
0143EXT4 | COILING DOOR REPLACEMENT | 0143 | There is an 8'x8' coiling door on the west side of the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated coiling door and replacement with a new manually operated coiling door. Removal and disposal of the existing door is included in this estimate. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0144INT1 | INTERIOR FINISHES | 0144 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceiling at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0144ENR1 | WINDOW REPLACEMENT | 0144 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 16 units. Removal and disposal of the existing windows is included in this estimate. The estimate includes additional costs due to the difficulty of the installation. | GUARD TOWER 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 75 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0139SEC1 | CELL DOOR LOCK REPLACEMENT | 0139 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 2 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0140SEC1 | CELL DOOR LOCK REPLACEMENT | 0140 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 3 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0138SEC1 | CELL DOOR LOCK REPLACEMENT | 0138 | The existing cell door locks are original to the building. The control panel, paracentric and mogul electric door cylinders are warn, have reached the end of their expected life and have become a security and safety concern for correctional officers. This project would provide for a new electric door control system including cylinders, keys, control panel and all required electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | HOUSING UNIT 1 | 9990 | Correct | NNCC |  | Carson City | 1963 | 21586 | 2014-05-01 | Immediate to Two Years | Currently Critical | 1 | 287500
0143INT2 | INTERIOR FINISHES | 0143 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA reports dated 04/22/1999 and 01/11/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2014. | GENERATOR/ SWITCH GEAR ROOM | 9990 | Correct | NNCC |  | Carson City | 1974 | 550 | 2014-05-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2750
0358SFT4 | FIRE RATED CEILING REPAIRS | 0358 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
0359ADA3 | ADA RESTROOM REMODEL | 0359 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of both restrooms is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
0359ENR2 | WINDOW REPLACEMENT | 0359 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 39 units. Removal and disposal of the existing windows is included in this estimate. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29250
0363INT4 | CEILING SYSTEM REPLACEMENT | 0363 | The majority of the building has a suspended acoustical tile ceiling system. The t-bar framing is old, bent and rusted in some areas and many ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including the framing, acoustical tile and seismic bracing assemblies. Removal and disposal of the existing ceiling system is included in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0363INT3 | INTERIOR DOOR REPLACEMENT | 0363 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including lever action door handles, hardware and paint. Frames are not included in this estimate. Removal and disposal of the existing doors is included in this cost estimate. A total of 6 interior doors was used in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1991PLM2 | WATER TREATMENT SYSTEM INSTALLATION | 1991 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1991ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1991 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
0359ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0359 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1991SFT4 | FIRE RATED CEILING REPAIRS | 1991 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
0363ENR1 | HVAC EQUIPMENT REPLACEMENT | 0363 | The four HVAC packaged units were installed in 1995. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of four new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0363INT2 | CARPET REPLACEMENT | 0363 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0363ENR2 | WINDOW REPLACEMENT | 0363 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0356INT5 | FIRE RATED CEILING REPAIRS | 0356 | The fire rated ceiling in the telecommunications closet is damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2500
0357SFT5 | FIRE RATED CEILING REPAIRS | 0357 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
0357EXT4 | ROOF REPLACEMENT | 0357 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0358EXT4 | ROOF REPLACEMENT | 0358 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 14400
0358ADA3 | ADA RESTROOM UPGRADE | 0358 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
0354HVA4 | CHILLER AND COOLING TOWER REPLACEMENT | 0354 | The building is cooled by a chiller and cooling tower system. The equipment is original to the building and is reaching the end of its useful life. It is recommended to schedule replacement of the chiller and cooling tower in the next 2-3 years. This project provides for disposal of the existing units and replacement with a new water cooled centrifugal chiller and cooling tower including connections to utilities. The new system shall be designed to significantly reduce electrical usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing equipment and all required connections to utilities. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0363EXT3 | EXTERIOR DOOR REPLACEMENT | 0363 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0355SFT5 | EXIT SIGN INSTALLATION | 0355 | The building does not have any exit signs which does not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1800
1993ADA3 | ACCESSIBLE ENTRANCE RAMP | 1993 | The building is lacking an accessible entrance into the building. The building offers a program to the public. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 35000
0354EXT5 | ROOF REPLACEMENT | 0354 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0359EXT2 | ROOF REPLACEMENT | 0359 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1981. It is recommended that the single-ply membrane on this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. The asphalt composition shingle roofing is not included in this estimate. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 36000
1993EXT4 | ROOF REPLACEMENT | 1993 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The clay tile roofing is not included in this estimate. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
0354PLM3 | PLUMBING REPLACEMENT | 0354 | The plumbing and waste system is older and in poor condition. All of the pipes are original to the building and should be scheduled for replacement. The piping that supports the HVAC system has mineral build-up and corrosion throughout as do the domestic water lines. The sewer pipes also have considerable build up inside the pipes and get clogged often causing back ups and flooding in the building. This project recommends replacing all of the water, HVAC and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0354ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0354 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
0354ENR2 | WINDOW REPLACEMENT | 0354 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 52 units. Removal and disposal of the existing windows is included in this estimate. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
0354SFT4 | INTERIOR HANDRAIL REPLACEMENT | 0354 | The interior stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railing is included. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0355SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0355 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0358ADA4 | ADA DOOR HARDWARE REPLACEMENT | 0358 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 54750
0355ENR2 | WINDOW REPLACEMENT | 0355 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 14 units. Removal and disposal of the existing windows is included in this estimate. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0356PLM3 | WATER HEATER REPLACEMENT | 0356 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0356SFT6 | EXIT SIGN UPGRADE | 0356 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1800
0356ADA3 | ADA KITCHEN REMODELS | 0356 | The two kitchens in the building are in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
0357SFT6 | EXIT SIGN UPGRADE | 0357 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. There are also missing signs at some of the exit doors. IBC - 2012 Chapter 10 was referenced for this project. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5400
0357ADA3 | ADA KITCHEN REMODELS | 0357 | The five kitchens in the building are in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 50000
0357ADA2 | ADA RESTROOM UPGRADE | 0357 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of four of the first floor restrooms is necessary. This project would provide funding for construction of four unisex accessible restrooms on the first floor. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 20000
0358ADA5 | ADA KITCHEN REMODEL | 0358 | The two kitchens in the building are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
0354EXT4 | EXTERIOR FINISHES | 0354 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 62500
0359INT3 | JANITORS CLOSET REPAIRS | 0359 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1991SIT2 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 1991 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0358ENR1 | WINDOW REPLACEMENT | 0358 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 40 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0355SFT2 | EXTERIOR LANDING REPLACEMENT | 0355 | The landing outside the main door into 4B is lower than allowed by the 2012 International Building Code and the Americans with Disabilities Act (ADA). This report recommends modifying the concrete flatwork outside this door to provide a landing no more than ½" lower than the threshold. This project would provide for the removal and replacement of a section of the flatwork to provide a code compliant landing and transition to the remaining flatwork. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2500
0358EXT3 | EXTERIOR FINISHES | 0358 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
1991EXT7 | ROOF / CAP FLASHING MAINTENANCE | 1991 | It is important to maintain the finish, weather resistance and appearance of the roof's cap flashing, caulking and penetrations. This project recommends work to protect these elements, including re-caulking and painting the metal roof cap flashing to maintain it in a good, weather-tight condition. This project should be completed within the next one to two years. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1200
1991SFT6 | EXTERIOR STAIR HANDRAIL INSTALLATION | 1991 | The concrete exterior stairs at the entry are lacking a handrail as required in the 2012 IBC Chapter 10, Section 1012. This project would provide for a tubular steel framed handrail to be installed. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
0358PLM3 | WATER HEATER REPLACEMENT | 0358 | There are two 40 gallon gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0356EXT1 | EXTERIOR FINISHES | 0356 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0356INT4 | INTERIOR FINISHES | 0356 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0358INT3 | INTERIOR FINISHES | 0358 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
0357INT4 | INTERIOR DOOR REPLACEMENT | 0357 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including lever action door handles, hardware and paint. Frames are not included in this estimate. Removal and disposal of the existing doors is included in this cost estimate. A total of 40 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 6/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 20000
0357EXT2 | EXTERIOR FINISHES | 0357 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
1993EXT1 | EXTERIOR FINISHES | 1993 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32900
0359SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0359 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 72800
0354INT5 | INTERIOR FINISHES | 0354 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62500
0357SFT2 | EGRESS WINDOWS | 0357 | After this building was built, residential sleeping room emergency egress requirements came into the International Building Code. Part of these requirements included a maximum sill height of 44" above the finished floor. The window sill height currently is 47" above finished floor. This project recommends replacing the existing windows with 48" x 48" dual pane horizontal sliders, installed to meet minimum safety standard for emergency egress. Project based on 2012 IBC Chapter 10 Section 1029.3, This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 16000
0357INT3 | INTERIOR FINISHES | 0357 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 6/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46325
0355EXT1 | EXTERIOR FINISHES | 0355 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0359EXT1 | EXTERIOR FINISHES | 0359 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
0355INT4 | INTERIOR FINISHES | 0355 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1992EXT2 | EXTERIOR FINISHES | 1992 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23050
0359INT2 | INTERIOR FINISHES | 0359 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/19/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
1991EXT2 | EXTERIOR FINISHES | 1991 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/22/1998 and 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23050
1992ADA3 | ADA SIGNAGE | 1992 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 3000
0357ELE2 | GFCI DUPLEX OUTLET REPLACEMENT | 0357 | There are several outlets in the restrooms and kitchens throughout the building which are not GFCI protected. These outlets should be changed to GFCI type outlets per the 2011 NEC. There are also several GFCI outlets throughout the building which are damaged and not working properly. This project would provide for the purchase and installation of GFCI duplex outlets. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 1500
0357ENR1 | WINDOW REPLACEMENT | 0357 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 27 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0358SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0358 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1991EXT6 | ROOF REPLACEMENT | 1991 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1992. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The clay tile roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
1992ADA4 | ADA RESTROOM REMODEL | 1992 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
1992EXT7 | ROOF REPLACEMENT | 1992 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1992. It is recommended that the single-ply membrane on this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. The clay tile roofing is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
1993SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1993 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 92120
1994HVA2 | WATER TREATMENT | 1994 | The chemical water treatment systems for the cooling tower, the chillers and the boilers were not operating at the time of the survey. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 12000
1992ADA2 | ADA DOOR HARDWARE REPLACEMENT | 1992 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 9600
9991SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9991 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the parking lot east of Building #15. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 40,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0355SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0355 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0363SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0363 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 42336
1994SIT4 | COURTYARD IMPROVEMENTS | 1994 | The building and courtyard walls have considerable damage to the concrete masonry units (CMU) from lawn sprinklers wetting the CMU and poor drainage. Four of the five courtyards are due to be re-worked in order to prevent further damage. This project would remove the turf within three feet of the CMU walls, adjust the sprinklers so they do not wet the walls and re-grade or install French drains to ensure proper drainage out of the courtyards. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0357SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0357 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #11 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1992INT3 | INTERIOR FINISHES | 1992 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 23050
1992ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1992 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1992ADA6 | ADA KITCHEN REMODEL | 1992 | The two kitchens in the building are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
1992PLM2 | WATER TREATMENT SYSTEM INSTALLATION | 1992 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1992SFT5 | FIRE RATED CEILING REPAIRS | 1992 | The fire rated ceilings in the two mechanical equipment closets are damaged and should be scheduled for immediate repairs. Penetrations have been made in the one hour fire rated assemblies when new equipment or utility lines are installed which compromises the fire protection design of the building. This project would provide for the removal of the remaining gypsum board ceiling and installation of new 5/8" type X fire rated gypsum board including taping and fire proofing all ceiling penetrations to provide a one hour fire rated ceiling assembly. Taping, texture and paint are included in this estimate. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
1991INT4 | INTERIOR FINISHES | 1991 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 23050
1991ADA2 | ADA DOOR HARDWARE REPLACEMENT | 1991 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 9600
1993ENR2 | HVAC EQUIPMENT REPLACEMENT | 1993 | Four of the HVAC roof top units were recently replaced, the remaining four are more than 20 years old and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of four new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
1991ADA4 | ADA RESTROOM REMODEL | 1991 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of two restrooms is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 40000
1993SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1993 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 3290
1994SIT3 | GATE OPERATOR REPLACEMENT | 1994 | The site has an automatic vehicle access gate to control access into the maintenance yard. The gate operator has been malfunctioning and has difficulty opening and closing the gate and is usually left open due to its problematic operation. This project recommends replacing the gate operator with a high quality operator that can handle heavy traffic as well as servicing the gates and related hardware to ensure prolonged operation. The new gate operator is required to meet UL Standard 325, per NRS 405.270. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1994ENR1 | DIRECT DIGITAL CONTROL SYSTEM FOR HVAC UPGRADE | 1994 | Presently the building has an older direct digital control (DDC) system for the HVAC system. The current Schneider system was an upgrade from the original Yamas system. The original Yamas equipment is failing and does not integrate well with the new Schneider software. A new comprehensive system of software and equipment is due to be installed. The new system should allow starting of equipment, monitoring of status, monitoring of space temperatures, monitoring and control of hot and chilled water temperatures, and similar typical centrally controlled elements. Detailed control of the individual elements of the buildings systems can yield tremendous benefits based upon the reported operating hours coupled with varying occupancy loads. The system should include a microprocessor control center which monitors and manages all components of the buildings HVAC system. The system should also have the capability of controlling other building systems (such as lighting, alarms, etc.) and of communicating with the central management system for the campus. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
1994SEC1 | SECURITY CARD ACCESS UPGRADE | 1994 | This building is equipped with a security control system that is outdated and should be scheduled for immediate replacement. Problems exist with the door control panel and door access readers for the client rooms and access doors. The "Checkpoint" system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. Due to the security level of the facility it is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the control panels, computer software and approximately 35 door access card readers. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 87500
1994EXT3 | EXTERIOR DOOR REPLACEMENT | 1994 | Some of the exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. They are warped and do not open and close smoothly and have problems with the locking mechanisms. This project would provide for the replacement of five door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1994SIT2 | SITE DRAINAGE UPGRADES | 1994 | The building has drainage problems mainly on the north side where grade does not properly slope away from the building and drain pipes get clogged. The rain accumulates in several areas adjacent to the building, creating a water problem which infiltrates the interior during inclement weather. It is unknown where the drainage pipes attached to the downspouts lead to after they leave the building, but they get backed up and overflow near the building. This project would create positive flow away from the buildings by re-grading, paving, installing additional drainage swales as needed and scoping the drain pipes to determine why they back up. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1995EXT2 | WINDOW REPLACEMENT | 1995 | The windows are original, single pane construction in metal frames. These older windows are drafty and at least one of them is broken. This project recommends replacing the windows with dual pane units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | POOLHOUSE/STORAGE | 9991 | HHS | DPBH | SNCAS | Las Vegas | 1981 | 836 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9991SEC1 | DOOR HARDWARE REPLACEMENT | 9991 | The door handles and locking mechanisms on the interior and exterior doors across the site are due for replacement. Staff has had continuous problems with the hardware and there is no common system between the buildings which requires an enormous number of keys to access all of the buildings. This project would provide for the replacement of the hardware on all of the doors. Removal and disposal of the existing hardware is included in this estimate. The estimate was provided by the maintenance staff who have procured a quote for this work. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
9991ADA2 | SIDEWALK REPAIRS | 9991 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete sidewalks around the site do not meet ADA requirements and are in need of repairs. Settling, spalling and cracking have created elevation changes or gaps that are non-ADA compliant. This project would provide for removing the damaged sections of concrete and replacing them with new concrete. 500 SF of 4" thick P.C. concrete sidewalk was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 7500
9991ENV1 | PEST CONTROL | 9991 | There are numerous stray rabbits that have taken up residence throughout the site. The rabbits cause many problems including digging holes that people trip in, damaging the landscaping including eating the plants, leaving droppings all over the campus and possibly spreading diseases. Due to these issues, this project provides for removal of the rabbits and clean up of the droppings by a licensed pest control business. | SNCAS SITE | 9991 | HHS | DCFS | SNCAS | Las Vegas |  |  | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1991ADA3 | ADA KITCHEN REMODEL | 1991 | The two kitchens in the building are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 30000
0358SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0358 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #12 RESIDENTIAL PROGRAMS SOCIAL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 9265 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0363SFT3 | ELECTRICAL EQUIPMENT REPLACEMENT | 0363 | The existing XFMR (transformer) and electrical panel located on the exterior of this building is not NEMA 3R rated and the workspace in front of the panel is about plus or minus 24 inches; 30 inches is required by code. This project would provide for the removal and replacement of these two items with a NEMA 3R rated transformer and electrical panel and provide for 30 inches of workspace in front of the electrical panel. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 10000
0355SFT4 | SAFETY GLAZING INSTALLATION | 0355 | There are four windows around the building which have an exposed bottom edge less than 18 inches above the floor. This condition requires safety glazing according to 2012 IBC Section 2406.4.3. This project would provide for the removal and replacement of the windows with safety glazing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #9 FISCAL/PAYROLL SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 5000
1994INT1 | INTERIOR FINISHES | 1994 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 292000
1994EXT1 | EXTERIOR FINISHES | 1994 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 292000
1995INT1 | INTERIOR FINISHES | 1995 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | POOLHOUSE/STORAGE | 9991 | HHS | DPBH | SNCAS | Las Vegas | 1981 | 836 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4180
1994SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1994 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #17 DESERT WILLOW TREATMENT CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1998 | 58400 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1993SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1993 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1992SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1992 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #14 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1993INT3 | RESTROOM REMODEL | 1993 | The non-ADA restroom in the building has older fixtures, finishes and cabinets. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, cabinets, hardware, floor and wall finishes. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0359SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0359 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #8 ADMINISTRATION/OFFICE FACILITY | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 5200 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0356SFT5 | WINDOW REPLACEMENT | 0356 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. There are four windows around the building which have an exposed bottom edge less than 18 inches above the floor. This condition requires safety glazing according to 2003 IBC Section 2406.3. This project recommends replacing the windows with dual pane, higher efficiency units including safety glazing where required. This estimate is for the replacement of 15 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 15000
0356SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0356 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #10 WRAPAROUND | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 4000 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0354SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0354 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #7 WEST NBHD FAMILY SERVICES CENTER | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1974 | 12500 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1995EXT1 | EXTERIOR FINISHES | 1995 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | POOLHOUSE/STORAGE | 9991 | HHS | DPBH | SNCAS | Las Vegas | 1981 | 836 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4180
0363INT1 | INTERIOR FINISHES | 0363 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15120
0363EXT1 | EXTERIOR FINISHES | 0363 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15120
0363SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0363 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #16 EARLY CHILDHOOD SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1995 | 3024 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1993INT1 | INTERIOR FINISHES | 1993 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Four to Ten Years | Long-Term Needs | 3 | 32900
1993EXT3 | EXTERIOR DOOR REPLACEMENT | 1993 | The existing exterior door in the storefront entrance is original to the building. It is damaged from age and general wear and tear and does not function properly. This project would provide for the replacement and installation of a new metal door, frame and ADA compliant hardware. Removal and disposal of the existing door is included in this estimate. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
1993ADA2 | ADA RESTROOM UPGRADE | 1993 | The designated unisex ADA accessible restroom is not fully compliant. The flush handle is on the wrong side, the faucet controls are not compliant and the sink location is not compliant. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #15 WEST NEIGHBORHOOD FAMILY SERVICES | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 6580 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 2000
1991SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1991 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | #13 RESIDENTIAL UNIT | 9991 | HHS | DCFS | SNCAS | Las Vegas | 1981 | 4610 | 2012-10-17 | Immediate to Two Years | Currently Critical | 1 | 4000
0243INT2 | INTERIOR FINISHES | 0243 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 38000
0243EXT3 | EXTERIOR FINISHES | 0243 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exposed outriggers is included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 53200
0243ADA1 | ADA MODIFICATIONS | 0243 | The restroom has been retrofitted for ADA accessibility but is not 100% ADA compliant. Also, the facility is lacking ADA direction signage. This project would provide for an ADA sign package and minor modifications to the existing ADA designated restroom. A new high low drinking fountain and casework modifications to the public reception area are also included in this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design were used for reference on this project This project or a portion there of was previously recommended in the FCA report dated 06/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 20000
0243INT1 | VINYL COMPOSITION TILE (VCT) REPLACEMENT | 0243 | The majority of the interior floor covering is vinyl composition tile (VCT) in poor condition. The VCT flooring in the building should be replaced. This project would provide for the removal and replacement of the VCT throughout the building. A $2,500 asbestos survey allowance is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58500
0243EXT5 | EXTERIOR DOOR REPLACEMENT | 0243 | The existing exterior doors and frames are damaged from age and use. This project would provide for the installation of 4 new door assemblies including frames hardware and paint, Removal and disposal of the existing doors is included in this estimate. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0243EXT6 | REPLACE WINDOWS AND FRAMES | 0243 | The existing wood framed window systems are damaged from age and exposure. This project would provide for the removal of the existing wood window systems and replacement with new aluminum storefront window systems. The remainder of the windows are old single pane and should be scheduled for replacement. This project would also provide for the installation of new dual pane window systems. Removal and disposal of the old window systems are included in this estimate. A total of 32 units was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38400
0243INT4 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 0243 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 32 doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
0243ADA2 | REPAIR SIDEWALKS | 0243 | Tree roots have damaged the sidewalks around the building causing uplift and cracking. In several areas, the damage is enough to cause the path of travel to no longer meet ADA accessibility requirements and is a tripping hazard. This project makes allowance for cutting the roots back to prevent further damage and repairing the sidewalks to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
0243SFT3 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0243 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
0243SIT2 | TREE REMOVAL | 0243 | There is a deciduous tree growing next to the building. The tree in time will cause damage to the foundation and structure. It should be removed before damage occurs. This project would provide funding to remove the tree. Debris removal is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #2 PHARMACY/LABORATORY BUILDING | 9991 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 7600 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1951EXT3 | EXTERIOR DOOR REPLACEMENT | 1951 | There are 5 single leaf exterior metal doors and 3 exterior storefront systems in need of replacement. They are damaged from age and abuse. This project would provide for the installation of new door systems including frames and hardware. Removal and disposal of the old units is included in this estimate. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
9992SIT2 | CRACK FILL AND SEAL ASPHALT PAVING | 9992 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the parking lot and access roads on the site. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 70,000 square feet of asphalt area was used to generate this estimate. | SNAMHS SITE | 9992 | HHS | DPBH | SNAMHS | Las Vegas |  |  | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
1954EXT3 | REROOF BUILDING | 1954 | The statewide roofing program has set the useful life of an average roof at 15-20 years. The roof warranty expires at the end of the same time frame. This roof was installed in 1995. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53000
1954ENV1 | RELOCATE IRRIGATION SYSTEM | 1954 | The existing irrigation system along the south side of the building appears to be spraying water on the side of the building. This has led to extreme damage to the exterior stucco and there are water stains on the interior gypsum board. This could lead to mold growth if not addressed soon. This project would provide for the relocation of the sprinklers away from the building as well as repairing damaged lines which were exposed in the southwest corner. This project should be completed prior to replacing the damaged stucco addressed in another project. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1000
1951ENR1 | REPLACE WINDOWS | 1951 | The windows in the building are original, not energy efficient and in need of replacement. This project would provide for the installation of new dual pane insulated window units. Safety glazing of window units is recommended due to the use of this facility. Removal and disposal of the old units is included in this estimate. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38400
1950INT8 | NURSES STATION UPGRADE | 1950 | There are 4 nurses stations that are in need of upgrades. The casework is worn from age and use and they should be scheduled for replacement. This project would provide for the removal of the existing casework and installation of new casework at the nurse's station. Removal and re-installation of existing glazing is included in the estimate. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
1950ADA4 | LOBBY CASEWORK ADA UPGRADE | 1950 | The existing entry / lobby reception area is not ADA compliant. This project would provide for new ADA compliant casework to be installed in the lobby area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 4500
1950ADA5 | ADA BUILDING SIGNAGE | 1950 | The building is lacking ADA compliant signage to identify spaces, restrooms and offices. This project would provide for the installation of ADA compliant signage throughout the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 8000
1950PLM6 | REPAIR SEWER LINES | 1950 | The existing sanitary sewer system in the building is failing in numerous areas. This project would provide for saw cutting, excavation and installation of new sanitary waste lines in the building. This project includes removal of the existing piping and fittings as required. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 300000
1950INT9 | REPLACE IINTERIOR DOORS | 1950 | The existing interior doors are worn from age and abuse. Many of the locking mechanisms do not operate properly and should be replaced. This project would provide for the installation of new hollow metal doors, frames, and hardware. Painting is included in this estimate Removal and disposal of the old doors and frames is included in this estimate. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 253000
1950EXT3 | EXTERIOR DOORS | 1950 | The existing exterior hollow metal door systems are damaged from age and abuse. This project would provide for 9 new exterior door assemblies to be installed including hardware and painting. Removal and disposal of the existing doors are included in this estimate. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29700
9992SIT3 | CONCRETE SIDEWALK REPAIRS | 9992 | There are some areas of damaged concrete walkways that are in need of replacement due to large cracks and heaving / settling. This project would provide for the removal and replacement of the damaged concrete walkways as needed. 1,000 square feet was used to generate this estimate. | SNAMHS SITE | 9992 | HHS | DPBH | SNAMHS | Las Vegas |  |  | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 10000
1954ENR1 | WINDOW REPLACEMENT | 1954 | There are two old aluminum windows which should be scheduled for replacement. This project would provide for two new dual pane window units to be installed.. Removal and disposal of the old windows is included in this estimate. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1954ENR2 | HVAC REPLACEMENT | 1954 | There are two evaporative coolers and one packaged unit on the roof which have reached the end of their expected life. This project would provide for two new evaporative coolers and one packaged unit to be installed on the roof. Roof curb modifications and connections to existing utilities are included in this estimate. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1954SFT6 | MEZZANINE STORAGE STAIRS GUARDRAILS | 1954 | The existing stairs and guardrails that access the mezzanine storage area do not meet current building code requirements. This project would provide for the removal of the existing stairs and rails and installation of new wood framed stairs and guardrails. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1200
1954INT2 | REPLACE VCT IN OFFICE | 1954 | The existing vinyl composition tile (VCT) is damaged from age and use. This project would provide for the installation of new VCT in the office area. Removal of the existing tile is included in this estimate. This cost does NOT include any monies for asbestos containing material testing or removal if it is present. 400 square feet was used for this estimate. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
1950EXT2 | EXTERIOR FINISHES | 1950 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exterior metal security cages is included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 189000
1950INT4 | RESTROOM WALL TILE REPLACEMENT | 1950 | Throughout the facility, the ceramic tile wall covering in the restrooms are cracked and failing. This project recommends replacement of the ceramic tile wall coverings. This project should be coordinated with the accessibility upgrade, which includes ADA restroom remodeling if they have not been completed. Demolition of the existing tile is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 6/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1950SFT3 | REPLACE EXERCISE YARD CONCRETE | 1950 | A secured exercise area surrounds the exterior of the building. Patients are allowed in this area. Much of the concrete flatwork is irregularly surfaced or broken and presents a hazard. This project would provide for the removal and replacement of the concrete slab in the exercise area. This project or a portion thereof was previously recommended in the FCA report dated 6/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 25000
1950INT6 | FLOORING REPLACEMENT | 1950 | Approximately one-third of the floor covering in this building is carpet, in poor condition. It is recommended that the carpet be replaced with heavy duty institutional grade carpet in the next one to two years. The remainder is a vinyl composition tile (VCT) except for the restrooms which is ceramic tile. This is also in poor condition. This project would provide for the removal and replacement of the carpet ceramic tile and VCT in this building. This project or a portion there of was previously recommended in the FCA report dated 06/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 340200
1950INT5 | INTERIOR FINISHES | 1950 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 189000
1951INT2 | INTERIOR FINISHES | 1951 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 53500
1949EXT3 | CONCRETE FLATWORK | 1949 | The concrete slab outside Rooms 111 and 139 has been broken and lifted up by tree roots. These areas should be repaired. At the exterior door to Room 122, there is a step down to the landing. This presents a hazard and is not in compliance with the International Building Code. This project recommends replacing the slab so the threshold is not more than ½" higher than the exterior concrete landing and changing the door swing so it does not swing out over the step. This project or a portion there of was previously recommended in the FCA report dated 06/23/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 1500
1952INT2 | INTERIOR FINISHES | 1952 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1952EXT3 | EXTERIOR FINISHES | 1952 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1949SFT1 | INSTALL FIRE SPRINKLER SYSTEM | 1949 | Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or has an addition. The building in this report is currently classified as a B occupancy. This project would provide for a fire sprinkler system to be installed including backflow prevention and monitoring. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 210000
1949INT3 | STORAGE ROOM RAMP | 1949 | The door into Room 128, a storage room, swings out over a set of stairs. This step down is a violation of the International Building Code. This project recommends building a wooden landing inside the door and a ramp down to the lower floor, to make the space more usable. Steel prefabricated handrails should be provided. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1950PLM3 | PLUMBING FIXTURES / IMPROVEMENTS | 1950 | At the nurses stations in rooms 146, 232, and 265, the sinks and faucets should be replaced. Room 211 has a sink which should be removed and the pipes capped off. In medical exam room 127, the faucet should be replaced. The drain piping from the dishwasher in kitchen 214 requires an air gap fitting. Also, this project would provide for the installation of new toilets, sinks, faucets and casework, shower pans, tubs, toilet partitions and drinking fountains for lower and upper level. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
1951EXT1 | EXTERIOR FINISHES | 1951 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exposed outriggers is included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 53500
1949EXT4 | EXTERIOR FINISHES | 1949 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. The wood outriggers are in need of sanding, sealing and painting as soon as possible to prevent further damage. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 210000
1949INT4 | INTERIOR FINISHES | 1949 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next five to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
1949EXT5 | WINDOW / DOOR GLAZING REPLACEMENT | 1949 | There are ten windows that face onto the patio. They are single pane glazed units and should be replaced with dual-pane glass. This project would provide for the removal and replacement of these windows. Safety glazing will be used in areas required by the 2012 IBC. Also, the remaining 70 windows are single pane and original to the facility. This project also would provide for the installation of new windows throughout the building. Removal and disposal of the existing windows is included in this estimate. 6 glass double doors are also included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 6/25/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 330420
1952ADA2 | ADA UPGRADES | 1952 | There is an ADA restroom located in the facility which is in need of some minor improvements. Also, the existing drinking fountain is non-ADA compliant. This project would provide for a new high-low ADA compliant drinking fountain and minor modifications to the restroom which may include flush handle modifications and some fixture location improvements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 6000
1950SFT1 | FIRE ALARM UPGRADE | 1950 | This building is equipped with an automatic fire detection and alarm system, but the system has reached the end of it's serviceable life. It is recommended that the fire detection and alarm system be upgraded. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 30000
1951INT1 | CARPET AND TILE REPLACEMENT | 1951 | The interior floor covering is vinyl tile, in poor condition. The carpet is stained, and repeated cleanings have failed to eliminate the stains. The flooring in the building should be replaced. This project would provide for the removal and replacement of the carpet and vinyl tile throughout the building. This project does not include the ceramic floor tile in the restrooms. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 74900
1951EXT6 | INSTALL EXTERIOR HANDRAILS | 1951 | The 2012 IBC Chapter 1009.15 requires handrails be installed on stairs with two or more risers. The exterior stairs do not meet these requirements. This project would provide for two 1-1/2 inch diameter steel handrails, one on each side of the stairway to meet the 2003 IBC code requirements. Painting of the railing is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 2500
1953SFT1 | REPLACE LOADING DOCK STAIRS | 1953 | The 2003 IBC Chapter 1009.5.1 requires the horizontal slope of stair treads in any direction not to exceed 2 percent. Chapter 1009.11 requires handrails be installed on stairs with two or more risers and a landing is required at the top and bottom of the stairs. The stairs next to the loading dock do not meet these requirements. This project would provide for the rebuilding of the concrete stairway to meet the 2012 IBC code requirements. Two handrails, one on each side of the stairway are included in this cost estimate. This project or a portion there of was previously recommended in the FCA report dated 6/18/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1949INT6 | VINYL COMPOSITION TILE (VCT) REPLACEMENT | 1949 | The existing vinyl composition tile (VCT) is in poor condition and should be scheduled for replacement. This project would provide for the installation of new VCT in the facility. Removal and disposal of the old tile is included in this estimate. A $2,500 allowance for an asbestos survey is included in this estimate. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132100
1949ADA2 | INSTALL HIGH LOW DRINKING FOUNTAIN | 1949 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 4000
1954EXT1 | EXTERIOR FINISHES | 1954 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 6/18/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 26500
1954PLM3 | REPLACE WATER HEATER | 1954 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the old electric water heater is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9992ADA1 | ADA SIGNAGE | 9992 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established signage criteria for permanent spaces in buildings and accessible route of travel from parking to building(s). The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide for directional signage along the accessible route of travel from the ADA accessible parking to each building and public space. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design were used for reference on this project. This project or a portion there of was previously recommended in the FCA report dated 02/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | SNAMHS SITE | 9992 | HHS | DPBH | SNAMHS | Las Vegas |  |  | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 5000
1949SFT3 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1949 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
1950SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1950 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3500
1951INT7 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 1951 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 25 doors was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
1951INT5 | REPAIR WOMEN'S SHOWER | 1951 | The Women's restroom has an active leak in the shower area and has caused damage to the gypsum board of the adjacent room. If the leak and gypsum board is not repaired, the moisture may cause mold and dry-rot. This project would provide for the repair to the shower. This may include removal of the ceramic tile shower pan and 2 courses of wall tile, waterproofing the shower pan and reinstall tile, grout and seal. Removal and replacement of the gypsum board in the adjacent room will be required if it has been damaged. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 2000
1954SFT3 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1954 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1954INT1 | INTERIOR FINISHES | 1954 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26500
1951ADA2 | REPAIR SIDEWALK | 1951 | Tree roots have damaged the sidewalk around the south side of the building causing uplift and cracking. The damage is enough to cause the accessible path of travel to no longer meet ADA requirements. This project makes allowance for cutting the roots back to prevent further damage and repairing the sidewalks to meet ADA requirements and eliminate a tripping hazard. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 6/16/1998 and 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1200
1950INT7 | REPAIR ELEVATOR | 1950 | This building has a passenger elevator and a cargo elevator. The cargo elevator is out of service. This project would provide funding to repair the elevator to facilitate maintenance and control of the building. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1950PLM5 | REPLACE BOILERS / UPGRADE HVAC SYSTEM | 1950 | The two 1987 Hydrotherm boilers are original to the building, and are about 20 years old. The boilers are reaching the end of their serviceable life span, and should be scheduled for replacement. Two 500 MBH steam boilers were used for this cost estimate. This project should be implemented at the same time as the water treatment system project to ensure proper operation and care of the boilers. This project also includes monies for upgrades and work to existing equipment including but not limited to new VAV terminal units, exhaust fans on roof, diffusers, 2 scroll compressors, temperature controls and commissioning. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 225000
1950HVA3 | REPAIR WATER TREATMENT SYSTEM | 1950 | The chemical water treatment system was not operating at the time of the survey. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. This project should coincide with the HVAC replacement project. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3 INPATIENT HOSPITAL | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1988 | 37800 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 12000
1954SFT4 | OSHA SAFETY CABINETS | 1954 | Flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity, shall have a proper storage container, OSHA Chapter 1910.106 (7) (d). This project would provide two OSHA approved storage cabinets for gasoline, aerosol cans and other flammable items. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 6000
1949INT5 | INTERIOR DOOR ASSEMBLY REPLACEMENT | 1949 | The existing interior door assemblies are damaged from abuse and age. This project would provide for the removal of the existing door assemblies and the purchase and installation of new metal door assemblies. All hardware and painting is included in this estimate. Hardware is to include security keys and fusible links (for one-hour door assemblies) or where applicable. A total of 89 doors was used for this estimate. Removal and disposal of the existing door assemblies is also included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #1 ADMINISTRATION/OUTPATIENT SERVICES | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1969 | 30000 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 195800
1954SFT5 | INSTALL FIRE ALARM SYSTEM | 1954 | This building is lacking an automatic fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 21200
1954STR1 | STRUCTURAL ASSESSMENT OF STORAGE FLOOR | 1954 | An upper level storage mezzanine has been constructed inside of the Storage Building. The 2012 IBC Table 1607.1 has a minimum load requirement of 125p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and it could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 1500
1954EXT2 | REPLACE DAMAGED WOOD / STUCCO | 1954 | The existing wood and stucco finish along the loading dock and the south side is damaged and is in need of replacement. This project would provide for the removal of the existing stucco and wood exterior finish and installation of a new exterior stucco finish on the south side. Disposal of the old stucco and wood is included in this estimate. This project should be implemented concurrent with or after the irrigation system project has been completed. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2013. | #6 STORAGE/SHOP | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1981 | 5300 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 4320
0360EXT1 | EXTERIOR FINISHES | 0360 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. Reassigned to other projects. | #6A STORAGE BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 2005 | 800 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0360INT1 | INTERIOR FINISHES | 0360 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. Reassigned to other projects. | #6A STORAGE BUILDING | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 2005 | 800 | 2012-10-18 | Four to Ten Years | Long-Term Needs | 3 | 4000
1953INT1 | INTERIOR FINISHES | 1953 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7290
1953EXT3 | EXTERIOR FINISHES | 1953 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. Painting and / or sealing of the exposed outriggers is included as part of this project. | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 7290
1953SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1953 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012 | #5 FOOD SERVICE CENTER STORAGE | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 1458 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1952SFT0 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1952 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion there of was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #4 FOOD SERVICE CENTER | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 3400 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
1951SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 1951 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 2/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/18/2012. | #3A CRISIS OBSERVATION UNIT | 9992 | HHS | DPBH | SNAMHS | Las Vegas | 1972 | 10700 | 2012-10-18 | Immediate to Two Years | Currently Critical | 1 | 3000
0370ADA3 | ADA SIGNAGE | 0370 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1200
0371INT8 | INTERIOR FINISHES | 0371 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 24530
1959ENR1 | HVAC REPLACEMENT | 1959 | The HVAC cooling units and furnaces are not energy efficient and have reached the end of their expected and useful life. They are original to the building and are now over 20 years old. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 21750
1959PLM2 | WATER HEATER REPLACEMENT | 1959 | There is a 50 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1500
0367ENR1 | HVAC REPLACEMENT | 0367 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70275
0706ADA2 | ADA RESTROOM REMODEL | 0706 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restroom in the corridor and 1 unisex accessible restroom for the bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0370ENR1 | WINDOW REPLACEMENT | 0370 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0706INT5 | VCT FLOORING REPLACEMENT | 0706 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23850
0627EXT3 | EXTERIOR FINISHES | 0627 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO WEST (STORAGE) | 9993 | HHS | ADSD | DRC | Las Vegas | 1971 | 360 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1800
0628EXT3 | EXTERIOR FINISHES | 0628 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO EAST (STORAGE) | 9993 | HHS | ADSD | DRC | Las Vegas | 1971 | 360 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1800
0626EXT3 | EXTERIOR FINISHES | 0626 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GAZEBO SOUTH (STORAGE) | 9993 | HHS | ADSD | DRC | Las Vegas | 1971 | 360 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 1800
0372ELE2 | ELECTRICAL TRANSFORMER REPLACEMENT | 0372 | There is an electrical transformer located inside the mechanical room. The transformer is over 40 years old and was putting off more heat than it should at the time of the survey. This project recommends replacing the transformer with a new 150 kVA 3-phase power transformer. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0372PLM3 | WATER HEATER SEISMIC BRACING | 0372 | The water heater and water storage tank are not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater and water storage tank to the structure. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
0372INT5 | FLOORING REPLACEMENT | 0372 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 5-6 years. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 108000
1959ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1959 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0371ELE1 | EMERGENCY GENERATOR REPLACEMENT | 0371 | The building does not have an emergency back-up generator. The generator that used to back-up the building has reached the end of its useful life and has been removed. This project would provide for a new diesel powered 300 KVA generator including required connections to utility systems. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0706ADA3 | ADA SIGNAGE | 0706 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
0370HVA1 | HVAC REPLACEMENT | 0370 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43860
0370EXT4 | EXTERIOR FINISHES | 0370 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14620
0371ADA2 | KITCHEN REMODEL | 0371 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0371EXT3 | EXTERIOR FINISHES | 0371 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24530
0256SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0256 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0367SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0367 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0368SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0368 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0369SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0369 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0370SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0370 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0369INT5 | NONABSORBENT FINISHES | 0369 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0371SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0371 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0706SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0706 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
1671SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1671 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0372SIT3 | SITE DRAINAGE IMPROVEMENTS | 0372 | The building has considerable damage to the stucco finish and foundation from improper drainage around the building. The grade does not slope away from the building in several areas, especially on the east and west sides of the building. This is causing water to pool up next to the building, infiltrate the interior and damage the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0369ADA2 | ADA RESTROOM REMODEL | 0369 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 3 restrooms is necessary. This project would provide funding for construction of 2 unisex accessible restrooms in the corridor and 1 unisex accessible restroom between bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0367ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0367 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0368INT8 | FLOORING REPLACEMENT | 0368 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 45936
0368ENR1 | HVAC REPLACEMENT | 0368 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76560
0368ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0368 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0369INT8 | INTERIOR FINISHES | 0369 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 25520
0369INT9 | FLOORING REPLACEMENT | 0369 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 4-5 years. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 40832
0706ENR1 | HVAC REPLACEMENT | 0706 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39750
0369ENR1 | HVAC REPLACEMENT | 0369 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76560
1959INT7 | FLOORING REPLACEMENT | 1959 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11600
0369ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0369 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0369ADA4 | ADA SIGNAGE | 0369 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1200
0369ADA5 | KITCHEN REMODEL | 0369 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0370ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0370 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0706ADA4 | KITCHEN REMODEL | 0706 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1671ENR1 | HVAC REPLACEMENT | 1671 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39750
1671ADA2 | ADA RESTROOM REMODEL | 1671 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restroom in the corridor and 1 unisex accessible restroom for the bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
1671ADA3 | ADA SIGNAGE | 1671 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
1671ADA4 | KITCHEN REMODEL | 1671 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1672INT5 | VCT FLOORING REPLACEMENT | 1672 | The VCT (vinyl composite tile) flooring in the gymnasium is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23850
1672ENR1 | HVAC REPLACEMENT | 1672 | The HVAC roof top units and furnaces are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39750
1672ADA2 | ADA RESTROOM REMODEL | 1672 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restroom in the corridor and 1 unisex accessible restroom for the bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1672ADA4 | KITCHEN REMODEL | 1672 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
1672ADA3 | ADA SIGNAGE | 1672 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1000
1671INT5 | VCT FLOORING REPLACEMENT | 1671 | The VCT (vinyl composite tile) flooring in the gymnasium is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23850
9993ELE1 | INTERCOM SYSTEM REPLACEMENT | 9993 | The buildings on the site are equipped throughout with an intercom system, but the system is older and no longer functioning. This project would provide for a new wireless intercom system including an amplifier, speakers and antennas as required for a complete operating system. The main station would be located in Building #1391 Administration building. 11 residential buildings are recommended for this installation. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
0372INT4 | INTERIOR FINISHES | 0372 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67500
0368SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0368 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 2552
0368EXT5 | EXTERIOR FINISHES | 0368 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25520
0370ADA5 | KITCHEN REMODEL | 0370 | The kitchen in the building is in fair to poor condition. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0369EXT4 | EXTERIOR FINISHES | 0369 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25520
0370ADA4 | ADA RESTROOM REMODEL | 0370 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 restrooms is necessary. This project would provide funding for construction of 1 unisex accessible restrooms in the corridor and 1 unisex accessible restroom between bedrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0370INT4 | INTERIOR FINISHES | 0370 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14620
0367EXT2 | EXTERIOR FINISHES | 0367 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23425
1672SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1672 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
1959SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1959 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0368INT6 | INTERIOR FINISHES | 0368 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25520
9993EXT2 | EXTERIOR FINISHES, SHADE RAMADAS | 9993 | There are 10 steel ramadas in different locations throughout the site which measure 18'x22' each for a total of 3,960 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7920
9993EXT3 | EXTERIOR FINISHES, STORAGE SHEDS | 9993 | There are 18 storage sheds located throughout the site ranging from 100 to 216 square feet each for a total of 2,560 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project recommends work to protect the buildings, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project should be done on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12800
1959INT6 | NONABSORBANT FINISHES | 1959 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material in both restrooms to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1959EXT1 | EXTERIOR FINISHES | 1959 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 7250
1672INT4 | INTERIOR FINISHES | 1672 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
1671INT4 | INTERIOR FINISHES | 1671 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
0706INT4 | INTERIOR FINISHES | 0706 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
0367INT3 | INTERIOR FINISHES | 0367 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23425
0372EXT5 | EXTERIOR FINISHES | 0372 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 67500
0367INT4 | INTERIOR DOOR REPLACEMENT | 0367 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0372SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0372 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 10000
9993ENR1 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 9993 | This project recommends the installation of an Energy Management System (EMS) for the entire site. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment on the site and in each building through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. A new system has been installed on the Administration building. This estimate is based on installing the system on the rest of the buildings and connecting it to the existing system except for the residential cottages. The system is recommended to coincide with the HVAC project recommendations. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
0706EXT2 | EXTERIOR DOOR REPLACEMENT | 0706 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0256EXT3 | EXTERIOR FINISHES | 0256 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 53280
0256ENR1 | WINDOW REPLACEMENT | 0256 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0256ELE2 | ELECTRICAL UPGRADE | 0256 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 213120
0256INT8 | ADA RESTROOM UPGRADE | 0256 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 2 Men's and 2 Women's restrooms is necessary. This project would provide funding for construction of 2 Men's and 2 Women's accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 100000
9993SEC2 | SECURITY SYSTEM | 9993 | The facility currently does not have a security system installed. Access on or off of the property is uncontrolled and there have been security problems including the homeless inhabiting areas of the property. This project recommends card-access control, security fencing, security cameras and additional site lighting be installed to remedy this problem. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250000
0370INT6 | INTERIOR DOOR REPLACEMENT | 0370 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0372SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0372 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 4000
0369INT7 | INTERIOR DOOR REPLACEMENT | 0369 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9993SIT6 | LANDSCAPE RENOVATIONS | 9993 | The existing landscaping on the site consists of a large amount of lawn interspersed with trees and shrubbery. The maintenance staff noted that the lawn is a maintenance problem due to the cost of water and labor to maintain it in the desert climate of Las Vegas. This project would provide for removal of most of the lawn and replacement with a xeriscape landscape while preserving the more mature trees and shrubbery. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
0371INT7 | INTERIOR DOOR REPLACEMENT | 0371 | There are several existing interior bi-pass closet doors that are damaged from abuse and age. This project would provide for the removal of the existing bi-pass doors and the purchase and installation of new solid core wood hinged doors and hollow metal frames. All hardware, painting and framing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0256INT5 | JANITORS CLOSET REPAIRS | 0256 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0367HVA1 | REPLACE HVAC SYSTEM | 0367 | The heating and cooling to this building is provided by forced air furnaces with cooling coils that are original equipment. Based on the age of the equipment, this report recommends scheduling replacement of these units within the next two to four years. This project or a portion there of was previously recommended in the FCA report dated 06/17/1998. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/07/2008. Project complete. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0367EXT3 | WINDOW REPLACEMENT | 0367 | The existing windows in this building are of single pane wire mesh construction in metal frames. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0256ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0256 | This building contains three water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 8000
0256ADA4 | ADA SIGNAGE | 0256 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 1500
0706EXT1 | EXTERIOR FINISHES | 0706 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1310 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
1671EXT1 | EXTERIOR FINISHES | 1671 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1309 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13250
1959INT5 | INTERIOR FINISHES | 1959 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1307 MULTI-PURPOSE | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 1450 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7250
0372EXT1 | EXTERIOR DOOR REPLACEMENT | 0372 | The 13 exterior wood and metal man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood and metal doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
0370EXT2 | EXTERIOR DOOR REPLACEMENT | 0370 | The 5 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This estimate does not include the direct exit doors from the bedrooms. This project or a portion there of was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1301 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 2924 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0372EXT2 | WINDOW REPLACEMENT | 0372 | The windows and skylights are original and should be scheduled for replacement. The windows are single pane in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. The skylights have had numerous leaks and are cracked in several places. This project recommends replacing the windows with dual pane, higher efficiency units and replacing the skylights with new skylight systems.. This estimate is for the replacement of 60 window units including wooden frames and 2 skylights. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1300 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1972 | 13500 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0369EXT5 | CONCRETE LANDING REPLACEMENT | 0369 | The client bedrooms have exterior doors which open directly onto concrete landings in eight locations. The landings do not comply with 2012 IBC Section 1008.1.5 which requires the landing to be at the same elevation on each side of the door and to not exceed a two percent slope. This project addresses installing landings designed to current codes and connecting to the existing site flatwork. This report recommends removing shrubbery on the latch edge of the main entry door, and placing concrete level with the front landing to provide an accessible entry. This project or a portion there of was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0371EXT1 | EXTERIOR DOOR REPLACEMENT | 0371 | Most of the exterior doors are hollow core metal doors and severely rusted. This project allows for the replacement of 6 existing metal doors and frames with insulated steel doors. The price includes new hardware and disposal of the existing door assemblies. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0371ENR1 | WINDOW REPLACEMENT | 0371 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1306 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1981 | 4906 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0368ENR3 | WINDOW REPLACEMENT | 0368 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 27 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1302 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0369EXT1 | EXTERIOR DOOR REPLACEMENT | 0369 | The 12 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This estimate does not include the direct exit doors from the bedrooms. This project or a portion there of was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1303 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 5104 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
0256ELE3 | EMERGENCY GENERATOR REPLACEMENT | 0256 | The building does not have an emergency back-up generator. The generator that used to back-up the building has reached the end of its useful life and has been removed. This project would provide for a new diesel powered 300 KVA generator including required connections to utility systems. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 100000
0256INT10 | CARPET REPLACEMENT | 0256 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66500
0367ADA2 | ADA RESTROOM UPGRADE | 0367 | There are several restrooms in the building. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the large Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0367ADA3 | BREAK ROOM REMODELS | 0367 | The kitchenettes and associated cabinets in the two employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 30000
0256INT9 | INTERIOR FINISHES | 0256 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 53280
0367ADA4 | ADA SIGNAGE | 0367 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 900
0256ADA3 | BREAK ROOM REMODEL | 0256 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 02/06/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1391 DRC ADMINISTRATION | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 10656 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 15000
9993ENV1 | PEST CONTROL | 9993 | There are numerous stray rabbits that have taken up residence throughout the site. The rabbits cause many problems including digging holes that people trip in, damaging the landscaping including eating the plants, leaving droppings all over the campus and possibly spreading diseases. Due to these issues, this project provides for removal of the rabbits and clean up of the droppings by a licensed pest control business. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9993SIT9 | DRAINAGE REPAIRS | 9993 | There are numerous places where drainage ponding occurs on Transverse Drive. The entire roadway should be removed and replaced, and a sidewalk with curb and gutter should be installed along the north side of Transverse Drive, after grading occurs to achieve proper drainage. This project provides for removal and replacement of the asphalt paving and concrete sidewalks. 40,000 square feet of roadway and sidewalks was used to generate the estimate. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
0367INT5 | FLOORING REPLACEMENT | 0367 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37480
9993SIT8 | SEWER SYSTEM REPLACEMENT | 9993 | The sanitary wastewater system is showing signs of deterioration. Because of the deterioration, the system is not working to its full potential. Most of the lines are original to the site and are in fair to poor condition. The passage of time and constant heavy use are contributing factors to problems that arise. Deposits within the pipes will cause them to be restricted, which will slow the flow of water. This project would provide for the complete replacement of the sanitary sewer system on site from the city connection to each occupied building on site. This project would provide for the removal and installation a new sewer / waste water infrastructure in the building including all connections, supports, anchoring. 5,000 lineal feet of cast iron pipe was used to generate this estimate. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
0367PLM3 | PLUMBING REPAIRS | 0367 | In the kitchen and laundry areas, there are three faucets that have been damaged and should be replaced. The dishwasher in one kitchen was installed without an air gap fitting; this report recommends one be installed. There is one exterior hose bibb that is not freeze proof; its' replacement is recommended. This project or a portion there of was previously recommended in the FCA reports dated 06/15/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1304 OFFICE | 9993 | HHS | ADSD | DRC | Las Vegas | 1976 | 4685 | 2013-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1672EXT1 | EXTERIOR FINISHES | 1672 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 06/17/1998 and 02/07/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/04/2013. | #1308 RESIDENTIAL | 9993 | HHS | ADSD | DRC | Las Vegas | 1992 | 2650 | 2013-06-04 | Immediate to Two Years | Currently Critical | 1 | 13250
9993SIT7 | SLURRY SEAL ASPHALT PAVING | 9993 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 130,000 square feet of asphalt area was used to generate this estimate. | DESERT REGIONAL CENTER SITE | 9993 | HHS | ADSD | DRC | Las Vegas |  |  | 2013-06-04 | Four to Ten Years | Long-Term Needs | 3 | 97500
0188ADA6 | ADA ACCESSIBLE COUNTER | 0188 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The admitting station has a service counter for the inmates and staff to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0188SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0188 | Problems exist with the door control panel and door locks for the controlled doors. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 10 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 150000
0188ADA7 | ADA RESTROOM REMODELS | 0188 | The accessible restrooms in the building are not completely compliant and do not have stainless steel, institutional-grade equipment. A complete retrofit is necessary. This project would provide funding for remodeling the four Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint including that the fixtures are institutional-grade, stainless steel fixtures. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0190CUL1 | KITCHEN EQUIPMENT REPLACEMENT | 0190 | Most of the kitchen cooking equipment has been removed from the building to supply occupied facilities. The equipment that is still installed is original to the building and has reached the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next one to two years, including ovens and hoods, grills, sinks and dishwashers. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. The propane tanks have been removed from the site. If any propane fired equipment is installed, additional costs must be included for the purchase and installation of the propane system. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 300000
0191EXT3 | EXTERIOR DOOR REPLACEMENT | 0191 | The existing exterior doors to the Laundry & Dry Cleaning are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 6 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 9000
0192EXT5 | EXTERIOR DOOR REPLACEMENT | 0192 | The existing exterior doors to the Auto Maintenance Shop/Warehouse are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 3 doors was used to generate this estimate. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4500
0190EXT4 | EXTERIOR DOOR REPLACEMENT | 0190 | The existing exterior doors to the Culinary/Dining/Central Plant are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 15 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 22500
0193EXT5 | EXTERIOR DOOR REPLACEMENT | 0193 | The existing exterior doors to the Auto Maintenance Shop are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0194PLM4 | WATER HEATER REPLACEMENT | 0194 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
9994PLM1 | PLUMBING SCOPE SERVICE | 9994 | The plumbing supply lines and sewer lines should be thoroughly inspected prior to reoccupying the facility. After being abandoned, many problems can occur with the plumbing including breaks from shifting soils, blockages or deterioration from rust. It is recommended to have the piping scoped with a camera to determine whether there are any problems with the lines. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
9994ELE3 | HIGH MAST LAMP REPLACEMENT | 9994 | There are 10 high mast security light poles throughout the facility that have 8 security lamps each. A lot of these lamps were burned out at the time of the survey and should be scheduled for replacement. This project provides for the purchase and installation of 80 security lamps for the high mast light poles. The cost includes removal and disposal of the existing lamps. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0181INT4 | INTERIOR FINISHES | 0181 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0180INT4 | INTERIOR FINISHES | 0180 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0180EXT6 | EXTERIOR FINISHES | 0180 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0176ADA5 | REMOVE/ REPLACE CONCRETE PATIO | 0176 | Outside of the Visitation Room is a concrete patio with stairs and terraces which provides an outdoor space to visit with inmates. The patio is in disrepair with major cracks in the concrete, stairs that do not comply with code and no compliance with ADA requirements. This project would provide for removal of the existing improvements and installation of a new flat concrete patio which complies with all applicable codes. Removal and disposal of the existing concrete is included in this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 22500
0191INT3 | INTERIOR FINISHES | 0191 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 24000
0179PLM5 | WATER HEATER REPLACEMENT | 0179 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0191ADA1 | ADA SIGNAGE | 0191 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0194EXT2 | EXTERIOR DOOR REPLACEMENT | 0194 | The existing exterior doors to the Guard Tower are original to the building. They are showing signs of wear and deterioration. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0181SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0181 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0188INT3 | INTERIOR FINISHES | 0188 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 51500
0179ADA4 | ADA UPGRADES - STAGE | 0179 | The Chapel is lacking an accessible path to the stage. The stage is required to have an accessible path to it per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp or powered lift to access the stage. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0190HVA1 | HVAC REPLACEMENT | 0190 | Four evaporative coolers are installed on the roof of this building. They are severely scaled and have reached the end of their useful and expected life. This project would provide for four new evaporative coolers to be installed including all required connections to utilities. The estimate includes removal and disposal of the old coolers. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 350000
0190EXT5 | EXTERIOR FINISHES | 0190 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. There are areas where the stucco is damaged from equipment hitting the walls and leaks from the rooftop HVAC equipment. This project includes funds to repair the damaged areas prior to painting. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 140000
2567EXT3 | EXTERIOR DOOR REPLACEMENT | 2567 | The existing exterior door to the Recreation / Gym is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0195EXT3 | EXTERIOR DOOR REPLACEMENT | 0195 | The existing exterior doors to the Guard Tower are original to the building. They are showing signs of wear and deterioration. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 2 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0191EXT4 | EXTERIOR FINISHES | 0191 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. There are areas where the stucco is damaged from equipment hitting the walls and leaks from the rooftop HVAC equipment. This project includes funds to repair the damaged areas prior to painting. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 24000
0192ADA1 | ADA SIGNAGE | 0192 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
2567ENR1 | LIGHTING REPLACEMENT | 2567 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 365
0194EXT1 | EXTERIOR SIDING REPLACEMENT | 0194 | The Tower has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 75000
0195EXT2 | EXTERIOR SIDING REPLACEMENT | 0195 | The Tower has a painted masonite siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the masonite siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 75000
0193ADA2 | ADA RESTROOM REMODEL | 0193 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0193PLM3 | WATER HEATER REPLACEMENT | 0193 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0192SFT5 | MEZZANINE REMOVAL | 0192 | The second floor mezzanine appears to be constructed without building permits or structural calculations. Since the mezzanine is now enclosed, it does not meet the building code's definition of a mezzanine. The area also does not have proper ventilation, smoke detectors or compliant stairs and railings. This project would provide funding for the removal of the second floor mezzanine and stairs. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0183INT4 | INTERIOR FINISHES | 0183 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0192INT2 | INTERIOR FINISHES | 0192 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50300
2567EXT2 | EXTERIOR FINISHES | 2567 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 810
0192ADA3 | ADA RESTROOM REMODEL | 0192 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0192PLM3 | WATER HEATER REPLACEMENT | 0192 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0192SFT6 | HANDRAIL INSTALLATION | 0192 | There are two steps leading from one bay to the next that do not have handrails. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. NRS 338.180, 2012 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0192SFT7 | INTERIOR LANDING INSTALLATION | 0192 | There is an out-swinging interior door in the building which swings out over a step and does not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
9994SIT5 | FACILITY START-UP / RECOMMISSIONING | 9994 | The Southern Nevada Correctional Center was vacant during the survey of 2016. During the site visit to all of the buildings, there were numerous plumbing leaks, damaged plumbing fixtures and active water leaks. The central plant was running at minimum capacity and some of the buildings' HVAC components had not been in service since the closure of the prison. This project would provide for anticipated start-up costs and recommissioning of the entire facility including complete HVAC, plumbing and waste line testing and repairs, culinary ansul fire protection and cooking equipment start-up and inspection, and fire protection system testing and inspection. The possible replacement of existing HVAC equipment in the central plant is not included in this estimate as it is unknown. Actual fixture replacement of plumbing fixtures and cooking equipment is not included in this project as it is unknown until facility is opened again. Projects for plumbing fixture replacement are addressed in the individual building project reports and mostly address replacement of porcelain fixtures with stainless steel. Kitchen equipment replacement is addressed in the individual building report. This is a budgetary allowance for anticipated costs associated with the start-up and preoccupancy of the facility. Any potential leaks or damage to the underground hot water loop, domestic water and waste lines in unknown due to facility not being in operation. This project is a priority one project and will need to be done prior to occupancy. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3380000
0194PLM3 | PLUMBING FIXTURES REPLACEMENT | 0194 | The existing water closet and sink are reaching the end of their expected life. They are worn and damaged from many years of use and should be scheduled for replacement. This project would provide for the installation of a new water closet and sink including all plumbing parts and connections. Removal and disposal of the old fixtures is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0192EXT4 | EXTERIOR FINISHES | 0192 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting and sealing the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50300
0187SFT4 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0187 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0180ELE3 | ELECTRICAL UPGRADE | 0180 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0180HVA2 | HVAC REPLACEMENT | 0180 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0187PLM6 | PLUMBING FIXTURE REPLACEMENT | 0187 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0186SFT4 | WINDOW INSTALLATION | 0186 | The upper level room overlooking the gymnasium is missing several window panels. A total of nine panels have been removed creating a safety hazard. It is recommended to reinstall the glazing panels. This estimate is for the purchase and installation 9-6'x5' security glazing panels. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 21600
0186INT3 | FLOORING REPLACEMENT | 0186 | The composite flooring in the gymnasium and the VCT (vinyl composite tile) in the Gun Post are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new composite floor in the gymnasium and 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the Gun Post in the next 1-2 years. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 204800
0186ADA5 | ADA RESTROOM/ SHOWER REMODEL | 0186 | The existing restroom and shower area is in poor condition and does not meet ADA accessibility standards. This project would provide for the remodeling of the restroom / shower area including new floor tile and wall finishes, fixtures and providing ADA compliance. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 37000
2567INT2 | FLOORING REPLACEMENT | 2567 | The VCT (vinyl composite tile) flooring in the building is worn and damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1134
0186EXT2 | EXTERIOR FINISHES | 0186 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128000
2567INT1 | INTERIOR FINISHES | 2567 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SALLY PORT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 810
0187ADA6 | ADA UPGRADES | 0187 | 3% of the cells in each housing unit are required to comply with ADA accessibility guidelines. This unit does not have any accessible cells, showers, drinking fountains or path of travel through the unit. This project would provide for 2 accessible cells, 1 accessible shower, 2 accessible drinking fountains, a compliant path of travel from the entrance of the building to these areas and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 70000
0187EXT4 | EXTERIOR FINISHES | 0187 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 180900
0187ELE3 | ELECTRICAL REPLACEMENT | 0187 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 723600
0185PLM3 | PLUMBING FIXTURE REPLACEMENT | 0185 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 44 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0182INT4 | INTERIOR FINISHES | 0182 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0188PLM3 | WATER HEATER REPLACEMENT | 0188 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0184INT4 | INTERIOR FINISHES | 0184 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0186ELE2 | ELECTRICAL UPGRADE | 0186 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 512000
0183EXT7 | EXTERIOR DOOR REPLACEMENT | 0183 | The existing exterior door to the Housing Unit 4 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0194ENR1 | LIGHTING UPGRADE | 0194 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed where appropriate for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0195INT2 | INTERIOR FINISHES | 0195 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25600
0194INT2 | INTERIOR FINISHES | 0194 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25600
0179INT4 | INTERIOR FINISHES | 0179 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped including the damaged area where the HVAC unit was removed. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0179EXT4 | EXTERIOR DOOR REPLACEMENT | 0179 | The existing exterior doors to the Chapel/Law Library are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 4 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0180EXT5 | EXTERIOR DOOR REPLACEMENT | 0180 | The existing exterior door to the Housing Unit 1 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0176EXT6 | EXTERIOR DOOR REPLACEMENT | 0176 | The existing exterior doors to the Administration/ Visitation are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 9 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 13500
0182EXT5 | EXTERIOR DOOR REPLACEMENT | 0182 | The existing exterior door to the Housing Unit 3 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0195PLM4 | WATER HEATER REPLACEMENT | 0195 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0184EXT7 | EXTERIOR DOOR REPLACEMENT | 0184 | The existing exterior door to the Housing Unit 5 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0185EXT5 | EXTERIOR DOOR REPLACEMENT | 0185 | The existing exterior door to the Housing Unit 6 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0186EXT4 | EXTERIOR DOOR REPLACEMENT | 0186 | The existing exterior doors to the Recreation / Gym are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 5 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 7500
0187EXT5 | EXTERIOR DOOR REPLACEMENT | 0187 | The existing exterior door to the Housing Unit 7 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0188EXT4 | EXTERIOR DOOR REPLACEMENT | 0188 | The existing exterior doors to the Housing Unit 8 are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 10 doors was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0187SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0187 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 45225
0181EXT5 | EXTERIOR DOOR REPLACEMENT | 0181 | The existing exterior door to the Housing Unit 2 is original to the building. It is showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the door, replacement is recommended. This project would provide for the removal and disposal of the existing door and frame, and replacement with new exterior security door including door frame, hardware, security glazing, painting and connections to the security system as required. A total of 1 door was used to generate this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0179ADA5 | RESTROOM REMODEL | 0179 | The water closets and the lavatories in the three restrooms are worn from many years of use. It is recommended that all fixtures be replaced with new units. The new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 90000
0185INT4 | INTERIOR FINISHES | 0185 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
9994SIT4 | SITE DRAINAGE IMPROVEMENTS | 9994 | The buildings across the site have visible damage to the exterior walls and foundations from improper drainage. There are many areas where the grade does not slope away from the buildings allowing water to pool up against the walls. These areas show visible water damage to the stucco and will continue to cause damage. This project would create positive flow away from the buildings by regrading and installing French drains as needed. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0178EXT3 | EXTERIOR FINISHES | 0178 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0178INT4 | INTERIOR FINISHES | 0178 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0190ADA3 | ADA UPGRADES - DINING | 0190 | The building is lacking an accessible path of travel through the interior, the ramp in the Dining area is not compliant and there are no accessible dining tables installed. The building is used for serving inmates meals and is required to have accessible facilities per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible path of travel, ramp from the dining area to the service line and an accessible dining table in the building. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0178ADA4 | RESTROOM REMODEL | 0178 | The water closets and the lavatories in the three restrooms and the lavatory in the hallway are worn from many years of use and inactivity. It is recommended that all fixtures be replaced with new units. The new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 90000
0195ENR1 | LIGHTING UPGRADE | 0195 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed where appropriate for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0178PLM5 | WATER HEATER REPLACEMENT | 0178 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0195PLM3 | PLUMBING FIXTURES REPLACEMENT | 0195 | The existing water closet and sink are reaching the end of their expected life. They are worn and damaged from many years of use and should be scheduled for replacement. This project would provide for the installation of a new water closet and sink including all plumbing parts and connections. Removal and disposal of the old fixtures is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0179EXT3 | EXTERIOR FINISHES | 0179 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63500
0193SFT7 | PIPE BOLLARD INSTALLATION | 0193 | The Maintenance Shop has two sectional overhead doors. These areas are in need of bollards to protect the building. This project would provide funding for 4 eight inch diameter bollards to be located on each side of the sectional overhead doors at the exterior. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0193INT3 | INTERIOR FINISHES | 0193 | The interior finishes are in poor condition. It is recommended that the painted gypsum board interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 38500
0193EXT4 | EXTERIOR FINISHES | 0193 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 38500
0195INT3 | FLOORING REPLACEMENT | 0195 | The VCT (vinyl composite tile) flooring in the Guard Tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4032
0194INT3 | FLOORING REPLACEMENT | 0194 | The VCT (vinyl composite tile) flooring in the Guard Tower is damaged and has reached the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4032
0188EXT3 | EXTERIOR FINISHES | 0188 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 51500
0178EXT4 | EXTERIOR DOOR REPLACEMENT | 0178 | The existing exterior doors to the Education are original to the building. They are showing signs of wear and deterioration from constant use and inmate abuse. Due to security concerns and the condition of the doors, replacement is recommended. This project would provide for the removal and disposal of the existing doors and frames, and replacement with new exterior security doors including door frames, hardware, security glazing, painting and connections to the security system as required. A total of 5 doors was used to generate this estimate. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 7500
0180SEC1 | DOORS, LOCKS AND CONTROL PANEL REPLACEMENT | 0180 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0186HVA1 | HVAC REPLACEMENT | 0186 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 320000
0183HVA2 | HVAC REPLACEMENT | 0183 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0183SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0183 | There is no security camera or recording system in the Housing Unit 4 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0194SFT2 | FIRE ALARM INSTALLATION | 0194 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2304
0194PLM5 | PLUMBING REPLACEMENT | 0194 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 14400
0184HVA2 | HVAC REPLACEMENT | 0184 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0194ELE1 | ELECTRICAL UPGRADE | 0194 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 11520
0185HVA2 | HVAC REPLACEMENT | 0185 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0187HVA2 | HVAC REPLACEMENT | 0187 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 452250
0188HVA1 | HVAC REPLACEMENT | 0188 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128750
0176SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0176 | There is no security camera or recording system in the Administration/ Visitation Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 83650
0178SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0178 | There is no security camera or recording system in the Education Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 44450
0179SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0179 | There is no security camera or recording system in the Chapel/Law Library Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 44450
0182SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0182 | There is no security camera or recording system in the Housing Unit 3 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0184SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0184 | There is no security camera or recording system in the Housing Unit 5 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0195SFT2 | FIRE ALARM INSTALLATION | 0195 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2304
0186SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0186 | There is no security camera or recording system in the Recreation/Gym Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 89600
0178HVA1 | HVAC REPLACEMENT | 0178 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0185SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0185 | There is no security camera or recording system in the Housing Unit 6 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0181SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0181 | There is no security camera or recording system in the Housing Unit 2 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
0181ELE3 | ELECTRICAL UPGRADE | 0181 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0188PLM4 | PLUMBING REPLACEMENT | 0188 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 257500
0176ELE2 | ELECTRICAL UPGRADE | 0176 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 298750
0178ELE2 | ELECTRICAL UPGRADE | 0178 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 254000
0179ELE2 | ELECTRICAL UPGRADE | 0179 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 254000
0188ELE3 | ELECTRICAL UPGRADE | 0188 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 206000
0176HVA1 | HVAC REPLACEMENT | 0176 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 298750
0186PLM4 | PLUMBING REPLACEMENT | 0186 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128000
0179HVA1 | HVAC REPLACEMENT | 0179 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0181HVA2 | HVAC REPLACEMENT | 0181 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0182HVA2 | HVAC REPLACEMENT | 0182 | The Water Source Heat Pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new Water Source Heat Pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing Water Source Heat Pump units and all required connections to utilities. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 346250
0195PLM5 | PLUMBING REPLACEMENT | 0195 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 14400
0182ELE3 | ELECTRICAL UPGRADE | 0182 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0183ELE3 | ELECTRICAL UPGRADE | 0183 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0184ELE3 | ELECTRICAL UPGRADE | 0184 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0185ELE4 | ELECTRICAL UPGRADE | 0185 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 554000
0180PLM3 | PLUMBING REPLACEMENT | 0180 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0180SFT4 | FIRE ALARM REPLACEMENT | 0180 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. the current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0180SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0180 | There is no security camera or recording system in the Housing Unit 1 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96950
2567EXT4 | ROOF REPLACEMENT | 2567 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. | SALLY PORT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 81 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 972
0195ELE1 | ELECTRICAL UPGRADE | 0195 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 11520
0187SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0187 | There is no security camera or recording system in the Housing Unit 7 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 126630
0184SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0184 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0178PLM4 | PLUMBING REPLACEMENT | 0178 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0176PLM5 | PLUMBING REPLACEMENT | 0176 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 298750
0188PLM5 | PLUMBING FIXTURE REPLACEMENT | 0188 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing 10 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 75000
0188SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 0188 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 41200
0187SFT6 | FIRE ALARM SYSTEM REPLACEMENT | 0187 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 144720
0186SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0186 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 102400
0176EXT5 | EXTERIOR FINISHES | 0176 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 119500
0176INT4 | INTERIOR FINISHES | 0176 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted prior to occupancy. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in areas where water is present, such as the kitchen and bathrooms, for added durability. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 119500
0193ELE1 | ELECTRICAL UPGRADE | 0193 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 154000
0185SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0185 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0182PLM6 | PLUMBING REPLACEMENT | 0182 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0183SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0183 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0182SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0182 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. the current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0181SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0181 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 110800
0179SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0179 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50800
0178SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0178 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50800
0176SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 0176 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 95600
0187PLM7 | PLUMBING REPLACEMENT | 0187 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 904500
0177EXT2 | EXTERIOR FINISHES | 0177 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DOG KENNEL(VACANT) | 9994 | Correct | SNCC |  | Jean | 1987 | 156 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1560
0176PLM4 | WATER HEATER REPLACEMENT | 0176 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0192SFT8 | FIRE ALARM REPLACEMENT | 0192 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 40240
0190SEC1 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0190 | There is no security cameras or recording system in the Culinary/Dining/Central Plant building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 98000
0193SFT6 | FIRE ALARM SYSTEM REPLACEMENT | 0193 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30800
0190SFT5 | FIRE ALARM SYSTEM REPLACEMENT | 0190 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 112000
0190PLM4 | PLUMBING REPLACEMENT | 0190 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 700000
0190ELE2 | ELECTRICAL UPGRADE | 0190 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 560000
0190PLM3 | BOILER SYSTEM REPLACEMENT | 0190 | There are two hot water boilers servicing the prison. The life expectancy of these units is 20 to 25 years with proper water treatment programs and maintenance. Replacement parts for performing routine and/or emergency maintenance are difficult to locate due to the equipment’s age. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment, including all required connections to utilities and equipment. The existing chemical water treatment system will need to be tested and adjusted once the equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 500000
0191SFT5 | FIRE ALARM REPLACEMENT | 0191 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and no longer comply with current requirements. The current system is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 19200
0191PLM3 | PLUMBING REPLACEMENT | 0191 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 120000
0179PLM4 | PLUMBING REPLACEMENT | 0179 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 158750
0191HVA2 | HVAC REPLACEMENT | 0191 | There are two evaporative coolers installed on the roof of this building. They are severely scaled and have reached the end of their useful and expected life. This project would provide for two new evaporative coolers to be installed, and would include all required connections to the utilities. The estimate includes removal and disposal of the old evaporative coolers. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 60000
0181PLM6 | PLUMBING REPLACEMENT | 0181 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0192PLM4 | PLUMBING REPLACEMENT | 0192 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50300
0192ELE2 | ELECTRICAL UPGRADE | 0192 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 201200
0192HVA1 | HVAC REPLACEMENT | 0192 | There are two electric heaters installed in the Auto Maint Shop. They are in poor condition and have reached the end of their useful and expected life. This project would provide for two new electric heaters to be installed, and would include all required connections to the electrical. The estimate includes removal and disposal of the old electric heaters. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 125750
0193PLM4 | PLUMBING REPLACEMENT | 0193 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 38500
0193HVA2 | HVAC REPLACEMENT | 0193 | There are four electric heaters/air conditioning units installed in the Maintenance Shop. They are in poor condition and have reached the end of their useful and expected life. This project would provide for four new electric heaters/air conditioning units to be installed, and would include all required connections to the electrical. The estimate includes removal and disposal of the old heating/air conditioning units. The water source heat pumps in this building are also being recommended for replacement. These heat pumps are not energy efficient, and have reached the end of their expected and useful life. This project would provide for installation of new water source heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing water source heat pump units and all required connections to utilities. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96250
0185PLM5 | PLUMBING REPLACEMENT | 0185 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0184PLM6 | PLUMBING REPLACEMENT | 0184 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0183PLM5 | PLUMBING REPLACEMENT | 0183 | The sanitary wastewater and copper plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The copper lines have rusted and there are pin holes throughout the system. The lines are original to the site and are in poor condition. The hard water is also a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and has slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and copper piping system. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 692500
0188SEC2 | SECURITY SURVEILLANCE SYSTEM INSTALLATION | 0188 | There is no security camera or recording system in the Medical Unit 8 Building. This is a safety issue for the staff and inmates as all areas cannot be seen by the security staff or recorded in case of an incident. This project would provide for the installation of surveillance cameras and a security system for the entire building and all required connections to existing utility systems. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 36050
0191ELE1 | ELECTRICAL UPGRADE | 0191 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. The current wiring in the building is #14 and does not meet the current demand. #14 wiring is also against State Public Works Division's Adopted Standards, 8.5.4, for lighting and power circuits. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 96000
0179PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0179 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0187EXT3 | ROOF REPLACEMENT | 0187 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 217080
0187INT4 | LIGHTING UPGRADE | 0187 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 81405
0190INT2 | LIGHTING UPGRADE | 0190 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 63000
0185INT3 | LIGHTING UPGRADE | 0185 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0184INT3 | LIGHTING UPGRADE | 0184 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0179INT3 | LIGHTING UPGRADE | 0179 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 28575
0179INT2 | CARPET/ TILE REPLACEMENT | 0179 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 1-2 years. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 88900
0188ENR1 | LIGHTING UPGRADE | 0188 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 23175
0191INT2 | LIGHTING UPGRADE | 0191 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10800
0183INT3 | LIGHTING UPGRADE | 0183 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0182INT3 | LIGHTING UPGRADE | 0182 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0181INT3 | LIGHTING UPGRADE | 0181 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0180ENR1 | LIGHTING UPGRADE | 0180 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 62325
0179ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0179 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0179EXT2 | ROOF REPLACEMENT | 0179 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 76200
0179SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0179 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15875
0179ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0179 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0185ADA4 | ADA SIGNAGE | 0185 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0179ADA2 | ADA SIGNAGE | 0179 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0183EXT6 | EXTERIOR FINISHES | 0183 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0176ADA6 | RESTROOM REMODELS | 0176 | The water closets and the lavatories in the six restrooms throughout the building are worn from many years of use and being idle due to multiple closures. It is recommended that all fixtures be replaced with new units. The new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0176ADA4 | ADA SIGNAGE | 0176 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria and is confusing for public access to visitation. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0187ADA5 | ADA SIGNAGE | 0187 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0179SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0179 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CHAPEL/ LAW LIBRARY(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 88900
0188ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0188 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0187INT1 | REPAIR ELEVATOR | 0187 | This building has an elevator, but it has been out of service for some time, and it does not comply with ADA standards. This project would provide funding to repair the elevator to improve maintenance, facilitate control of this building and comply with the ICC/ANSI A117.2009 Section 407. These repairs are to include but not limited to updating the control panel, door reversing light beams, call button, hall station upgrades, and a hands-free telephone. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 80000
0190SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0190 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 35000
0190ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0190 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0191SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0191 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0191ADA2 | ADA RESTROOM UPGRADE | 0191 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirror, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0190ADA4 | RESTROOM REMODEL | 0190 | The water closets and the lavatories in the five restrooms throughout the building are worn from many years of use and being idle due to multiple closures. It is recommended that all fixtures be replaced with new units. At least two of the new units and restroom layouts are also required to comply with ADA requirements. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 150000
0188PLM1 | 2" BACKFLOW ASSEMBLY | 0188 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0186INT1 | INTERIOR FINISHES | 0186 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 128000
0186ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0186 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0190ADA1 | ADA SIGNAGE | 0190 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0188SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0188 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 12875
0186ADA1 | ADA SIGNAGE | 0186 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0188ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0188 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0188ADA3 | ADA SIGNAGE | 0188 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0188ELE2 | ROOFTOP SECURITY LIGHT REMOVAL | 0188 | The building has roof-mounted security lights that have been superseded by the installation of a high-mast security lighting system. This project will provide funding for the removal of the fixtures, conduit and associated wiring removed back to the panel. This will free up capacity for other electrical needs in the buildings. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0192SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0192 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 12575
0193SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0193 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 9625
0193INT1 | STRUCTURAL ASSESSMENT | 0193 | A second floor area was added to this building accessed via two different wooden staircases. There is no record of a CIP project for this work or of any structural evaluations having been conducted. This project recommends that a licensed engineer perform a structural investigation to assess the load bearing capacity of the structure. Future projects would be based on this report. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0176SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0176 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 95600
0185EXT6 | EXTERIOR FINISHES | 0185 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0190EXT3 | ROOF REPLACEMENT | 0190 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 168000
0183PLM1 | PLUMBING FIXTURE REPLACEMENT | 0183 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0186ADA4 | LEVER ACTION HARDWARE INSTALLATION | 0186 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0176ADA2 | TDD INSTALLATION | 0176 | The visitation area is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in the non-contact visitation area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 20000
0186ENR1 | LIGHTING UPGRADE | 0186 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 57600
0186SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0186 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 32000
0186PLM1 | 2" BACKFLOW ASSEMBLY | 0186 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0190PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0190 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0191PLM1 | 2" BACKFLOW ASSEMBLY | 0191 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0192PLM1 | 2" BACKFLOW ASSEMBLY | 0192 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0193PLM1 | 2" BACKFLOW ASSEMBLY | 0193 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0194PLM1 | 2" BACKFLOW ASSEMBLY | 0194 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0195PLM1 | 2" BACKFLOW ASSEMBLY | 0195 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0190INT1 | INTERIOR FINISHES | 0190 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 140000
0176ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0176 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0190SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION/ UPGRADE | 0190 | The building has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention for the areas not currently sprinklered in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | CULINARY/ DINING/ CENTRAL PLANT(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 14000 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 196000
0176ADA3 | LEVER ACTION HARDWARE INSTALLATION | 0176 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 12000
0186SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0186 | The building has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 179200
0195HVA1 | HVAC REPLACEMENT | 0195 | The building is conditioned by one wall-mounted heat pump. It is reaching the end of its useful and expected life. This project would provide for a new heat pump to be installed including all required connections to utilities. The estimate includes removal and disposal of the old heat pump. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0194HVA1 | HVAC REPLACEMENT | 0194 | The building is conditioned by one wall-mounted heat pump. It is reaching the end of its useful and expected life. This project would provide for a new heat pump to be installed including all required connections to utilities. The estimate includes removal and disposal of the old heat pump. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0195EXT1 | ROOF REPLACEMENT | 0195 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Interior ceiling stains and exterior soffit stains indicate that there are active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3456
0194EXT3 | ROOF REPLACEMENT | 0194 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Interior ceiling stains and exterior soffit stains indicate that there are active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3456
0191EXT2 | ROOF REPLACEMENT | 0191 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 28800
0188EXT2 | ROOF REPLACEMENT | 0188 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MEDICAL UNIT 8(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 5150 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 61800
0178ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0178 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0178SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0178 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15875
0176SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0176 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 29875
0178SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0178 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50800
0180PLM2 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0180 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0181PLM2 | 2" BACKFLOW ASSEMBLY | 0181 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0182PLM2 | 2" BACKFLOW ASSEMBLY | 0182 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0178PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0178 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0176PLM1 | 2" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0176 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0187INT3 | INTERIOR FINISHES | 0187 | The interior finishes are in poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 180900
0182SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0182 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0183SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0183 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0184SEC1 | CONTROL PANEL DOORS AND LOCKS REPLACEMENT | 0184 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0185SEC1 | CONTROL PANEL, DOORS AND LOCKS REPLACEMENT | 0185 | Problems exist with the door control panel and door locks for the cells. The panel and locks are original equipment and should be scheduled for replacement. Buttons on the panel do not work or get stuck frequently and the door locks are not consistently responsive to the panel. Repairs to the control panel and locks are difficult because replacement parts are no longer being manufactured for the units. Improper operation will cause security risks to the staff and inmates. It is recommended that the door control panel and 56 door locks be replaced. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 840000
0180SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0180 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0181SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0181 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0187PLM4 | 2" BACKFLOW ASSEMBLY | 0187 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0184SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0184 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0183SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0183 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0181EXT6 | EXTERIOR FINISHES | 0181 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0182EXT6 | EXTERIOR FINISHES | 0182 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0184EXT6 | EXTERIOR FINISHES | 0184 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 138500
0178INT3 | LIGHTING UPGRADE | 0178 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 28575
0176ENR1 | LIGHTING UPGRADE | 0176 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 53775
0187ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0187 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0178EXT2 | ROOF REPLACEMENT | 0178 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 76200
0178ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0178 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0178ADA2 | ADA SIGNAGE | 0178 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | EDUCATION A(VACANT) | 9994 | Correct | SNCC |  | Jean | 1979 | 6350 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0176EXT2 | REPLACE WINDOWS | 0176 | The steel framed window assemblies are damaged from exposure and age and the frames and stops should be scheduled for replacement. They are located in the Visitation room and near the employee entrance to the Warden's Office. The frames and glazing stops are rusting and approaching failure due to water infiltration at joints, adjacency to grade and expansion and contraction over time. The heat and exposure to the sun have warped and bent the frames and glazing stops beyond repair. This project will include removal and disposal of the existing frame assembly and replacement with new steel frames and glazing stops. Reinstallation of the existing glazing panels is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 139200
0183PLM3 | 2" BACKFLOW ASSEMBLY | 0183 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0184PLM2 | 2" BACKFLOW ASSEMBLY | 0184 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016.. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0185PLM2 | 2" BACKFLOW ASSEMBLY | 0185 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0182SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0182 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0185SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0185 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 Lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 34625
0184EXT4 | ROOF REPLACEMENT | 0184 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0193INT2 | JANITORS CLOSET REPAIRS | 0193 | The mop sinks in the Janitor Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitor Closets. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 5600
0193ADA1 | LEVER ACTION HARDWARE INSTALLATION | 0193 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0193EXT1 | ROOF REPLACEMENT | 0193 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 46200
0185EXT4 | ROOF REPLACEMENT | 0185 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0192SFT4 | VEHICLE EXHAUST EXTRACTION SYSTEM | 0192 | The Auto Maintenance Shop has no exhaust extraction system to remove toxic exhaust fumes. In enclosed areas where motor vehicles operate, mechanical ventilation shall be provided per the 2012 IBC 406.6.3 and UMC 502.14. This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by manufacturer. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 50000
0182EXT4 | ROOF REPLACEMENT | 0182 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0192ELE1 | LIGHTING UPGRADE | 0192 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 22635
0183EXT4 | ROOF REPLACEMENT | 0183 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0192EXT2 | OVERHEAD COILING DOOR REPLACEMENT | 0192 | There is a 10'x14' overhead coiling door which is damaged and does not function properly. Exposure and wind have caused the door to bend, crack and lose the finish. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with new manually operated overhead coiling door. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 10000
0181EXT4 | ROOF REPLACEMENT | 0181 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0180EXT4 | ROOF REPLACEMENT | 0180 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 166200
0193EXT3 | OVERHEAD COILING DOOR REPLACEMENT | 0193 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 20000
0186EXT3 | ROOF REPLACEMENT | 0186 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | RECREATION/ GYM(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 12800 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 153600
0187PLM5 | WATER HEATER REPLACEMENT | 0187 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 7(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 18090 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
9994ELE2 | TRANSFORMER AND DISTRIBUTION PANELS SERVICE | 9994 | Southern Nevada Correctional Center opened in 1978. There is evidence of deterioration on the transformer cabinets and main distribution panels site wide. There are no records of inspection or servicing of these electrical items. It is highly recommended that these items be serviced on an annual basis. This project would provide for a photo infrared inspection and servicing of all the transformer and main distribution panels. Other projects may be developed from the results of the inspections. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0185PLM4 | WATER HEATER REPLACEMENT | 0185 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 6(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0184PLM4 | WATER HEATER REPLACEMENT | 0184 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0183PLM4 | WATER HEATER REPLACEMENT | 0183 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0192EXT1 | ROOF REPLACEMENT | 0192 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 60360
0192ADA2 | LEVER ACTION HARDWARE INSTALLATION | 0192 | Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed in this building to meet these guidelines. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | AUTO MAINT SHOP/ WAREHOUSE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 5030 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 3000
0191HVA1 | STEAM BOILER REPLACEMENT | 0191 | The steam boiler that powers the laundry equipment has been removed for use at an occupied facility. This project would provide for the installation of a new electric steam boiler including all required connections to utilities and equipment. The estimate is based on a 518 KW electric steam boiler. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of chemical water treatment system. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | LAUNDRY & DRY CLEANING(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 2400 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 85000
0180PLM4 | WATER HEATER REPLACEMENT | 0180 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0181PLM4 | WATER HEATER REPLACEMENT | 0181 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0176EXT4 | ROOF REPLACEMENT | 0176 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended to replace the singly-ply membrane and repair the Cor-ten roofing system as needed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 05/04/1998, 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | ADMINISTRATION/ VISITATION(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 11950 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 143400
0183EXT5 | WINDOW WEATHER-STRIPPING REPLACEMENT | 0183 | The exterior glazing currently has metal window stops and weather-stripping that is rusted, damaged and is in need of replacement, especially at the main entrance to the housing unit at grade level. This project would provide for the removal and replacement of the window stops and weather-stripping. This estimate includes painting to match existing conditions. This project or a portion there of was previously recommended in the FCA report dated 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 4(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 9600
0180PLM5 | PLUMBING FIXTURE REPLACEMENT | 0180 | The plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 100 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional costs would be incurred for relocating plumbing. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0181PLM5 | PLUMBING FIXTURE REPLACEMENT | 0181 | The plumbing fixtures in the cells are a mix of porcelain and stainless steel wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0182PLM5 | PLUMBING FIXTURE REPLACEMENT | 0182 | The plumbing fixtures in the cells are a mix of porcelain and stainless steel wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0193ENR1 | LIGHTING UPGRADE | 0193 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 17325
0184PLM5 | PLUMBING FIXTURE REPLACEMENT | 0184 | Approximately half of the plumbing fixtures in the cells are separate porcelain wall hung lavatories and water closets. These units are in poor condition and should be replaced with stainless steel fixtures designed for correctional facilities. This project would provide for the removal and replacement of the old porcelain plumbing fixtures with new stainless steel fixtures. The estimate is based on installing a 50 separate water closets and sinks in the same place as the existing porcelain fixtures. If combination style units are feasible to install, there may be a cost savings on the materials, but additional work to install. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 5(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 375000
0193SFT4 | EMERGENCY EYE WASH STATION | 0193 | The building has outdated containers of eye wash solution. Where the eyes or body of any person may be exposed to injurious corrosive materials, suitable facilities for quick drenching or flushing of the eyes and body shall be provided within the work area for immediate emergency use, reference OSHA 1910.151(c). This project would provide funding for the purchase and installation of an emergency eye and body wash station. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 6000
0182PLM4 | WATER HEATER REPLACEMENT | 0182 | There are two 120 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | HOUSING UNIT 3(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 | 13850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0193HVA1 | EXHAUST FAN INSTALLATION - WELDING AREA | 0193 | The building has a welding area. Depending on what type of material is being welded, it may require a local hood and ventilation system. This project would provide funding for the engineering, exhaust fan, ducting, electrical connections, installation and repairs to the roof as required. OSHA 1910.252(3) was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | MAINTENANCE SHOP(VACANT) | 9994 | Correct | SNCC |  | Jean | 1978 | 3850 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 15000
9994SIT2 | ASPHALT CONCRETE REPLACEMENT | 9994 | The access road and the parking area around the Maintenance and Auto Shop area is in poor condition and has significant alligatoring and large cracks. The paving has deteriorated to the point that it is no longer viable to re-seal. This project would provide for the removal and disposal of the existing A.C. paving and installation of 80,000 square feet of A.C. paving over a compacted sub-base. This estimate includes striping for parking areas and safety zones and excludes the main public / employee parking area. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | SOUTHERN NV CORRECT CTR SITE(VACANT) | 9994 | Correct | SNCC |  | Jean | 1976 |  | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 400000
0194SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0194 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 1(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0195SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0195 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10, 1011.6.2 exit sign illumination 5 foot candles (54 lux), was referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/21/2006 and 04/26/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/08/2016. | GUARD TOWER 2(VACANT) | 9994 | Correct | SNCC |  | Jean | 1982 | 288 | 2016-03-08 | Immediate to Two Years | Currently Critical | 1 | 2000