## Sheet 1
State of Nevada
Active Project List
State Public Works Division
Facility Condition Analysis
August 1, 2019
This is a living document. As projects are verified as completed, they could be removed from the report. As projects are recommended, they could be added to the report. This report is effective as of the date listed above.
Project Number | Project Title | FCA Building Number | Project Description | Building Name | Site Number | Department | Division | Agency | City | Year Built | Square Feet | Survey Date | Priority Class Description | Priority Class Description2 | Priority Class Code | Construction Cost
3761EXT3 | ROOF REPLACEMENT | 3761 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | LAKEVIEW METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 200 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 2400
3762EXT2 | GUARDRAIL | 3762 | The NFPA 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an AWWA D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | LAKEVIEW WATER TANK | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 205 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 12000
3031SIT1 | SITE DRAINAGE UPGRADES | 3031 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3, Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3031EXT1 | EXTERIOR FINISHES | 3031 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 9520
3760EXT1 | EXTERIOR FINISHES | 3760 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior fencing, privacy slats, fence posts and hardware. This project would provide funding to protect the exterior of the building excluding the roof. It is recommended that this project be implemented in the next 4-5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAKEVIEW PROPANE STORAGE BLDG | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 40 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 80
3761SFT1 | EXTERIOR LANDING INSTALLATION | 3761 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing that complies with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | LAKEVIEW METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 200 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3765EXT1 | EXTERIOR FINISHES | 3765 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOBART METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2007 | 48 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 480
3762INT1 | INTERIOR FINISHES | 3762 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | LAKEVIEW WATER TANK | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 205 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3763SFT1 | EXTERIOR LANDING INSTALLATION | 3763 | There is an out-swinging exterior door from the building that swings out over a step and does not have a landing that complies with IBC 2012. IBC Section 1008 which requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | DIVERSION DAM METER BLDG | 9788 | Admin | PubWorks | B&G | Carson City | 2007 | 72 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3761EXT2 | EXTERIOR FINISHES | 3761 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit and T1-11 walls, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAKEVIEW METER BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 200 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 2000
9788SIT1 | FENCING INSTALLATION | 9788 | The Marlette Lake Water System Site has several buildings, abandoned water ways, and many areas where the general public use the area for hiking, biking, and other outdoor activities. This site requires a higher level of security for the safety of the general public and also to protect the drinking water supply. This project would provide for permanent chain link fencing to surround the high security buildings to protect the drinking water supply. Additional chain link fencing is needed for the general public’s safety to protect them from areas where safety is a concern. This project would provide 1000 LF of chain link fencing throughout the site at $35 per LF. | MARLETTE LAKE WATER SYSTEM SITE | 9788 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
9788SFT1 | WALKING SURFACES/ GUARDRAILS | 9788 | The Marlette Lake Water System Site has several dams, uneven walking surfaces and wet locations that don’t have the proper slip resistant platform walking surfaces required by OSHA 1910.22(a)(2), Where wet processes are used, drainage shall be maintained and false floors, platforms, mats, or other dry standing places should be provided where practicable. There are several locations where it is required for employees to access dams, buildings and other locations where there is possible risk of falling into pits, dams and ditches. Per OSHA 1910.22(c), covers and/or guardrails shall be provided to protect personnel from the hazards of open pits, tanks, vats, ditches, etc. This project will provide funding for OSHA required nonslip platforms and railings to be installed across dams, ditches, and uneven surfacing throughout the site where necessary. | MARLETTE LAKE WATER SYSTEM SITE | 9788 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 25000
3762EXT1 | EXTERIOR FINISHES | 3762 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 4-5 years. An additional recommendation is to conduct inspections and testing on a cyclical basis based per NAC 445. | LAKEVIEW WATER TANK | 9788 | Admin | PubWorks | B&G | Carson City | 1987 | 205 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 2050
3763EXT1 | EXTERIOR FINISHES | 3763 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DIVERSION DAM METER BLDG | 9788 | Admin | PubWorks | B&G | Carson City | 2007 | 72 | 2016-09-13 | Four to Ten Years | Long-Term Needs | 3 | 720
3031HVA1 | HEATER REPLACEMENT | 3031 | The building currently has open combustion air for the generator. The combustion air is located on the side wall and on the ceiling. When the heater runs in the building the heat rises and escapes through the combustion air on the ceiling. This makes the building very unpleasant to work in when the weather is cold. This project would remove the existing heater and provide for the installation of two suspended radiant heaters. The estimate includes two radiant heaters, seismic supports and connections to all the utilities. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3031ENV1 | SPILL CONTAINMENT | 3031 | The building does not have a method for containing spills or leakage from drums. This project would add secondary containment pallets for all containers in the building and install placards on the building’s exterior. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 6500
3031SFT1 | BATTERY STORAGE | 3031 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. Batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced and a smoke alarm. This project will provide funding for the requirements of Section 608 of the 2012 IFC proper way to store, charge and/or use batteries indoors. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 25000
3031INT1 | INTERIOR FINISHES | 3031 | It is recommended to repair and seal the interior concrete block walls at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9520
3031SFT2 | EXIT SIGN AND EGRESS LIGHTING | 3031 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 4760
3031SIT2 | GENERATOR MAINTENANCE | 3031 | Preventative maintenance for generators plays a critical role in maximizing reliability, minimizing repairs, reducing long term costs and prolonging the life expectancy of generators. This project would provide for a licensed contractor to perform the preventive maintenance on the generator that is required from the manufacturer specifications. | GENERATOR BUILDING | 9788 | Admin | PubWorks | B&G | Carson City | 2009 | 952 | 2016-09-13 | Immediate to Two Years | Currently Critical | 1 | 10000
9790ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9790 | There is one existing light pole at the site. With increased traffic and development in the area, insufficient site lighting is a security and safety concern. This project would provide for the installation of 8 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. The existing pole may be acceptable to re-use. If so, the estimate can be reduced accordingly. | FLEET SERVICES - LAS VEGAS SITE | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 |  | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
9790ADA1 | ADA UPGRADES | 9790 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A compliant path of travel from the accessible parking spaces and from the public right of way to the entrance are necessary to comply with ADA accessibility requirements. The current path from the parking spaces is not in compliance due to a curb ramp that is too small and the downspout protruding into the path. There is also no path from the public right of way. This project would provide for complaint concrete walkways and curb ramps. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | FLEET SERVICES - LAS VEGAS SITE | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 |  | 2015-03-18 | Immediate to Two Years | Currently Critical | 1 | 25000
3155EXT2 | EXTERIOR FINISH REPAIRS | 3155 | The exterior of the building is covered by an Exterior Insulation Finishing System (EIFS). There are at least 3 large cracks in the EIFS that should be repaired in order to maintain a waterproof envelope around the building. This project would provide funding to repair the cracks and bring the finish back to its original condition. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3155HVA1 | HEATING UPGRADE | 3155 | The electric heater in the garage is broken and the wash bay does not currently have any heating equipment. The garage is uncomfortably cold in the winter and the wash bay cannot be used in cold temperatures. It is recommended to install heating equipment in these areas to ensure a comfortable work environment and an operational wash bay. This project would provide for the purchase and installation of three electric heaters including all required connections to existing utilities. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3155INT2 | CARPET REPLACEMENT | 3155 | The carpet in the Conference Room is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
3155INT1 | INTERIOR FINISHES | 3155 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20425
3155ENR1 | EXTERIOR LIGHTING UPGRADE | 3155 | There are 12 wall pack lighting fixtures mounted on the exterior of the building. These light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the 12 exterior lighting fixtures with new LED light fixtures, using existing wiring. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
9790SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9790 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 35,000 square feet of asphalt area was used to generate this estimate. | FLEET SERVICES - LAS VEGAS SITE | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 |  | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
3155EXT1 | EXTERIOR FINISHES | 3155 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FLEET SERVICES OFFICE - LAS VEGAS | 9790 | Admin | PubWorks | B&G | Las Vegas | 2007 | 4085 | 2015-03-18 | Four to Ten Years | Long-Term Needs | 3 | 20425
3113SFT2 | FIRE ALARM REPAIRS | 3113 | This building is equipped with an automatic fire detection and alarm system that needs to be inspected and cleaned before occupancy. This project would provide for a complete system inspection by a qualified inspector, cleaning of the smoke and heat detectors and replacement of 5 detectors. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 3000
9793ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9793 | There are four existing light poles in the parking lot. They are the older metal halide type fixtures and are not energy efficient. This project would provide for the purchase and installation of 4 solar powered LED exterior light fixtures on the existing poles. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
3113ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 3113 | This building contains a water fountain near the main entrance. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 4000
3113ADA1 | ADA SIGNAGE | 3113 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 1500
9793SIT2 | LANDSCAPING AND IRRIGATION UPGRADE | 9793 | The existing landscaping consists of a few plantings, rocks, dirt and old irrigation lines. These features have reached the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing plantings and irrigation lines and the purchase and installation of new plants, irrigation lines and hardscape features. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Four to Ten Years | Long-Term Needs | 3 | 7500
9793SFT1 | EXTERIOR OUTLET REPLACEMENT | 9793 | There is an electrical outlet on the exterior of the building near the front entrance that does not meet code. This outlet should be changed to a GFCI type outlet per the 2005 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof cover. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
9793ENV1 | ABANDON FUEL TANK MONITORING SYSTEM | 9793 | An underground fuel storage tank was removed in 1993 and minor contamination was discovered. The contamination was remediated but an electronic monitoring system and passive venting system were installed and are still in place. The systems were never properly abandoned after the issuance of the closure letter by the Clark County Health District. This project would provide for abandoning the systems including the passive venting system and the monitoring wells. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
9793ADA1 | ADA PARKING SPACES AND PATH OF TRAVEL | 9793 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. Concrete parking spaces, a passenger loading area and path of travel to the accessible entrance are necessary to comply with ADA accessibility requirements. This project would provide for two ADA parking spaces including a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project should be implemented concurrently with the ACCESSIBLE ENTRANCE MODIFICATIONS project. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 25000
9793SIT1 | SLURRY SEAL ASPHALT PAVING | 9793 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site-wide including the access road and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 75,000 square feet of asphalt area was used to generate this estimate. | AGRICULTURE LAS VEGAS SITE | 9793 | Agricult | Agri |  | Las Vegas | 1978 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56250
3113INT3 | JANITOR'S CLOSET REPAIRS | 3113 | The mop sink in the Janitor's Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 1400
3113SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 3113 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This estimate is based on a $9.00/SF for sprinkler installation and a lump sum of $20,000 for connection to water supply including backflow prevention. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 165386
3113ADA3 | ADA RESTROOM UPGRADE | 3113 | The building does not have fully compliant ADA accessible restrooms. The existing restrooms do not meet all of the Americans with Disabilities Act (ADA) requirements. A complete retrofit may be necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 30000
3113HVA1 | REPLACE COOLING MEDIA | 3113 | There are 4 roof mounted evaporative cooling units on the warehouse roof which are missing the cooling media. This project would provide for new cooling media to be installed. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 2000
3113PLM3 | WATER HEATER / ROOF ACCESS MODIFICATIONS | 3113 | The existing gas fired water heater appears to not have proper combustion air and is larger that needed. The closet where it is located used to contain the roof access ladder which has been modified and no longer is usable. This project would provide for the removal of the gas fired water heater, installation of a gas fired tankless water heater and a new roof access ladder including all required gypsum board repairs and painting. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 9500
3113ENR2 | EXTERIOR INSULATION & FINISH SYSTEM | 3113 | The building is constructed with exterior unisulated CMU / slumpstone masonry and does not meet today's energy code requirements. This project would provide for the installation of an exterior insulation and finish system (EIFS) over the exterior walls. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105001
3113INT4 | CEILING TILE REPLACEMENT | 3113 | There are several areas of stained and / or damaged ceiling tiles in the building. This project would provide for the replacement of stained or missing tiles throughout the building. It is recommended that this project be executed after the roof is replaced. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3113ADA4 | ACCESSIBLE ENTRANCE MODIFICATIONS | 3113 | The current entrance to the building is on the north elevation and is not ADA compliant. There were no accessible entrances to the building at the time of the survey. The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. In order to comply with the ADA, it is recommended to modify the building and site to provide a compliant entrance from the ADA parking spaces and from the public right of way. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project should be implemented concurrently with the ADA PARKING SPACES AND PATH OF TRAVEL project. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 100000
3113ENR1 | LIGHTING UPGRADE | 3113 | The existing lighting fixtures in the warehouse are the older T-12 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed for additional savings. Any electrical wiring upgrades are not included in this estimate. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9750
3113INT1 | INTERIOR FINISHES | 3113 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80770
3113EXT2 | ROOF REPLACEMENT | 3113 | The roof on this building was in poor to fair condition at the time of the survey. The roof is probably original to the building dating back to the late 1970's. The built-up roofing system has had at least one coating applied over the top and there is evidence of past leaks. Natural gas lines are supported by damaged wood members and the HVAC units are not on proper curbs. The flat roof has signs of cracking and the sealant is in poor condition. The clay tile areas have broken tiles throughout and mastic repairs around vents and roof scuppers. Numerous apparent leaks were observed on the interior ceiling. It is recommended that this building be re-roofed in the next 1-2 years to prevent further damage to the building. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 193848
3113INT2 | CARPET REPLACEMENT | 3113 | The carpet in the warehouse offices is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. 1,000 square feet of floor area was used to generate this estimate. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
3113EXT1 | EXTERIOR FINISHES | 3113 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the brick masonry and stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | AGRICULTURE LAS VEGAS | 9793 | Agricult | Agri |  | Las Vegas | 1978 | 16154 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80770
2790PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2790 | The existing water softening/ treatment systems in the building are currently not operational or are ineffective. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. A significant amount of scaling was observed on the cooling towers indicating a problem with the water treatment system. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2790PLM1 | WATER HEATER REPLACEMENT | 2790 | There is a 100 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2790SIT1 | CARPORT STRUCTURE INSTALLATION | 2790 | There is a need for a carport structure on the top floor of the parking garage. The employee vehicles are exposed to the sun and the carport could provide solar power to the building. This project would provide for the purchase and installation of a 60' x 250' steel carport structure on the top floor of the parking garage with a photovoltaic system including solar panels, deep cycle solar batteries and all associated electrical boxes and hardware to connect it to the electrical system. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500000
2790INT1 | INTERIOR FINISHES | 2790 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 424070
9794SIT1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9794 | There are approximately 10 existing light poles around the site with metal halide fixtures. The older fixtures are not energy efficient and are due for an upgrade to a higher efficiency unit with a longer life cycle. This project would provide for the installation of 10 solar powered LED exterior light fixtures on the existing poles. | CAMPOS OFFICE & PARKING COMPLEX SITE | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 |  | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2790EXT1 | EXTERIOR FINISHES | 2790 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPOS OFFICE & PARKING COMPLEX | 9794 | Admin | PubWorks | B&G | Las Vegas | 2009 | 188061 | 2015-03-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 376122
0891EXT1 | EXTERIOR FINISHES | 0891 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is replacing damaged metal panels, removing dirt around building to below the finish floor elevation and sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0893EXT2 | EXTERIOR DOOR REPLACEMENT | 0893 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0893EXT3 | OVERHEAD DOOR REPLACEMENT | 0893 | There is an 10'x8' overhead coiling door on the North side of the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. Removal and disposal of the existing door is included in this estimate. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0890INT1 | INTERIOR FINISHES | 0890 | The interior finishes are in poor condition. It is recommended that the damaged interior gypsum board walls and ceilings be removed and replaced and painted in the next two to four years. Prior to painting, all remaining existing surfaces should be repaired and prepped. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0893SFT2 | FIRE EXTINGUISHER INSTALLATION | 0893 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 1000
0891INT1 | INTERIOR FINISHES | 0891 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0891SFT1 | FIRE EXTINGUISHER INSTALLATION | 0891 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 1000
2343EXT1 | EXTERIOR FINISHES | 2343 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is priming and painting to repair the graffiti damage and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY SEED BANK | 9795 | CNR | Forestry |  | Washoe Valley | 1995 | 1450 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7250
0894EXT2 | WINDOW REPLACEMENT | 0894 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0893SFT1 | EXTERIOR LANDING INSTALLATION | 0893 | There is an out-swinging exterior door which swings out over dirt and does not have a landing. This does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the landing not be less than 1/2" below the threshold. This project addresses installing a landing designed to current code. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 500
0893EXT1 | EXTERIOR FINISHES | 0893 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is replacing damaged metal panels, removing dirt around building to below the finish floor elevation and sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be repaired, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY SEED/REFRIGERATOR BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1984 | 600 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0894HVA1 | HVAC EQUIPMENT INSTALLATION | 0894 | The building is currently used year round and does not have any source of heating or cooling. This project would provide for installation of a new HVAC system including heating and cooling. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0890SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0890 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 9800
0894ENR1 | LIGHTING UPGRADE | 0894 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0889SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0889 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 2000
0894INT1 | INTERIOR FINISHES | 0894 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0894EXT1 | EXTERIOR FINISHES | 0894 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
2340EXT1 | EXTERIOR FINISHES | 2340 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior membrane and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NURSERY GREENHOUSE #2 (WEST) | 9795 | CNR | Forestry |  | Washoe Valley | 2002 | 3000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 30000
2341EXT1 | EXTERIOR FINISHES | 2341 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY LATH HOUSE (NORTH) | 9795 | CNR | Forestry |  | Washoe Valley | 2006 | 9000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 18000
2342EXT1 | EXTERIOR FINISHES | 2342 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining the wood and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY LATH HOUSE (SOUTH) | 9795 | CNR | Forestry |  | Washoe Valley | 2006 | 9000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 12000
0894SFT3 | EXTERIOR LANDING INSTALLATION | 0894 | The exterior door from the Shop does not have a code compliant landing. The landing does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the landing not be less than 1/2" below the threshold. This project addresses installing a landing designed to current code. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 1000
0889SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0889 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 10500
9795SFT2 | WATER LINE / FIRE PROTECTION | 9795 | This project would provide for a fire sprinkler supply line to be installed to the public water system if fire sprinklers were to be installed at the site This project also includes 1,000 lineal feet of 6" water main to tie into the existing public water system. Backflow prevention is included in this estimate. The public water system location will need to be verified if this project were to be implemented. | WESTERN REGION NDF NURSERY | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 100000
0894SFT1 | INSTALL SMOKE DETECTOR | 0894 | The building does not have any smoke detectors. Chapter 9 of the 2006 IBC and IFC require smoke detectors to be installed. This project would provide for the installation of electric smoke detectors with a battery backup. | NURSERY SHOP | 9795 | CNR | Forestry |  | Washoe Valley | 1978 | 480 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 500
0891EXT2 | REPLACE CONCRETE APRONS / LANDINGS | 0891 | The concrete landings and aprons at the exterior doors are damaged, cracking and present a tripping hazard. This project would provide for the removal of the existing concrete and installation of new 4 inch thick concrete landings and aprons. 200 square feet of concrete was used to generate this estimate. | NURSERY PLANTING BUILDING | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 900 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0889EXT2 | REPLACE ROOF | 0889 | The existing composition roofing system is damaged, has missing shingles and leaks. This project would provide for the replacement of the roof with a standing seam metal roofing system including underlayments. Removal of the existing roofing system is included in this estimate. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 27250
0888EXT1 | EXTERIOR FINISHES | 0888 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior membrane and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY GREENHOUSE #1 (EAST) | 9795 | CNR | Forestry |  | Washoe Valley | 1979 | 3000 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 6000
0889INT3 | VCT FLOORING REPLACEMENT | 0889 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. The restroom flooring is addressed in another project. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0889PLM1 | WATER HEATER REPLACEMENT | 0889 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0889INT2 | RESTROOM REMODEL | 0889 | The restroom in the building is in poor condition and is due for a complete remodel. This project would provide for a complete remodel including the restroom fixtures, hardware, floor and wall finishes. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0889SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0889 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 500
0889ADA1 | ADA UPGRADES | 0889 | The access into the building, entrance door, signage and information counter are not ADA compliant. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp and compliant stairs and handrails to access the building. This project should be coordinated with the ADA parking site project. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances and route of travel inside the building. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 30000
0890EXT1 | EXTERIOR FINISHES | 0890 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 1400
0890SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0890 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 2800
2343EXT3 | EXTERIOR LANDING INSTALLATION | 2343 | There is an exterior stairway and ramp from the loading dock which do not have landings and the loading dock area is currently dirt. This project would provide for concrete landings to be installed at the bottom of the ramp and stairs and a concrete slab-on-grade to be installed where trucks make their deliveries. | NURSERY SEED BANK | 9795 | CNR | Forestry |  | Washoe Valley | 1995 | 1450 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0889INT1 | INTERIOR FINISHES | 0889 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0889EXT1 | EXTERIOR FINISHES | 0889 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0890PLM1 | WATER HEATER REPLACEMENT | 0890 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0890HVA1 | HVAC EQUIPMENT REPLACEMENT | 0890 | The wood stove, electric heaters and window-mounted evaporative cooler were installed in 1980. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new central HVAC system for the building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0890INT3 | INTERIOR DOOR REPLACEMENT | 0890 | The interior doors in this building are hollow core units and are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 3 interior doors was used in this estimate. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0890INT2 | VCT FLOORING REPLACEMENT | 0890 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. Asbestos Containing Material (ACM) may be present and testing of the flooring is recommended prior to proceeding with this project. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6300
0890EXT2 | WINDOW REPLACEMENT | 0890 | The windows are original, single pane construction in a metal frame. These older windows are drafty, not energy efficient and at least one is broken. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0890ENR1 | LIGHTING UPGRADE | 0890 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0889HVA1 | HVAC EQUIPMENT REPLACEMENT | 0889 | The natural gas fired wall heater and the window mounted evaporative cooler are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new central HVAC system for the building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | NURSERY OFFICE | 9795 | CNR | Forestry |  | Washoe Valley | 1900 | 500 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9795ADA1 | ADA IMPROVEMENTS | 9795 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area, sidewalks and ramps are necessary to comply with ADA requirements. The sidewalks and ramps will provide access to the Office, the public restrooms at the Cook House, the Lath Houses and any other area on the site that the public is allowed to go to view and purchase plants. This project would provide for a concrete van accessible ADA parking, loading space and all necessary walkways and ramps. This will require regrading, installing P.C. concrete, striping, signage, railings and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | WESTERN REGION NDF NURSERY | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 55000
2343EXT2 | LOADING DOCK REPAIRS | 2343 | The hydraulic lift on the loading dock was not functioning properly at the time of the 2009 survey. The lift is original to the building and should be scheduled for repair. This project would provide for a licensed mechanic to repair the lift to it's original working condition. | NURSERY SEED BANK | 9795 | CNR | Forestry |  | Washoe Valley | 1995 | 1450 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2344INT1 | INTERIOR FINISHES | 2344 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. | NURSERY PUMP HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 2002 | 85 | 2018-08-15 | Four to Ten Years | Long-Term Needs | 3 | 425
2344EXT1 | EXTERIOR FINISHES | 2344 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY PUMP HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 2002 | 85 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 850
2345EXT1 | EXTERIOR FINISHES | 2345 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NURSERY PLANTING BUILDING STORAGE | 9795 | CNR | Forestry |  | Washoe Valley | 2003 | 540 | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
2345STR1 | STRUCTURAL ASSESSMENT | 2345 | This structure was built without plans and inspections. This project recommends that a licensed engineer perform a structural investigation to evaluate the construction. Future projects would be based on this report. | NURSERY PLANTING BUILDING STORAGE | 9795 | CNR | Forestry |  | Washoe Valley | 2003 | 540 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 2500
9795SIT2 | IRRIGATION UPGRADE | 9795 | The existing landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 3,000 linear feet was used to generate this estimate. | WESTERN REGION NDF NURSERY | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0890ADA2 | ADA RESTROOM / REMODEL UPGRADE | 0890 | The Men's and Women's designated public restrooms and restroom access hallway do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for the remodeling of a Men's and Women's ADA accessible restrooms and widening of the hallway to provide minimum clearances for access into the restrooms. These items may include a new sink, toilet, grab bars, door hardware, mirrors, fixtures, exhaust fans, flooring and paint for each restroom and some minor remodeling including some demolition of existing walls and new wall construction; all of which, is non-structural. ADA signage is also included in this estimate. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | NURSERY COOK HOUSE | 9795 | CNR | Forestry |  | Washoe Valley | 1980 | 700 | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 35000
9795ENV4 | BACKUP WELL PUMP REPLACEMENT | 9795 | The nursery has a main well and backup well. The backup well equipment is at the end of its useful life and should be replaced. This project provides for the replacement of the 1.5 hp pump and associated equipment. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/29/2009. | WESTERN REGION NDF NURSERY | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9795ENV1 | 4" BACKFLOW ASSEMBLY, VAULT, AND POWER | 9795 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/29/2009. | WESTERN REGION NDF NURSERY | 9795 | CNR | Forestry |  | Washoe Valley | 0 |  | 2018-08-15 | Immediate to Two Years | Currently Critical | 1 | 25000
2731EXT1 | EXTERIOR FINISHES | 2731 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope including painting or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE | 9796 | Military | NNG | Fire Sci | Carlin | 2006 | 120 | 2007-11-08 | Four to Ten Years | Long-Term Needs | 3 | 360
2960EXT1 | EXTERIOR FINISHES | 2960 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #10-TOILET ROOMS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 573 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2865
2951PLM1 | WATER HEATER REPLACEMENT | 2951 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2952ENR1 | INCANDESCENT LIGHTING UPGRADE | 2952 | The existing lighting fixtures are incandescent type, and are not energy efficient. This project will upgrade incandescent fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 8941
2952PLM1 | WATER HEATER REPLACEMENT | 2952 | There is a 100 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. Removal and disposal of the existing equipment is included in this estimate. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2953ENR1 | INCANDESCENT LIGHTING UPGRADE | 2953 | The existing lighting fixtures are mostly T-8 fluorescent lights and do not require upgrading at this time. However, there are large areas lit by the older incandescent type lamps, and are not energy efficient. This project will upgrade incandescent fixtures to higher efficiency units with a longer life cycle. CFL (compact fluorescent lamps) are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 5000
2953PLM1 | WATER HEATER REPLACEMENT | 2953 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2953EXT2 | ROOF REPLACEMENT | 2953 | The roof on this building was in fair condition at the time of the survey. There are two roof coverings on the building, standing seam metal and Sarnafil single-ply membrane. The statewide roofing program has set the useful life of an average single-ply membrane roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that the single-ply membrane portion of the roof be replaced by 2014 to be consistent with the roofing program and the end of the warranty period. 4,624 square feet was used to generate this estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Four to Ten Years | Long-Term Needs | 3 | 69360
2954ENR1 | OCCUPANCY SENSOR INSTALLATION | 2954 | There are no occupancy sensors installed in the building to control lighting. It is recommended that sensors be installed in order to reduce energy costs. Occupancy sensors will be installed in restrooms, utility rooms and other low occupancy areas for additional savings. This project provides for purchase and installation of 6 sensors. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 2400
2954PLM1 | WATER HEATER REPLACEMENT | 2954 | There is a 432 gallon, 985 MBH input propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2955ENR1 | OCCUPANCY SENSOR INSTALLATION | 2955 | There are no occupancy sensors installed in the building to control lighting. It is recommended that sensors be installed in order to reduce energy costs. Occupancy sensors will be installed in restrooms, storage rooms, utility rooms and other low occupancy areas for additional savings. This project provides for purchase and installation of 10 sensors. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 4000
2955PLM1 | WATER HEATER REPLACEMENT | 2955 | There is a 432 gallon, 1255 MBH input propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2955EXT2 | ROOF REPLACEMENT | 2955 | The roof on this building was in fair condition at the time of the survey. There are two roof coverings on the building, standing seam metal and Sarnafil single-ply membrane. The statewide roofing program has set the useful life of an average single-ply membrane roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that the single-ply membrane portion of the roof be replaced by 2014 to be consistent with the roofing program and the end of the warranty period. 6,600 square feet was used to generate this estimate. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Four to Ten Years | Long-Term Needs | 3 | 99000
2956EXT2 | ROOF REPLACEMENT | 2956 | The roof on this building was in fair condition at the time of the survey. There are two roof coverings on the building, standing seam metal and Sarnafil single-ply membrane. The statewide roofing program has set the useful life of an average single-ply membrane roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that the single-ply membrane portion of the roof be replaced by 2014 to be consistent with the roofing program and the end of the warranty period. 6,600 square feet was used to generate this estimate. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56550
2960PLM1 | WATER HEATER REPLACEMENT | 2960 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #10-TOILET ROOMS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 573 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2959PLM1 | WATER HEATER REPLACEMENT | 2959 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #9-CLASSROOM/TOILET #1 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2967PLM1 | WATER HEATER REPLACEMENT | 2967 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #9-CLASSROOM/TOILET #2 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2957HVA1 | CENTRAL PLANT UPGRADES | 2957 | The Central Plant contains a hot water boiler and evaporative cooling tower located on the equipment patio on the west side of the Buildings and Grounds building. The patio does not have a roof on it and the inclement weather makes it difficult to maintain the equipment. It is recommended that a roof over the patio be installed and to relocate the cooling tower outside of the patio. This project includes roof framing, installing a standing seam roofing system to match the existing roof, relocating the cooling tower and installing a thermostatically-controlled intake louver in the wall to provide combustion and cooling air to the boiler. Structural calculations will be required to ensure that loads from the new roof are properly supported. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2967EXT2 | EXTERIOR FINISHES | 2967 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #9-CLASSROOM/TOILET #2 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
2954EXT1 | EXTERIOR FINISHES | 2954 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48795
2955EXT1 | EXTERIOR FINISHES | 2955 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58910
2956EXT1 | EXTERIOR FINISHES | 2956 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48600
2958EXT1 | EXTERIOR FINISHES | 2958 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #8-CABANA/STORAGE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 2480 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12400
2951ENR1 | OCCUPANCY SENSOR INSTALLATION | 2951 | There are no occupancy sensors installed in the building to control lighting. It is recommended that sensors be installed in order to reduce energy costs. Occupancy sensors will be installed in restrooms, conference rooms, utility rooms, and other low occupancy areas for additional savings. This project provides for purchase and installation of 12 sensors. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 4800
2957PLM1 | WATER HEATER REPLACEMENT | 2957 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2959EXT1 | EXTERIOR FINISHES | 2959 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #9-CLASSROOM/TOILET #1 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
2956PLM1 | WATER HEATER REPLACEMENT | 2956 | There are two electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new 50 gallon and 20 gallon electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3035EXT1 | EXTERIOR FINISHES | 3035 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FIRE WATER PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1220 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6100
2957EXT1 | EXTERIOR FINISHES | 2957 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15840
2956INT1 | INTERIOR FINISHES | 2956 | The interior finishes are in fair condition. Most of the walls are unpainted CMU which do not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 1,118 square feet of area has been used to generate this estimate. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5590
2955INT1 | INTERIOR FINISHES | 2955 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58910
2954INT1 | INTERIOR FINISHES | 2954 | The interior finishes are in good condition. Most of the walls are covered with wallpaper and does not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 500 square feet of area was used to generate this estimate. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2953INT1 | INTERIOR FINISHES | 2953 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 98660
2952INT1 | INTERIOR FINISHES | 2952 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44705
2957INT1 | INTERIOR FINISHES | 2957 | The interior finishes are in fair condition. Most of the walls are unpainted CMU which do not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 250 square feet of area has been used to generate this estimate. | BLDG #7-BUILDINGS AND GROUNDS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 3168 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
3036EXT1 | EXTERIOR FINISHES | 3036 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DOMESTIC WATER PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3033EXT1 | EXTERIOR FINISHES | 3033 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SANITARY SEWER BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3034EXT1 | EXTERIOR FINISHES | 3034 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CHEMICAL STORAGE BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2962INT2 | VCT FLOORING REPLACEMENT | 2962 | The VCT (vinyl composite tile) flooring on the observation level is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | BLDG #13-TOWER | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 644 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5796
2964EXT1 | EXTERIOR FINISHES | 2964 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DAF/CHEMICAL BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 2002 | 3696 | 2009-11-18 | Four to Ten Years | Long-Term Needs | 3 | 11088
2962INT1 | INTERIOR FINISHES | 2962 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #13-TOWER | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 644 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3220
2962EXT1 | EXTERIOR FINISHES | 2962 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and painting of the steel posts, beams and columns, sealing and caulking of the metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #13-TOWER | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 644 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12880
9796EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9796 | There are 10 steel shade ramadas in different locations throughout the site which are either 600 s.f. or 1,366 s.f. for a total of 6,766 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. | FIRE SCIENCE ACADEMY SITE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 |  | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13532
3037EXT1 | EXTERIOR FINISHES | 3037 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WELL PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 200 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2952INT2 | FLOORING REPLACEMENT | 2952 | The VCT (vinyl composite tile) and carpet in the building are worn and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71528
2963EXT1 | EXTERIOR FINISHES | 2963 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #14-SECURITY KIOSK | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 60 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
2959INT1 | INTERIOR FINISHES | 2959 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #9-CLASSROOM/TOILET #1 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
2955INT2 | FLOORING REPAIRS / REPLACEMENT | 2955 | The sealed concrete and carpet in the building are worn and reaching the end of their useful life. It is recommended that the concrete be stripped and re-sealed and that the carpet in the offices be replaced. This project would provide for stripping the concrete and applying a new coat of sealant and removal and disposal of the carpet and installation of new heavy duty commercial grade carpet in the next two to three years. | BLDG #5-TURNOUT | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 11782 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58910
2953INT2 | FLOORING REPLACEMENT | 2953 | The VCT (vinyl composite tile) and carpet in the building are worn and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. The carpet in the Auditorium has recently been replaced and is not included in the estimate. 15,000 square feet was used to generate the estimate. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
2951INT2 | FLOORING REPLACEMENT | 2951 | The VCT (vinyl composite tile) and carpet in the building is worn and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 67584
3037INT1 | INTERIOR FINISHES | 3037 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WELL PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 200 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3036INT1 | INTERIOR FINISHES | 3036 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DOMESTIC WATER PUMP HOUSE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
3033INT1 | INTERIOR FINISHES | 3033 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SANITARY SEWER BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2964INT1 | INTERIOR FINISHES | 2964 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DAF/CHEMICAL BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 2002 | 3696 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18480
2963INT1 | INTERIOR FINISHES | 2963 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #14-SECURITY KIOSK | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 60 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
2960INT1 | INTERIOR FINISHES | 2960 | The interior finishes are in fair condition. Most of the walls are unpainted CMU which do not need to be addressed at this time. It is recommended that the painted gypsum board walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 150 square feet of area has been used to generate this estimate. | BLDG #10-TOILET ROOMS | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 573 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
2967INT1 | INTERIOR FINISHES | 2967 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #9-CLASSROOM/TOILET #2 | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 1320 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
3034INT1 | INTERIOR FINISHES | 3034 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CHEMICAL STORAGE BUILDING | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 100 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2956INT2 | FLOORING REPAIRS | 2956 | The sealed concrete in the building is damaged and reaching the end of its useful life. It is recommended that the concrete be sealed in order to extend its useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next two to three years. | BLDG #6-FIRE STATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9720 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48600
2954INT2 | CARPET REPLACEMENT | 2954 | The carpet in the building is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. 9,000 square feet was used to generate this estimate. | BLDG #4-STAFF RESIDENCE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 9759 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63000
9796SIT1 | SLURRY SEAL ASPHALT PAVING | 9796 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 4- 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 175,000 square feet of asphalt area was used to generate this estimate. | FIRE SCIENCE ACADEMY SITE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 |  | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 131250
2953EXT1 | EXTERIOR FINISHES | 2953 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #3-CLASSROOM | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 19732 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 98660
2952EXT1 | EXTERIOR FINISHES | 2952 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #2-FOOD SERVICE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8941 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44705
2951INT1 | INTERIOR FINISHES | 2951 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42240
2951EXT1 | EXTERIOR FINISHES | 2951 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the control joints, metal panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG #1-ADMINISTRATION | 9796 | Military | NNG | Fire Sci | Carlin | 1998 | 8448 | 2009-11-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42240
9796ADA1 | INSTALL ADA SIGNAGE | 9796 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. Directional and building signage from the ADA parking spaces to the entrance of the core facility buildings is missing. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | FIRE SCIENCE ACADEMY SITE | 9796 | Military | NNG | Fire Sci | Carlin | 1998 |  | 2009-11-18 | Immediate to Two Years | Currently Critical | 1 | 2500
2811PLM2 | ISOLATION VALVE INSTALLATION | 2811 | There are no isolation valves for the building's water lines. The main water line that serves the 78,145 sf building on the site is in need of 25 isolation valves. This will allow the maintenance staff to conduct repairs and maintenance to the plumbing without shutting down the entire building. More importantly, a leak in the building can be shut down quickly minimizing damage in an emergency. This estimate provides for 2-1/2" ball valves to be installed in individual rooms throughout the building. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2811SFT2 | FIRE SUPPRESSION/ MECHANICAL UPGRADE | 2811 | Staff at the Nevada State Museum indicated, during the time of the survey, when the spray booth is in use paint overspray is landing on the fire suppression sprinkler head. They have been written up by the State Fire Marshal’s Office for having paint on a fire suppression sprinkler head. Per NFPA 33 Chapter 7 Section 7.2 states, Each spray area shall be provided with mechanical ventilation that is capable of confining and removing vapors and mists to a safe location and is capable of confining and controlling combustible residues, dusts, and deposits. Section 7.2.3 Mechanical ventilation shall be kept in operation at all times while spray operations are being conducted and for a sufficient time thereafter to allow the vapors from drying coated objects or material and residues to be exhausted. It is recommended to have a Mechanical Engineer determine the proper Cubic Feet per Minute (CFM) needed to remove all paint vapors and install exhaust venting to meet the requirements. Per NFPA 33 Chapter 9 Section 9.4.1 The automatic sprinkler system shall be a wet pipe system, a dry pipe system, a pre action system, or an open-head deluge system, whichever is most appropriate for the portion of the spray operation being protected. This project would provide for removing the plastic from the fire suppression sprinkler head and installing the exhaust venting in order to remove the paint overspray from the booth. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 15000
2811EXT4 | ROOF REPAIRS | 2811 | The cooling towers are leaking water onto the single-ply membrane roofing system. The single-ply membrane roofing system is starting to lose the top layer and is showing some of the second layer (scrims). This project would provide funding to repair the cooling tower’s leaks, and have the single-ply membrane patched where needed. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 2000
2811SFT1 | HIGH DENSITY STORAGE REPAIRS | 2811 | The high density storage system in the building is malfunctioning. The photo eyes and security switches are not operating properly, which is a safety concern. It is recommended that a licensed contractor repair the malfunctioning safety devices. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 4000
2811ELE2 | ELECTRICAL PANEL UNUSED OPENINGS | 2811 | The wiring in the electrical panel has missing breakers and it is recommended to have blanks installed at the unused openings. Per NEC 408.7 states, unused openings for circuit breakers and switches shall be closed using identified closures, or other approved means that provide protection substantially equivalent to the wall of the enclosure. Unused openings create a safety issue during repairs or upgrades. This project would provide for blanks to be installed where the missing breakers are located. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 250
2811ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2811 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states, a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funding to relocate the items blocking the electrical panels. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 250
2811EXT1 | EXTERIOR FINISHES | 2811 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Four to Ten Years | Long-Term Needs | 3 | 781450
2811INT1 | INTERIOR FINISHES | 2811 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Four to Ten Years | Long-Term Needs | 3 | 781450
2811PLM1 | WATER HEATER REPLACEMENT | 2811 | There are three, 30 gallon, electric water heaters in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2811EXT2 | LOADING DOCK UPGRADES | 2811 | The existing loading dock does not have safety rails on the dock platform nor along the approach ramp, which has a sharp drop on one side of several feet down. There have been several near-miss accidents, where dock users have nearly fallen off the platform due to lack of rails. In addition, the approach ramp to the dock platform has a very sharp angle and is very narrow, which makes it difficult and dangerous to move loading vehicles or equipment from the approach ramp to the platform. This project would provide for the removal of the ramp and the installation of a wider, better angle ramp and for the installation of safety rails per IBC 2012. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Immediate to Two Years | Currently Critical | 1 | 213012
2811EXT3 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 2811 | The roof drainage downspout runs next to the loading dock. Delivery vehicles have run into the down spout and crushed it. Due to this, the water no longer flows away from the building, foundation and loading dock. This project would provide for a new 30’ down spout. The new down spout shall be located away from the loading dock to prevent future vehicle damage and to allow for runoff to flow away from the building. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2811SEC1 | SECURITY SYSTEM UPGRADE | 2811 | At the time of the survey, the lighting and video surveillance systems were failing, inadequate, and non-programmable. The current lighting system runs on a 3" floppy disc and both the lighting and video surveillance systems software are too old to accept software updates. It is recommended that both systems be replaced with new systems and adding a building intrusion infrared alarm system to the 78,145 sf building. This project recommends replacing the panels, software, hardware, and adding additional wiring where needed. | NEVADA STATE MUSEUM, LAS VEGAS | 9817 | CultAffr | M&H | Museums | Las Vegas | 2008 | 78145 | 2016-05-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 630000
0418SIT3 | CARPORT STRUCTURE | 0418 | There are approximately 10 state vehicles parked in the rear parking lot at any given time. Many of these vehicles carry sensitive measuring and testing equipment which can deteriorate quickly due to exposure to the elements. This project would provide a steel carport capable of protecting 10 vehicles to be built on the North side of the site. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0418INT3 | INTERIOR FINISHES | 0418 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35435
0418SIT5 | SLURRY SEAL ASPHALT PAVING | 0418 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including loading zones, access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 20,000 square feet of asphalt area was used to generate this estimate. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 18000
0418ADA3 | ADA PARKING UPGRADE | 0418 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The main entrance to the building has ADA parking stalls which do not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking area up to code including a compliant path of travel from the spaces to the building entrance, updated signage and any other necessary upgrades. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 35000
0418SIT6 | LANDSCAPE SPRINKLER REPLACEMENT | 0418 | The landscape sprinkler system is old and consists of at least three different types of piping. The existing copper, PVC and galvanized iron piping has been spliced together over the years and is a constant maintenance problem. This project would provide for the replacement of the entire sprinkler system including piping, sprinkler heads, check valves and a new backflow preventer. The estimate includes disposal of the existing materials. An allowance for 300 feet of 2" schedule 40 PVC pipe, excavation and backfill is included with this estimate. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0418INT4 | CARPET REPLACEMENT | 0418 | The carpet in the Supervisor/ Metrology's office is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0418EXT4 | REPLACE STOREFRONT ENTRANCE SYSTEMS | 0418 | There are two separate storefront glazing systems that are showing signs of failure due to broken seals and general wear and tear. The storefront systems are an exterior application and are exposed to weather extremes. This project would provide removal and disposal of the (2) 15' wide storefronts and purchase and installation of two new systems including hardware. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0418EXT3 | WINDOW REPLACEMENT | 0418 | The windows in the original building are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. Several of the windows also have a metal wall panel below them that should be removed and replaced with a framed and insulated wall to match the adjacent walls. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units and does not include the windows in the storefront entrance systems which are addressed in a separate project. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0418EXT2 | EXTERIOR FINISHES | 0418 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 70870
0418ENR1 | INSTALL ENERGY MANAGEMENT SYSTEM | 0418 | This project recommends the installation of an Energy Management System (EMS) for the building. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0418ELE1 | LIGHTING UPGRADE | 0418 | The existing lighting fixtures in the original building are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. The estimate is based on quotes recently acquired by the staff for this project. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0418PLM2 | PLUMBING / WASTE LINE ASSESSMENT | 0418 | The plumbing / waste lines are original to the building and major failures are beginning to surface including broken waste lines and corroded flanges. This project recommends that a licensed plumbing contractor perform a camera scope to assess the condition of the piping especially the waste lines. Future projects would be based on this report. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 5000
0418SIT4 | REMOVE PALM TREES | 0418 | There are numerous palm trees along the perimeter of the paved parking along the north side of the site. They are damaging the concrete curbing and are in need of removal. This project would provide for the removal of the palm trees and repair of the damaged curbing. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 10000
0418PLM3 | 4" BACKFLOW ASSEMBLY, VAULT, AND POWER | 0418 | State Health Law (NAC 445A.67185) and the International Plumbing Code (IPC Section 608) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution can be discharged or drawn into the public water system as a result of back siphonage or backpressure. There is no backflow prevention on domestic water lines and fire sprinkler or standpipe lines. This project would provide funding for installation of a 4" reduced pressure backflow prevention assembly, required fittings, a vault below grade, and allowance for 200 feet of 1" conduit to provide power for the required heat source inside the vault. This estimate includes two assemblies, one for the domestic water and one for the fire line. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0418HVA1 | REPLACE ROOFTOP HVAC UNITS | 0418 | The heating and cooling to this building is provided by several rooftop packaged units of which 3 appear to be original equipment. They are in poor condition and have reached the end of their expected life. This project would provide for the installation of 3 new rooftop packaged HVAC units including connections to existing utilities. Removal and disposal of the old units is included in this estimate. This project is recommended to be undertaken at the same time as the energy management system installation. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
0418PLM1 | WATER HEATER REPLACEMENT | 0418 | The average life span of a water heater is eight to ten years. The existing 40 gallon gas water heater in the building has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 40 gallon gas water heater. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0418INT6 | RESTROOM REMODEL | 0418 | There are several restrooms in this building. This project would provide for a complete remodel and rehabilitation of one Men and one Women restroom in the original building including fixtures, casework, floor and wall finishes and hardware. This project is recommended to be completed after the PLUMBING / WASTE LINE ASSESSMENT project has determined the state of the plumbing system. This estimate does not include any funds for under slab plumbing and / or waste line replacement. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0418SFT4 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0418 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the energy management system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 3500
0418INT7 | RESURFACE CONCRETE FLOOR | 0418 | The painted concrete floor in the East wing laboratory is worn and cracked and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1900EXT2 | EXTERIOR FINISHES | 1900 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | GARAGE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 500 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 70870
0418EXT5 | OVERHEAD DOOR REPLACEMENT | 0418 | There is a 16'x14' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0418ELE2 | ELECTRICAL UPGRADE | 0418 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion there of was previously recommended in the FCA report dated 03/14/2000. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/05/2008. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Immediate to Two Years | Currently Critical | 1 | 141740
0418ENR2 | INSULATE LABORATORY | 0418 | The Metrology laboratory on the North side of the building was built in an existing garage that does not have proper insulation. The heating and cooling is not efficient in the room, the sensitive measuring and testing equipment is affected by the inconsistent temperatures and the staff working in the lab do not have a comfortable work environment. This project would provide for the furring of the interior side of the CMU, board insulation, 5/8" Type X gypsum board, paint and ceiling insulation to bring the room up to the appropriate "R" value to match the rest of the building. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
0418SEC1 | SECURITY SYSTEM | 0418 | The facility currently does not have a security system installed. Access on or off of the property is uncontrolled and there have been security problems including the homeless inhabiting areas of the property. This project recommends card-access control, security fencing, security cameras and additional site lighting be installed to remedy this problem. | LV B&G - PUBLIC WORKS OFFICE | 9818 | Admin | PubWorks | B&G | Las Vegas | 1974 | 7087 | 2008-02-05 | Four to Ten Years | Long-Term Needs | 3 | 200000
2451SIT1 | SITE FENCING | 2451 | The Building / Weir site is located in Clear Creek Canyon. The site currently is wide open to the public and is a safety hazard. This project would provide for an 6 foot tall industrial chain link fence with a locked gate to prevent the public from entering the site and building. Signage is included. | STEWART IRRIGATION DIVERSION BLDG | 9820 | Admin | PubWorks | B&G | Carson City | 1890 | 200 | 2005-03-11 | Immediate to Two Years | Currently Critical | 1 | 6000
2451ENV2 | CONCRETE WIER REHABILITATION | 2451 | The existing concrete weir structure is in need of cleaning and rehabilitation. This project would provide for resurfacing the concrete wier channels with a water resistant epoxy coating, replacing about 20 lineal feet of water intake piping, new filters and cleaning. | STEWART IRRIGATION DIVERSION BLDG | 9820 | Admin | PubWorks | B&G | Carson City | 1890 | 200 | 2005-03-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2558ADA1 | ADA IMPROVEMENTS | 2558 | The restrooms in the building are not 100% ADA compliant. This project would provide for improvements including but not limited to flush valve relocation and relocation of toilet tissue dispensers and signage. The conference / break room casework is also not 100% ADA compliant. This project would also provide for required modifications to the casework to provide ADA accessibility. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 3000
9822SIT3 | LANDSCAPING MAINTENANCE | 9822 | The site has some grass areas that are in need of regular maintenance, mowing and trimming. There are also numerous areas of weeds and brush which are in need of removal as they may damage the retaining walls and fencing. This project would provide for regular maintenance of the site including mowing and trimming, weed and brush removal on an annual basis. This is a one time estimate but should be scheduled in the agency's operating budget. A $200 monthly allowance is a recommended amount for budgeting. during the warmer months. | ELKO AGRICULTURE REGIONAL OFFICE SITE | 9822 | Agricult | Agri |  | Elko | 1997 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2558INT1 | INTERIOR FINISHES | 2558 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. A satin or semi-gloss paint should be utilized in wet areas for durability. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28500
2558ENR1 | LED LIGHTING UPGRADE | 2558 | The majority of the existing lighting in the building is older fluorescent T-8 lamps in recessed fixtures. This project would provide for re-lamping the existing fixtures with LED tubes. This project would result in energy savings. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17100
9822SIT1 | AC PAVING SEAL - CRACK FILL - REPAIR | 9822 | The existing AC paving on site is due for crack filling, sealing and re-striping. There are also some areas that are alligatoring and in need of removal and replacement. This project would provide for a crack fill and slurry seal as well as repair of damaged AC paving. Striping including ADA accessible parking and loading zones is included in this estimate. This project should be scheduled every 4-5 years based on environmental conditions. | ELKO AGRICULTURE REGIONAL OFFICE SITE | 9822 | Agricult | Agri |  | Elko | 1997 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9822SIT2 | AUTOMATIC GATE REPAIR | 9822 | The existing automatic sliding gate has been problematic for years. It sometimes opens and will not close. This project would provide for a new electronic gate motor and wiring to be installed including connections and testing of the new system. | ELKO AGRICULTURE REGIONAL OFFICE SITE | 9822 | Agricult | Agri |  | Elko | 1997 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2558SFT1 | OVERHEAD COILING DOOR REPAIR | 2558 | The existing power operated overhead coiling door does not operate properly according to staff. This project would provide for required repairs to the door motor and controls as needed. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2558EXT1 | EXTERIOR FINISHES | 2558 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are repairing damaged stucco fascia areas, painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. An acrylic paint should be utilized on the stucco areas for durability. | ELKO AGRICULTURE REGIONAL OFFICE | 9822 | Agricult | Agri |  | Elko | 1997 | 5700 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39900
1476INT6 | JANITORS CLOSET REPAIRS | 1476 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide Fiberglass Reinforced Panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1476ADA4 | ADA RESTROOM UPGRADE | 1476 | The Men's and Women's designated ADA restrooms do not entirely meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 40000
1476PLM1 | WATER HEATER REPLACEMENT | 1476 | There are two electric water heaters in the building. One water heater is a 12 gallon and the other is a 19 gallon. The average lifespan of a water heater is eight to ten years. The units were installed in 1992. It is recommended that 2 new electric water heaters, seismic straps, braided steel hose, expansion tanks, ball valves, hardwire electric lines and pans be installed in the next 2-3 years. Removal and disposal of the existing equipment is included in this estimate. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1476EXT6 | WINDOW REPLACEMENT | 1476 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 30000
1476EXT3 | EXTERIOR FINISHES | 1476 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 40000
1476INT5 | INTERIOR FINISHES | 1476 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 40000
1476ELE3 | ELECTRICAL PANEL UPGRADES | 1476 | The electrical panel in the building does not have an inside cover (dead panel) that properly protects individuals from touching the bus bar and the interior of the panel. This does not comply with NEC 2011 or OSHA 1910. This project would provide funds to fabricate and install a new dead panel in accordance with NEC 2011 and OSHA 1910. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 2000
1476ADA2 | BREAK ROOM REMODEL | 1476 | The kitchenette and associated cabinets in the employee break room are in good condition but don’t comply with ADA requirements. This project recommends changes to the kitchenette and associated break room for ADA compliance. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design. This estimate includes removal and disposal of the necessary existing materials. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 15000
1476ENR2 | LIGHTING UPGRADE | 1476 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 32000
9823ENR1 | EXTERIOR LIGHTING REPLACEMENT | 9823 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
9823ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9823 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 30000
1476EXT5 | ROOF REPLACEMENT | 1476 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time-frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 48000
9823SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9823 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 10,000 square feet of asphalt area was used to generate this estimate. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 14000
1476ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1476 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 07/23/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 4000
1476ELE2 | ELECTRICAL REPAIRS | 1476 | Heat tape was installed in the roof drains and the power cords were plugged into outlets on the roof. The electrical outlets were installed in such a way that the face is on top allowing rain and snow to fall directly into the plug. The conduit is not screwed together in some areas exposing the wires inside to the elements. These issues create a fire and safety hazard and will at the very least cause premature failure of the equipment. This project would provide for reworking the conduits, outlets and wiring by a licensed electrician. This project or a portion thereof was previously recommended in the FCA report dated 07/23/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | NEVADA JOB CONNECT - ELKO OFFICE | 9823 | ETR | ESD |  | Elko | 1985 | 4000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 1500
9823SFT1 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 9823 | The handrail on the concrete stairs on the north side of the site is older and does not meet current code for safety. The gripping surfaces are incorrect, they do not have proper extensions and they are installed on only one side of the stairs. This project recommends the installation of handrails in accordance with 2012 IBC Section 1012. Removal and disposal of the existing materials are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/23/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | ELKO DETR OFFICE SITE | 9823 | ETR | ESD |  | Elko | 0 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 7500
2107SFT1 | VISUAL NOTIFICATION UPGRADE, DISPATCH | 2107 | The building has a fire alarm system throughout, but there are no visual notification devices in the dispatch areas. This project recommends replacing several of the annunciators with combination visual/ auditory notification devices in these areas. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
2107HVA1 | HVAC SYSTEM REPAIRS | 2107 | The HVAC system has received minimal maintenance since the building was commissioned and some repairs and upgrades are necessary. Staff reports that the system does not provide adequate cooling during warmer weather and the temperature controls are inaccurate. The individual thermostats around the building do not display the same temperature as the energy management system. The server and communications rooms are not cooled sufficiently and staff has employed fans and propping doors open for adequate cooling and ventilation. There was at least one heat pump that was inoperable at the time of the survey as well as air filters that had not been replaced recently and clogged screens in the water lines. This project recommends evaluating the HVAC system and performing necessary repairs including re-balancing the system based on current needs. It is also recommended to contract an HVAC maintenance company to service the equipment on a continual basis. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2107ELE1 | ELECTRICAL UPGRADE, DISPATCH | 2107 | The dispatch areas have a higher electrical demand than the building was designed for. The electrical system is currently utilized to its maximum potential. The electrical panels and receptacles are at their limit and extension cords are being used for permanent power. It is recommended the system be upgraded to meet the evolving needs of the dispatch area. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
2107INT2 | CARPET REPLACEMENT | 2107 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 4-5 years. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Four to Ten Years | Long-Term Needs | 3 | 56000
2107ADA3 | ADA SIGNAGE | 2107 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that the restroom ADA signs be relocated off of the doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
2107ELE2 | PROVIDE CLEARANCE AT ELECTRICAL PANEL | 2107 | There is an electrical panel in the building which does not have proper clear floor space around it. A metal shelving system is partially blocking the panel. The 2012 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the shelving system currently blocking the working space. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 250
2107PLM1 | WATER TREATMENT VENDOR | 2107 | The existing water softening/ chemical water treatment systems in the building have not been properly maintained. This project would provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2107INT3 | CABINET REPAIRS | 2107 | The cabinetry in the break rooms and the desk at the reception area has been damaged and are delaminating. This project recommends the replacement of the finishes with heavy duty, quality melamine finishes which encapsulates the door, frame, and shelving. This estimate includes disposal of the existing materials. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9824SIT2 | TREE TRIMMING | 9824 | The site has trees which are growing up against the structure. The trees move in windy conditions, rubbing the roofs and wall finishes, which can cause damage to the building. The root systems are causing shifting and heaving of foundations and sidewalks, creating unsafe conditions. This lack of maintenance could become a safety issue. This project recommends that these issues be addressed by either trimming or removing trees before additional damage is done. | ELKO INTERAGENCY DISPATCH CENTER SITE | 9824 | CNR | Forestry |  | Elko | 2000 |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2107SFT2 | EGRESS LIGHTING REPLACEMENT | 2107 | The emergency egress lighting design is sufficient, but there are 5 wall packs that are inoperable. This project would provide for the purchase and installation of 5 emergency egress light packs to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
9824SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9824 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the heli-tack pad. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 100,000 square feet of asphalt area was used to generate this estimate. | ELKO INTERAGENCY DISPATCH CENTER SITE | 9824 | CNR | Forestry |  | Elko | 2000 |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
2107INT1 | INTERIOR FINISHES | 2107 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45715
2107EXT1 | EXTERIOR FINISHES | 2107 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ELKO INTERAGENCY DISPATCH CENTER | 9824 | CNR | Forestry |  | Elko | 2000 | 9143 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45715
9825SIT5 | WEED ABATEMENT | 9825 | The site has areas that are covered with weeds especially in the rear storage area. This project would provide for the removal and disposal of the weeds on the site and treatment of the area with an herbicide to prevent future weed growth. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2127EXT1 | EXTERIOR SIDING REPLACEMENT | 2127 | This building has vinyl siding which is damaged and reaching the end of its useful life and should be scheduled for replacement. Some of the vinyl pieces are missing and others are cracked and warped. The siding is out of warranty and has been discontinued by the manufacturer. New siding will be required in the future to maintain the building in good weather tight condition. This project recommends removing the vinyl siding and replacing it with T1-11 panels finished with an oil-based stain or paint. Removal and disposal of the vinyl siding is including in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25800
9825SIT6 | CONSTRUCT STORAGE BUILDING | 9825 | There is a major lack of storage on the site to support the various functions conducted by the Wildlife staff. Game evidence is currently stored outside which does not preserve the evidence properly and presents a theft opportunity. Testing equipment, storage and supplies are stored in temporary metal containers at the rear of the site which are difficult to access and provide little security. A new storage building would also provide space for lab activities. Dissections and other lab work are currently taking place in the existing office which is not designed for this activity. This project would provide for the purchase and installation of a 40' x 60' engineered steel building on a concrete foundation including connection to the existing electrical, water, sewer and propane services. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
2127INT1 | INTERIOR FINISHES | 2127 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8600
2127ADA1 | ADA SIGNAGE | 2127 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 600
2127SFT1 | GFCI DUPLEX OUTLET REPLACEMENT | 2127 | One of the GFCI outlets in the restroom is damaged. The test and reset buttons did not work at the time of the survey which poses a safety hazard. This project would provide for the purchase and installation of a GFCI duplex outlet for the restroom. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 300
2127ADA2 | ADA ACCESSIBLE COUNTER | 2127 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
2127ENR1 | LIGHTING UPGRADE | 2127 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2580
2127SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2127 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 6880
2127SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2127 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 12040
2127SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2127 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
2127PLM1 | WATER HEATER REPLACEMENT | 2127 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2127SFT6 | EXTERIOR LANDING INSTALLATION | 2127 | There is an exterior stairway at the rear of the building which does not have a landing. This does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the width of the landing shall not be less than the width of the stairway. This project addresses installing a landing designed to current code. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2127EXT2 | EXTERIOR FINISHES | 2127 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and repairing the vinyl siding and caulking of the windows, painting, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned, repaired and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ELY WILDLIFE FIELD OFFICE | 9825 | Wildlife |  |  | Ely | 2000 | 1720 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8600
9825SIT4 | CARPORT STRUCTURE INSTALLATION | 9825 | There are approximately 10 state vehicles parked in the rear parking area at any given time including trucks, boats, trailers and quads. Some of these vehicles carry sensitive measuring and testing equipment which can deteriorate quickly due to exposure to the elements. This project would provide a steel carport capable of protecting 10 vehicles to be built on the east side of the site. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9825SIT3 | VEHICLE GATE REPLACEMENT | 9825 | The site has a perimeter fence with a vehicle access gate to the south of the building. The manual sliding gate is not operating properly especially in the colder winter months. It is less than 20 feet wide which does not comply with the fire code. This project recommends the gates be upgraded to a motorized track system that can handle the freezing winter temperatures and meets the requirements of the fire code. The gates will be required to meet UL Standard 325, per NRS 405.270 and section 503.2.1 of the 2006 International Fire Code. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9825ADA1 | ADA PARKING SIGN REPLACEMENT | 9825 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria and the existing parking sign is outdated. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances and replacing the parking sign. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1500
9825SIT2 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9825 | There is no site lighting for the access road and parking area which is a security and safety concern. This project would provide for the installation of 4 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
9825SIT1 | SEAL ASPHALT PAVING | 9825 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including the access roads and parking lot. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 10,000 square feet of asphalt area was used to generate this estimate. | ELY WILDLIFE FIELD OFFICE SITE | 9825 | Wildlife |  |  | Ely | 2000 |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
1935SIT1 | SEAL AND STRIPE PARKING LOT | 1935 | The existing parking lot has numerous cracks, in which weeds are growing. This project would seal the cracks, seal the entire lot, restripe, and relocate the handicapped parking sign. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
1935ADA1 | INSTALL POWER DOOR OPENER AND HARDWARE | 1935 | The main entrance to this building is a pair of aluminum storefront doors arranged in a vestibule configuration. This project recommends the installation of a power-assisted door opener for the main entrance and includes the installation, related wiring and hardware. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Immediate to Two Years | Currently Critical | 1 | 7000
1935HVA0 | REPLACE HVAC SYSTEM AND CONTROLS | 1935 | The existing HVAC system is not able to effectively heat and cool the office spaces, handicapped restrooms, and the phone/server room. The rooftop units are reaching the end of their useful lives and should be replaced. Ductwork should be redesigned, installed, and balanced to effectively distribute the air in the spaces. New electric supplemental heating should be added to the two handicapped bathrooms, which are on exterior walls. An exhaust fan should be installed in the store room (phone and server room) to remove heat from the server. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61000
1935EXT1 | REFINISH SOFFITS | 1935 | The building soffits are starting to show signs of weathering. This project would cover the existing wood soffit with an aluminum cover and install soffit vents. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Four to Ten Years | Long-Term Needs | 3 | 3000
1935INT1 | BUILDING INTERIOR REFINISHING | 1935 | The building exterior walls are bare Concrete Masonry Units (CMU) and should be furred and insulated to conserve energy and improve comfort. Floor coverings, VCT and carpet are well worn and in need of replacement. The kitchen cabinets are in need of refinishing. The interior walls are in need of repainting. In numerous locations, sheetrock fasteners in partition walls are working loose and are protruding. Both doors to the handicapped restrooms have improper door stops that will damage the doors. the rear door is in need of weather strip, a door stop, repairs to the exit device. This project would furr the exterior walls, paint all interior walls, grind and fill the floor slab cracks, replace the VCT, replace the carpet with carpet tile, refinish the kitchen cabinets, install overhead stops on both handicapped restroom doors and the rear door, repair the rear door exit device, and install new brush type weather seal at the rear door. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52500
1935HVA2 | INSTAL ROOF ACCESS HATCH AND LADDER | 1935 | The existing building has no permanent access to the rooftop equipment. The shape of the Mansard roof makes using a ladder to access the roof unsafe. The Uniform Mechanical Code (1997 307.5 and 2003 904.10.3) require roof access for equipment servicing. This project would install a lockable roof access hatch and permanent fixed ladder in the Janitor's Closet or Store Room. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1935EXT2 | REPLACE ROOF | 1935 | The existing roof is due for replacement and is the subject of a 2005 CIP project request. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
1935LGT1 | LONG-TERM NEEDS | 1935 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and sealant where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | FALLON ETR OFFICE | 9827 | ETR | ESD |  | Fallon | 1978 | 4000 | 2004-06-04 | Four to Ten Years | Long-Term Needs | 3 | 20000
2462ADA3 | ADA PARKING AND SIGNAGE | 2462 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A parking area, an adjacent passenger loading area and signage are necessary to comply with ADA requirements. This project would provide for one parking space, including an adjacent accessible loading zone in the existing gravel parking area. The project includes required soil preparation, an asphalt parking area for one vehicle, signage, striping and marking an accessible route of travel to the building. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 12000
2462ADA2 | ADA RESTROOM REMODEL | 2462 | A restroom is present in this building. It does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with CABO/ANSI A117.1-1998 Chapter 6 and 2003 IBC Chapter 11. This project would provide funding for construction of a unisex accessible restroom. This project may require a new toilet, grab bars, sink, faucet and hardware. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 10000
2462ADA1 | ACCESSIBLE BUILDING ENTRANCE | 2462 | The building has steps leading into the main entrance. The entrance does not meet the requirements for ADA Accessibility ICC/ANSI A117.1-1998 404.2.4.1. The entry door has a threshold and hardware that does not meet the requirements for ADA accessibility, ICC/ANSI A117.1-1998 404.2.5. This project would provide funding for an accessible ramp, including upper and lower landing areas, handrails, curbing, and replacement of the door hardware and threshold to meet the ADA Accessibility Guidelines. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2462ELE1 | MISCELLANEOUS ELECTRICAL REPAIRS | 2462 | The exterior receptacles are standard duplex receptacles and there are missing safety plugs in the main electrical panel, which is mounted to a telephone pole adjacent to the building. This project would provide funding to install GFIC duplex outlets on the exterior and install safety plugs in the main electrical service including a lock to prevent the public from tampering with the electrical service. | INDIAN SPRINGS NHP SUBSTATION | 9829 | PubSafe | NHP |  | Indian Springs | 2002 | 720 | 2013-06-05 | Immediate to Two Years | Currently Critical | 1 | 1000
0286ADA4 | ELEVATOR UPGRADE | 0286 | The Department of Rehabilitation has offices on the second floor which are served by an older elevator. The configuration of the elevator and controls does not meet current ADA requirements. Due to the significant number of clients with special needs that the Department serves, a complying elevator should be installed. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/10/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2011. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 100000
0286EXT3 | EXTERIOR FINISHES | 0286 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205375
0286INT3 | INTERIOR FINISHES | 0286 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205375
0286ENV1 | ROOF MAINTENANCE | 0286 | There is a low roof section on the north side of the building that requires maintenance work. It has been overcome by pigeons and holds an abandoned HVAC unit. The pigeon droppings have accumulated to an unsafe level and should be cleaned up and the HVAC unit should be removed and disposed of. This project would provide for cleaning the roof area, removing and disposing of the HVAC unit and installing new pigeon deterrent devices. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0286INT4 | SUSPENDED CEILING SYSTEM REPLACEMENT | 0286 | The entire building has a suspended acoustical tile ceiling system that is original dating back to 1973. The t-bar framing is bent and rusted in some areas and some of the acoustical tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system including framing, bracing, acoustical tiles and HVAC grilles. Removal and disposal of the existing ceiling system is included in this estimate. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 205375
0286ADA5 | ADA SIGNAGE | 0286 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 7500
0286INT5 | BREAK ROOM REMODELS | 0286 | The kitchenettes and associated cabinets in the seven employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0286HVA2 | EXHAUST FAN REPLACEMENT | 0286 | The exhaust fan in one of the restrooms was not operating at the time of the survey. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of a new exhaust fan assembly including connections to utilities. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0286ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0286 | There are electrical panels in the east electrical room which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the fiber optic racks and other items currently blocking the working space. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 750
0286PLM1 | WATER HEATER REPLACEMENT | 0286 | There are two 50 gallon gas-fired water heaters in the building. One was installed in 2008, the other one is older. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Four to Ten Years | Long-Term Needs | 3 | 1500
0286ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0286 | This building contains several drinking water fountains on the first and second floors. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. Due to the layout of the building and that the various offices are separated from each other, four accessible fountains are required. This project would provide funding for the purchase and installation of four new accessible fixed high/ low ADA drinking fountains, three on the first floor and one on the second floor. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 16000
9831SFT1 | SIDEWALK / LANDING REPAIR | 9831 | The sidewalks serving the building are in overall good condition, but there are a couple of areas that require repairs. Some areas have cracks that need to be filled and at least one area has created a tripping hazard where one slab has heaved up next to another slab. This project addresses filling cracks and grinding high areas as necessary to remove tripping hazards and maintain the concrete in good condition. This project would also provide a code compliant landing at the exterior door adjacent to the driveway along the east side of the building. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2000
9831ADA2 | ADA PARKING UPGRADE | 9831 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A compliant concrete parking area and passenger loading area are necessary to comply with ADA requirements. The existing accessible parking spaces do not meet current guidelines. This project would provide for a concrete van accessible ADA parking and loading space, a passenger ADA space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 15000
9831ADA1 | ADA PATH OF TRAVEL UPGRADE | 9831 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. An accessible path of travel from the public way to the entrance of the building is necessary to comply with ADA accessibility requirements. This project would provide for repairing the asphalt portion and replacing the concrete walkway. This will require crack fill and seal of the asphalt, regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. 560 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 10000
9831SIT2 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9831 | There are five existing light poles around the site. The lighting fixtures and lamps are the older type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. This project would provide for the installation of 5 solar powered LED exterior light fixtures on the existing poles. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
9831SIT1 | SEAL ASPHALT PAVING | 9831 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 55,000 square feet of asphalt area was used to generate this estimate. | BELROSE OFFICE BUILDING SITE | 9831 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41250
0286ENV2 | PEST CONTROL | 0286 | There are numerous signs throughout this building of insect infestation including ants, bees, cockroaches and crickets. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2500
0286ADA7 | ADA ACCESSIBLE COUNTER | 0286 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The Youth Parole front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement as well as replacing the security glass to maintain a secure entrance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | BELROSE OFFICE BUILDING | 9831 | Admin | PubWorks | B&G | Las Vegas | 1973 | 41075 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 6000
9832SIT1 | SEAL ASPHALT PAVING | 9832 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the test driving area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 275,000 square feet of asphalt area was used to generate this estimate. This project should be implemented concurrently with the Concrete Curb Replacement project. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 206250
0265HVA2 | HVAC REPLACEMENT | 0265 | The existing HVAC system consists of 6 exterior mounted heat pumps combined with 6 interior air handlers. They are not energy efficient and are reaching the end of their expected and useful life. This project would provide for installation of new HVAC equipment and cleaning of the existing duct work and grilles. The estimate includes removal and disposal of the existing HVAC units and all required connections to utilities. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Four to Ten Years | Long-Term Needs | 3 | 36000
9832SIT2 | CONCRETE CURB REPLACEMENT | 9832 | The concrete curbing in the parking lot has been damaged and is failing in many areas. There is extensive cracking, crumbling and failure due to vehicles colliding with the curbs. Some replacements have been done recently, but these areas are already failing as well. Due to the high traffic volume and higher percentage of large commercial vehicles in this parking lot, it is recommended to replace the curbs with a more appropriate system. This project would provide for the installation of concrete curbing with a deeper footing throughout and a high strength concrete mix to ensure a longer life cycle of the new curbing. Removal and disposal of the existing curbing is included in this estimate. This project should be implemented concurrently with the Seal Asphalt Paving project. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0265INT1 | INTERIOR FINISHES | 0265 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27340
3106EXT1 | EXTERIOR FINISHES | 3106 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide funding for repairing, sealing and caulking of the exterior of the structure. Included in the cost is repairing the damaged concrete masonry units (CMU) and sealing and caulking the CMU, flashing, fixtures and all other penetrations. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INSPECTION STATION CANOPY | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 3074 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9832ADA1 | ADA SIGNAGE | 9832 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria including the current parking signs that do not indicate the minimum fine as $250. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2500
0265EXT3 | EXTERIOR FINISHES | 0265 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and sealing and caulking the CMU, windows, flashing, fixtures and all other penetrations. This includes repairing the broken masonry caps on the employee parking sign and the condenser enclosure. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27340
0265ADA3 | ADA SIGNAGE | 0265 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0265ADA2 | ADA RESTROOM UPGRADES | 0265 | The Men's and Women's designated ADA restrooms do not entirely meet the Americans with Disabilities Act (ADA) requirements. Examples of non-compliant items are the faucet handles and lack of under lavatory protection. Also, the ceramic sink in the Men's restroom is cracked. This project would provide funding for replacing the lavatory and countertop system in each restroom to ensure full compliance with accessibility regulations. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 5000
9832SIT3 | FENCE REPAIRS | 9832 | The chain link fence has been damaged and should be repaired immediately. Vagrants have cut a large hole in the fence on the south side of the property and have been entering and exiting through it. This project would provide for removing the damaged section and splicing in a new section of chain link. Further plans to install barbed wire or a similar deterrent can be made by the agency to prevent this from happening in the future. | DMV EXPRESS OFFICE SITE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0265ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0265 | The water fountain in the employee break room does not meet current accessibility requirements. For example, the flow of water from the spout is not parallel to the front of the unit or within the distances provided in the code and at the time of the survey, the knee clearance under the fountain was blocked by a trash can. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV EXPRESS OFFICE | 9832 | MtrVeh | B&G |  | Las Vegas | 1995 | 5468 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 4000
0257ADA1 | EMPLOYEE ADA RESTROOM REPAIRS | 0257 | The employee ADA restroom does not entirely meet the current accessibility requirements. The sign on the wall adjacent to the door is blocked by chairs. A person must be able to approach within 3 inches of the sign without encountering protruding objects. The clear floor space inside the restroom is blocked by storage items which impede on the required turning radius as well as access to the lavatory. This project provides for removing the chairs and storage items in order to maintain the restroom in a compliant status. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 500
0257EXT3 | REPAIR/ REPLACE FASCIA AND SOFFITS | 0257 | The metal fascia and the soffits around the building are weather beaten, peeling, and are showing signs of considerable wear. This project would provide funding to repair the fascia and soffits. Repairs include: replacing if necessary, sanding, scrapping, priming and painting. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
9833ADA1 | ADA SIGNAGE | 9833 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LAS VEGAS CASUAL LABOR SITE | 9833 | ETR | ESD |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 2500
9833SIT2 | CHAIN LINK FENCE REPLACEMENT | 9833 | The chain link perimeter fence does not keep vagrants out and has several areas that are in need of repair. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site and two vehicle gates with hardware. A three wire barbed fence is also recommended to be installed along the top of the chain link fence to prevent vagrants from entering the property. The cost estimate includes demolition and disposal of the existing fence. | LAS VEGAS CASUAL LABOR SITE | 9833 | ETR | ESD |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0257EXT2 | EXTERIOR FINISHES | 0257 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 24000
0257INT2 | INTERIOR FINISHES | 0257 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 12000
0257ENR1 | WINDOW REPLACEMENT | 0257 | The windows are original, single pane construction in a metal frame. There is also a clerestory row of plexiglass windows on two sides of the building. These older windows are drafty and not energy efficient. This project recommends replacing all of the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 glass units and 16 plexiglass units. Removal and disposal of the existing windows is included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0257EXT4 | EXTERIOR DOOR REPLACEMENT | 0257 | Two of the exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the north and south single door assemblies with new metal doors, frames and hardware. The storefront system on the east elevation has been replaced recently. Removal and disposal of the existing doors is included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9833SIT1 | ASPHALT PARKING LOT REPLACEMENT | 9833 | The asphalt parking lots are failing, with significant alligatoring, settling and general deterioration observed. The settling on the south side has caused drainage problems with standing water in the middle of the parking lot. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate as well as perimeter curbing and parking curbs as needed. 18,000 square feet was used to generate this estimate. | LAS VEGAS CASUAL LABOR SITE | 9833 | ETR | ESD |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
0257ADA2 | PUBLIC ADA RESTROOM REMODEL | 0257 | The Men's and Women's designated ADA restrooms in the Job Seeker Room do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 50000
0257EXT5 | HVAC STRUCTURE REPLACEMENT | 0257 | The HVAC units on the roof are surrounded by a wood framed structure. The structure partially protects the equipment from the elements and serves an architectural function by blocking the equipment from view. The wood framing and plywood walls have deteriorated and should be scheduled for replacement. This project would provide for removal and disposal of the existing materials and replacement with a new wood structure. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0257SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0257 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4000
0257PLM1 | WATER HEATER REPLACEMENT | 0257 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. The water heater is located in the attic. It cannot be converted to a gas-fired unit due to limited space and access. Removal and disposal of the existing equipment is included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0257PLM2 | BACKFLOW PREVENTION | 0257 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0257SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0257 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0257SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0257 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 33600
0257ENR2 | LIGHTING UPGRADE | 0257 | The lighting fixtures are the older mercury vapor type in the employee office and fluorescent T-12's in the Job Seeker Room which are not energy efficient. This project will upgrade the mercury vapor lamps to current standards and the T-12 lamps to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0257ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0257 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. | LAS VEGAS CASUAL LABOR OFFICE | 9833 | ETR | ESD |  | Las Vegas | 1975 | 2400 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4000
9835ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9835 | There are approximately seventeen existing light poles around the site. The existing light fixtures are the older high pressure sodium type. These are costly to replace and are not energy efficient. It is recommended to upgrade the fixtures to higher efficiency units with a longer life cycle. This project would provide for the installation of 17 solar powered LED exterior light fixtures. | GRANT SAWYER OFFICE SITE | 9835 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 110500
9835ADA1 | ADA SIGNAGE UPGRADES | 9835 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage in accordance with ADA requirements. This project would provide for purchasing and installing a "NO PARKING" sign at one of the loading zones next to the accessible parking space and replacing a "WHEEL CHAIR" sign with a current directional sign on the east elevation of the building. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | GRANT SAWYER OFFICE SITE | 9835 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 1000
1680EXT2 | EXTERIOR FINISHES | 1680 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing the entire building, repairing the tile and grout as needed, priming and painting the stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes are addressed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 224000
1680INT6 | INTERIOR FINISHES | 1680 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1120000
9835SIT1 | SEAL ASPHALT PAVING | 9835 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 400,000 square feet of asphalt area was used to generate this estimate. | GRANT SAWYER OFFICE SITE | 9835 | Admin | PubWorks | B&G | Las Vegas | 0 |  | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 200000
1680EXT6 | ROOF HATCH REPLACEMENT | 1680 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators on this large and heavy hatch do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 3500
1680ELE1 | VIDEO FEED INSTALLATION | 1680 | When the Governor holds press conferences here, the press personnel does not have a live video feed to hook up to in the parking lot. They must go to the Governors Office in order to connect their media trucks which creates a crowded room with excess wiring and equipment strewn about. Staff recommended utilizing the existing connection near the loading dock and installing a wireless transmitter there which can be accessed throughout the site. This project would provide for installing a transmitter to send a wireless signal from the Governor's Office to the entire site in order to simplify the coordination of the press conferences. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3099EXT1 | EXTERIOR FINISHES | 3099 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GRANT SAWYER GARAGE/PUMP HOUSE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 2462 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12310
3099PLM1 | SUMP PUMP REPLACEMENT | 3099 | The existing sump pump in the Fire Pump Room is undersized and should be scheduled for replacement. The State's property insurance company has recommended a larger pump. This project provides for replacing the existing 1/3 horsepower pump with a 1/2 horsepower pump. Removal and disposal of the existing equipment is included in the estimate. | GRANT SAWYER GARAGE/PUMP HOUSE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 2462 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
1680HVA4 | HVAC UPGRADE | 1680 | The HVAC system in the building is approaching the end of its expected life and should be scheduled for replacement. The cooling towers have already been replaced. The boilers, chillers, air handlers, control system, water treatment equipment and piping are all original to the building. Most equipment has an expected life of about 20-25 years. Also, the piping for the HVAC water lines is steel that is crimped at the connections. This type of piping is prone to leaking and should be replaced. The existing system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of new HVAC equipment throughout the building and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Four to Ten Years | Long-Term Needs | 3 | 6720000
1680SEC1 | SECURITY SYSTEM UPGRADE | 1680 | The site and building security system is outdated and there is at least one area where the system is vulnerable. Since the Gaming Control Board, Governor's Office and other highly secure offices are located here, it is recommended to upgrade the system in the next 2-3 years. This project addresses replacement of the cameras, door sensors and alarms including new digital recording equipment with sufficient storage capacity. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560000
1680EXT7 | EXTERIOR DOOR REPLACEMENT | 1680 | The exterior metal door at the loading dock is damaged from age and general wear and tear and has reached the end of its expected life. Carts and hand trucks have caused most of the damage during normal deliveries to the building. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
1680PLM2 | WATER HEATER REPLACEMENT | 1680 | Three of the four 100 gallon gas-fired water heaters in the boiler room have been replaced recently. The average life span of a water heater is eight to ten years. With the passage of time and constant use, the older unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. The other three water heaters in the room have been replaced recently, but do not have seismic straps installed. This project includes seismic straps for all four water heaters. Removal and disposal of the existing equipment is included in this estimate. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1680SFT4 | BOILER ROOM EMERGENCY SHUTOFF INSTALLATION | 1680 | The existing boiler room has no emergency shut off switch as required by code for boilers with a fuel input of greater than 2,500,000 btu/h. Each of these boilers has a maximum input of 3,500,000 btu/h. This project would install a mushroom switch just outside the boiler room door to shut down all power to both boilers in an emergency. It is also recommended to replace the labels on all of the shut off switches in the building including those for the chillers and exhaust fans. The 2006 Uniform Mechanical Code Table 10-3 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 2500
1680INT3 | RELOCATE DATA/ COM EQUIPEMENT | 1680 | The equipment in the Data/ Com Room on the first floor is subject to damage by leaking water pipes above it and should be relocated. Equipment in Room 1038 includes computer servers, spare computer parts, telephone equipment, data lines and other related items. Above this equipment, near the ceiling are several different types of pipes containing water including fire suppression system pipes, sewer pipes and water supply pipes for the HVAC equipment. All of these water pipes are susceptible to leaking from normal aging or a natural event such as an earthquake. It is recommended to relocate the sensitive data and communications equipment to a different room which does not have water pipes in it. The estimate includes reconnecting all equipment in the new location. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 15000
1680SFT1 | LOADING DOCK LIFT INSTALLATION | 1680 | The existing loading dock does not accommodate smaller delivery trucks requiring personnel to lift equipment onto the loading dock. The loading dock is also missing a ramp which would provide for some of the smaller deliveries to be wheeled up. Gaming Commission deliveries must be brought into the building through the building's rear personnel door which poses a security risk. This project would install a powered 6' x 8' loading dock lift and a concrete ramp for smaller deliveries in place of the damaged stairs. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 22500
1680HVA2 | KITCHEN MAKE-UP AIR UNIT INSTALLATION | 1680 | The exhaust hoods in the kitchen currently take air from the building and the building is balanced for this exhaust. Changes in building operation require the HVAC system to operate 24 hours a day yet the kitchen closes down over night. This creates an unbalanced air delivery system. This project would install a dedicated make-up air system for the kitchen to compensate for the hoods and rebalance the buildings HVAC system. The estimate is based on a 40,000 CFM make-up air unit. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29900
1680SFT3 | INSTALL SAFETY CAGE ON FIRE PROTECTION RISER | 1680 | The fire riser on the loading dock provides fire suppression to the Gaming Control Board computer room. The riser is exposed to delivery trucks and other vehicles using the loading dock which could damage the equipment. This poses a serious risk to the sensitive and highly secure information with regards to the Gaming Control Board. This project would install bollards and a chain link fence cage around the riser to protect it from impact damage and tampering. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
1680SFT5 | SIGNAGE UPGRADES | 1680 | The interior of the building is lacking evacuation diagrams and directional signage in most areas. Evacuation plans are required by the National Fire Protection Association for buildings with an occupancy greater than 500. Employees and visitors are often confused by the existing directional signage and labeling of the six story structure. Restrooms, stairs and elevators are difficult to find with the existing lack of signage. This project would provide additional evacuation diagrams throughout the building and a comprehensive upgrade to the directional signage for visitors and employees. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 15000
1680HVA7 | PROVIDE SEPARATE MAIL ROOM HVAC | 1680 | Mail rooms have become a security issue in recent years and Homeland Security recommends separating mail room HVAC systems from the remainder of the building systems. This project would provide a separate system for the mail room with an emergency shut off switch. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1680SFT8 | INTERIOR DOOR REPAIRS | 1680 | Numerous locks, closers, weather strips, smoke seals, and magnetic door holders need repair and adjustment. The magnetic door holders and automatic closers are all failing. This compromises the fire protection system in the building and should be addressed immediately. This project provides funding to repair, replace, or adjust door hardware throughout the facility. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Immediate to Two Years | Currently Critical | 1 | 40000
1680SFT7 | REPAIR PARKING LOT LIGHT BASES | 1680 | Several light poles in the parking lot have deteriorated concrete bases. This project would replace the cap concrete and seal it against weather deterioration. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1680EXT9 | ROOF REPLACEMENT | 1680 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. Exterior wall tiles have fallen on the roof membrane resulting in a large number of patches in the membrane. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1995. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 12/08/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/27/2011. | GRANT SAWYER STATE OFFICE | 9835 | Admin | PubWorks | B&G | Las Vegas | 1995 | 224000 | 2017-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2565EXT1 | EXTERIOR FINISHES | 2565 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will protect the building envelope and is recommended on a cyclical basis based on environmental conditions. | DETR LAS VEGAS OFFICE | 9837 | ETR | ETR |  | Las Vegas | 2006 | 59874 | 2013-06-05 | Four to Ten Years | Long-Term Needs | 3 | 179622
9837SIT1 | CRACK FILL / SEAL ASPHALT PAVING | 9837 | The existing asphalt concrete paving on site is in good condition. This project would provide for crack filling as needed and sealing and striping the pavement in the next three to four years. This project should be completed on a cyclical basis based on environmental conditions and use. | DETR LAS VEGAS OFFICE SITE | 9837 | ETR | ETR |  | Las Vegas | 0 |  | 2013-06-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46300
2565INT1 | INTERIOR FINISHES | 2565 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to six years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DETR LAS VEGAS OFFICE | 9837 | ETR | ETR |  | Las Vegas | 2006 | 59874 | 2013-06-05 | Four to Ten Years | Long-Term Needs | 3 | 299370
2470SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2470 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 37800
2470INT1 | INTERIOR FINISHES | 2470 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
2470ENR1 | HVAC EQUIPMENT REPLACEMENT | 2470 | The two HVAC roof top AC units serving the Vehicle Storage Garage are over 20 years old. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
9838SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9838 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and vehicle storage areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 32,000 square feet of asphalt area was used to generate this estimate. | LAUGHLIN WILDLIFE FIELD OFFICE SITE | 9838 | Wildlife |  |  | Laughlin | 0 |  | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
2470EXT1 | EXTERIOR FINISHES | 2470 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting of the EIFS and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAUGHLIN WILDLIFE FIELD OFFICE | 9838 | Wildlife |  |  | Laughlin | 2004 | 2700 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
9841SIT2 | SEAL & STRIPE PARKING LOT | 9841 | The existing paved area around the building is in good condition. This project would provide for striping some designated parking spaces which should be done within the next year and sealing the new AC paving in the next 5 years The striping should be coordinated with the ADA parking/striping project. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY SITE | 9841 | Military | NNG |  | Ely | 0 |  | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0676INT3 | INTERIOR FINISHES | 0676 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next four-five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Four to Ten Years | Long-Term Needs | 3 | 29631
0676EXT2 | EXTERIOR FINISHES | 0676 | The exterior finish is the building's first defense against weather elements. It is important to maintain the finish, weather resistance, and appearance of the building. Moisture and weather intrusion into a building causes indoor air quality issues and premature failure of the building. This project includes items to protect the exterior building envelope other than the roof. This can include re-pointing of mortar joints in areas where necessary or damaged and sealing the building exterior. This sealing can include scraping the paint, applying primer and painting all of the CMU walls and window frames, or reapplying any other type of a building exterior treatment. This project also includes repairing or replacing any flashing, fixtures, and other penetrations or transitions to maintain the building in a good, weather tight condition. This project should occur on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Four to Ten Years | Long-Term Needs | 3 | 49385
9841ADA1 | ADA PARKING | 9841 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This project provides for a van accessible space and an adjacent loading zone in the existing rear parking lot. The accessible route of travel and public entrance to the Armory will be from a designated rear door. Project includes parking stops, signage, and striping. This project should be done in conjunction with the slurry sealing and any other projected related to the parking area and accessibility. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY SITE | 9841 | Military | NNG |  | Ely | 0 |  | 2017-11-08 | Immediate to Two Years | Currently Critical | 1 | 1500
0676PLM1 | FLOOR COVERING REPLACEMENT | 0676 | The floor coverings in this building are in generally poor condition and have reached the end of their serviceable life. At the present time, most of the floor surfaces are 12"x12" vinyl floor tile with only a minimal area of concrete. The majority of the tiles are separating, cracked and loose. This project would provide for the removal, disposal and installation of new 12"x12" vinyl tile in the office areas, corridor and conference rooms. The vinyl floor tiles have been determined to contain asbestos containing material (ACM) and a figure of $4.25/SF @3,500 SF for abatement is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/16/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35875
0676ADA1 | ADA SIGNAGE | 0676 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Immediate to Two Years | Currently Critical | 1 | 1800
0676INT2 | INTERIOR FINISHES | 0676 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Four to Ten Years | Long-Term Needs | 3 | 52020
0676ENR3 | WINDOW REPLACEMENT | 0676 | The windows in the Drill Hall are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0676EXT3 | EXTERIOR DOOR REPLACEMENT | 0676 | The existing exterior metal doors and frame for the Vault Storage Room are damaged and do not provide the necessary security. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of the solid metal doors, frame and security hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | ELY ARMORY | 9841 | Military | NNG |  | Ely | 1959 | 9877 | 2017-11-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2705HVA1 | BOILER INSPECTION | 2705 | The building has two boiler systems that have not been inspected. Per NAC 455C.150 Inspection for operating permit; Internal inspection: an inspection for an operating permit must be an internal inspection if required by the Enforcement Section. NAC 455C.156 Frequency and scope of inspections; authority to require preparation for inspection; authorization to change interval between inspections (4): a lined potable water heater must have an external inspection at least once every 2 years. It is recommended to have all boiler systems inspected per NAC 455. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 1000
2705SFT0 | STORAGE REMOVAL | 2705 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, "Storage shall be maintained 2 feet or more below the ceiling in nonsprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings." This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 1000
2705PLM4 | WATER HEATER REPLACEMENT | 2705 | There is a 100 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 5000
3217SFT2 | STORAGE REMOVAL | 3217 | Per IFC 2012 315.3.3 combustible material shall not be stored in boiler rooms, mechanical rooms or electrical equipment rooms. It is recommended that all combustible materials be removed from boiler rooms, mechanical rooms or electrical equipment rooms within 1 year. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Immediate to Two Years | Currently Critical | 1 | 1000
3217EXT2 | EXTERIOR FINISHES | 3217 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the expansion joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 402130
2705INT1 | INTERIOR FINISHES | 2705 | The interior finishes are in good condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 787740
2705EXT2 | EXTERIOR FINISHES | 2705 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 787740
2705INT2 | RESTROOM FIXTURE REPLACEMENT | 2705 | It was observed on the date of inspection May 13, 2015 that the mirror is showing moisture infiltration and signs of deterioration. The sink is losing its enamel. The existing restroom fixtures are original to the building. The mirror and sink are worn and damaged and should be scheduled for replacement within 2-3 years. This project recommends the replacement of the existing mirror and sink. | LAS VEGAS READINESS CENTER | 9842 | Military | NNG |  | Las Vegas | 2007 | 78774 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9842SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9842 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 245,100 square feet of asphalt area was used to generate this estimate. | ANTHONY COMETA COMPLEX SITE | 9842 | Military | NNG |  | Las Vegas | 2007 |  | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245100
3217INT2 | INTERIOR FINISHES | 3217 | The interior finishes are in good condition. It is recommended to paint the interior walls and ceilings at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 402130
3218EXT1 | EXTERIOR FINISHES | 3218 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZMAT BUILDING | 9842 | Military | NNG |  | Las Vegas | 2013 | 960 | 2015-05-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
3640EXT1 | EXTERIOR FINISHES | 3640 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the steel structure. Included in the cost is painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MV PARKING STRUCTURE - SOUTH | 9842 | Military | NNG |  | Las Vegas | 2013 | 9075 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 18150
3219EXT1 | EXTERIOR FINISHES | 3219 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the painting of the steel structure. Included in the cost is painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MV PARKING STRUCTURE - NORTH | 9842 | Military | NNG |  | Las Vegas | 2013 | 8250 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 18150
3111EXT1 | EXTERIOR FINISHES | 3111 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 8-9 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MILITARY STORAGE BUILDING | 9842 | Military | NNG |  | Las Vegas | 2008 | 11200 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 22400
3217INT1 | FLOORING MAINTENANCE | 3217 | It is important to maintain the interior finish of the concrete floor. It is recommended that the concrete be stripped and re-sealed in order to extend its useful life. This project would provide for stripping the concrete and applying an Epoxy concrete paint in the next 5-6 years. | FIELD MAINTENANCE SHOP (FMS #7) | 9842 | Military | NNG |  | Las Vegas | 2013 | 40213 | 2015-05-13 | Four to Ten Years | Long-Term Needs | 3 | 261384
0399ADA4 | ADA RESTROOM UPGRADE | 0399 | The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 30000
0399ADA5 | ADA SIGNAGE | 0399 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 1500
0399EXT3 | EXTERIOR FINISHES | 0399 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is scraping, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0399INT1 | INTERIOR FINISHES | 0399 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the offices and the B&G shop be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
0399ELE2 | EXTERIOR OUTLET REPLACEMENT | 0399 | There is an electrical outlet on the exterior of the building that does not meet code. This outlet should be changed to a GFCI type outlet per the 2005 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof cover. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 300
9845SIT4 | MOTORIZED GATE INSTALLATION | 9845 | The site has a perimeter fence that has vehicle access gates off Galletti and Barnett. They are mechanically operated, have been problematic, and are difficult to open and close. This project recommends the gates be upgraded to a motorized track system that can handle heavy equipment traffic. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0399SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0399 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 15000
0399EXT4 | LOADING DOCK REPAIRS | 0399 | The main loading dock on the west side of the building is damaged and due for major repairs. The concrete is cracked and failing to the point of exposing the reinforcing steel and jeopardizing the integrity of the structure. The stairs from the parking lot also have significant deterioration and require complete replacement. This project would provide for repairs to the loading dock including removing and replacing concrete, replacement of the stairs and rails and refurbishing the lifts. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 125000
9845ADA2 | ADA SIGNAGE | 9845 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 1250
9845ADA1 | ADA PARKING UPGRADE | 9845 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking space up to code including removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 2500
0399INT3 | RESTROOM REMODEL - B&G SHOP | 0399 | The restroom in the B&G Shop is in overall poor condition and does not meet code for safety. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. Section 1008.1 of the 2006 International Building Code describes the requirements for landings at doors. There is no proper landing at the door. This project would provide for a complete remodel of the restroom and installation of a compliant landing. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0399ENR2 | WINDOW REPLACEMENT | 0399 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
0399ENR1 | LIGHTING UPGRADE | 0399 | The existing interior and exterior lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. T-5 High Output high bay lamps with electronic ballasts and compact fluorescent lights (CFL's) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86904
9845SIT1 | SLURRY SEAL ASPHALT PAVING | 9845 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide. Striping is included in this estimate. The ASPHALT PAVING project should be done prior to this long term cyclical maintenance work. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 120,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2011-04-12 | Four to Ten Years | Long-Term Needs | 3 | 90000
0399ENV1 | 4" BACKFLOW PREVENTION | 0399 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a 4" double check valve or reduced pressure principle backflow preventer for the main domestic water line. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 25000
9845SIT3 | DRAINAGE UPGRADES | 9845 | The site has several areas with inadequate drainage due to deteriorated asphalt and clogged drains. The standing water causes premature deterioration of the paving and other site improvements. This project would provide for drainage upgrades which may include pumping existing drains, installing new french drains and re-grading to ensure proper water flows. This project should be implemented concurrently with the ASPHALT PAVING REPLACEMENT project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 35000
0399STR2 | STRUCTURAL ASSESSMENT, STORAGE AREA | 0399 | A storage area has been constructed over the B&G office, accessed via non-complying stairs in the shop. There is no record of a CIP project for this work or of any structural evaluations having been conducted. This project recommends that a licensed engineer perform a structural investigation to assess the load bearing capacity of the structure. Future projects would be based on this report. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0399EXT2 | OVERHEAD DOOR REPLACEMENTS | 0399 | There are six overhead coiling doors throughout the facility in various stages of disrepair. Three of the doors are damaged and do not function properly. Exposure, wind and general wear and tear have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. The other three doors are in need of new weather seals to minimize air and debris infiltration. This project would provide for the removal and disposal of the doors and installing new weather seals. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0399ENV2 | 3" BACKFLOW PREVENTION | 0399 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a 3" double check valve or reduced pressure principle backflow preventer for the automatic fire suppression system. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 20000
0399HVA2 | HVAC UPGRADES, B&G SHOP | 0399 | The B&G shop is located at the north west corner of the building. An office was built in this area that has no ventilation as required by Section 1203 of the 2006 International Building Code. This project would provide for the purchase and installation of a wall mounted heat pump to provide cooling, heating and ventilation in the office area of the shop including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 3000
9845SIT2 | ASPHALT PAVING REPLACEMENT | 9845 | The asphalt around the building has failed, with significant alligatoring, settling, cracks and complete erosion. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate. 120,000 square feet was used to generate this estimate. This project should be implemented concurrently with the DRAINAGE UPGRADES project. | RENO PURCHASING WAREHOUSE SITE | 9845 | Admin | PubWorks | B&G | Reno | 0 |  | 2011-04-12 | Immediate to Two Years | Currently Critical | 1 | 1200000
0399HVA3 | BOILER REPLACEMENT | 0399 | The hot water boiler servicing the building was installed almost 20 years ago and should be scheduled for replacement. The life expectancy of this unit is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this older equipment. The controls and mixing valves should be replaced for the same reasons. There are currently several areas of the building which have stand alone electric heaters. It is recommended to remove those units and replace them with fan coil units serviced by the boiler. This project would provide for the removal and disposal of the existing boiler, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 1,700 MBH maximum output hot water boiler, associated equipment and new equipment to replace the electric heaters. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2011. | RENO PURCHASING WAREHOUSE | 9845 | Admin | PubWorks | B&G | Reno | 1960 | 58428 | 2011-04-12 | Four to Ten Years | Long-Term Needs | 3 | 85000
3098EXT1 | EXTERIOR FINISHES | 3098 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9845 | Admin | PubWorks | B&G | Reno | 2000 | 1250 | 2011-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
2483SEC1 | INSTALL FIRE ALARM CONTROL | 2483 | The building currently has only an exterior bell for fire notification. Due to the remote location, there is concern that in the event of a fire, no one will hear the bell . This project would install a fire alarm panel with dial-up notification to the local responder. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Immediate to Two Years | Currently Critical | 1 | 8500
2483HVA1 | SYSTEM TUNE-UP | 2483 | The HVAC system shows evidence of considerable dirt in the ductwork and it is reported that the thermostat is out of calibration. This project would generally clean-up the system, tighten the spaces around the furnace filters, and recalibrate or replace the thermostat. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Four to Ten Years | Long-Term Needs | 3 | 2500
2483EXT1 | REPLACE ROOF | 2483 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within the next two to four years to be consistent with the roofing program and the end of the warranty period. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28810
2483EXT2 | INSTALL ROOF ACCESS | 2483 | At the time of the survey, there was no built-in roof access. This project would install a roof access hatch and ladder at the same time the roof is replaced. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2483EXT3 | TREATMENT OF EXTERIOR FINISHES | 2483 | At the time of the survey, the exterior block was beginning to deteriorate due to frost damage. It is important to maintain the finish, weather resistance and appearance of the building. This project includes items to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and sealant and gaskets in and around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
2483INT1 | REPLACE VINYL FLOORING | 2483 | The flooring finishes in this building are reaching the end of their useful life. It is recommended that the flooring and cove base in the building be replaced. This project includes minor repair of sub floor or surface preparation prior to installing new floor materials. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Four to Ten Years | Long-Term Needs | 3 | 1575
2483PLM1 | INSTALL BACKFLOW PREVENTER COVER | 2483 | The landscape irrigation system backflow preventer has recently been replaced due to freezing. This project would install an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | RENO MOTOR POOL | 9846 | Admin | PubWorks | B&G | Reno | 1990 | 2155 | 2004-10-19 | Immediate to Two Years | Currently Critical | 1 | 7500
1473ADA4 | ADA RESTROOM UPGRADE | 1473 | The building does not have fully accessible restrooms and do not meet the ADA requirements. A retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 30000
1473SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1473 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 4000
1473HVA1 | EXHAUST FAN REPLACEMENT | 1473 | The exhaust fans in the restrooms were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1473INT2 | JANITORS CLOSET REPAIRS | 1473 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
9847SIT1 | SITE DRAINAGE UPGRADES | 9847 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | WASHOE CASUAL LABOR OFFICE SITE | 9847 | ETR | ESD |  | Sparks | 0 |  | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1473INT1 | INTERIOR FINISHES | 1473 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1473ENR2 | LIGHTING UPGRADE | 1473 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
1473EXT2 | EXTERIOR FINISHES | 1473 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Four to Ten Years | Long-Term Needs | 3 | 24000
1473PLM1 | WATER HEATER REPLACEMENT | 1473 | There are two natural gas fired water heaters in the building. One is a 50 gallon and the other is a 40 gallon water heater. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that the new natural gas fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
9847ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9847 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | WASHOE CASUAL LABOR OFFICE SITE | 9847 | ETR | ESD |  | Sparks | 0 |  | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 30000
1473SFT3 | EGRESS LIGHTING UPGRADE | 1473 | The emergency egress lighting is insufficient. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Immediate to Two Years | Currently Critical | 1 | 1200
1473ENR3 | EXTERIOR LIGHTING REPLACEMENT | 1473 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1473EXT3 | WINDOW REPLACEMENT | 1473 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. | WASHOE CASUAL LABOR OFFICE | 9847 | ETR | ESD |  | Sparks | 1985 | 2400 | 2016-10-26 | Four to Ten Years | Long-Term Needs | 3 | 10500
2028ADA1 | ADA SIGNAGE | 2028 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/12/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2011. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 1000
2028SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2028 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 10500
2028SFT7 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2028 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 4000
2028PLM1 | WATER HEATER INSTALLATION | 2028 | There is a 19 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new natural gas water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2028SFT5 | ELECTRICAL OUTLET COVERS | 2028 | The existing floor mounted electrical outlets present a safety hazard. Steam cleaning or shampooing the carpet can introduce moisture into the outlet. Also, being face up, dirt, lint or other items can accumulate in the outlets causing a short or possible fire hazard. This project would provide for replacing the faceplates of the floor mounted outlets with new floor outlet box cover plates. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 500
9850SIT2 | SLURRY SEAL ASPHALT PAVING | 9850 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving in the parking lot. Striping and signage including updated ADA parking requirements are included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 15,000 square feet of asphalt area was used to generate this estimate. The pavement maintenance is currently Carson City's responsibility even though the State owns the property. This project is for information only. | MUSEUM ADMINISTRATIVE SITE | 9850 | CultAffr | M&H | Museums | Carson City | 1910 |  | 2011-12-15 | Four to Ten Years | Long-Term Needs | 3 | 15000
2028SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2028 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 6000
2028SFT1 | SEISMIC RETROFIT | 2028 | This building is a historic wood framed structure on an old concrete foundation consisting of a perimeter stem wall and interior post and piers. The concrete in the stem wall and piers is crumbling and cracked and the wood framing is not properly anchored into the concrete foundation. Additional bracing is also required for the roof and wall framing to stabilize the structure in the event of an earthquake. It is recommended to design and construct a seismic retrofit on the structure to meet current life safety codes. The estimate is for the construction costs only. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 45000
2028INT1 | INTERIOR FINISHES | 2028 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2028SFT6 | FIRE EXTINGUISHER INSTALLATION | 2028 | NAC 477.283.1(L) states that "Portable fire extinguishers must be installed in all group A, B, E, F, H, I, M, R-1, R-2, R-4 and S occupancies. No exceptions will apply.". There are no fire extinguishers in the building. This project would provide for the purchase and installation of two fire extinguishers according to NAC 477.405 and any other requirements of the Fire Marshall. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 500
9850SIT1 | PIPE BOLLARD INSTALLATION | 9850 | To the north of the building, there is a parking lot for the office building next door. There have been several incidents of vehicles colliding with the building and damaging the siding and possibly the structure. This area is in need of pipe bollards to protect the building. This project would provide funding for 4 eight inch diameter pipe bollards to be located near the north elevation of the building. | MUSEUM ADMINISTRATIVE SITE | 9850 | CultAffr | M&H | Museums | Carson City | 1910 |  | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 2000
2028ENR3 | ATTIC INSULATION REPLACEMENT | 2028 | The insulation in the attic is a cellulose blown-in type that is old and most likely does not provide an adequate insulation value. This project would provide for installing a new layer of insulation on top of the existing insulation to ensure at least an R-38 insulation value. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2028EXT2 | EXTERIOR FINISHES | 2028 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the metal siding and caulking of the siding, windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2028SFT4 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2028 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | MUSEUM ADMINISTRATIVE OFFICE (VACANT) | 9850 | CultAffr | M&H | Museums | Carson City | 1942 | 1656 | 2011-12-15 | Immediate to Two Years | Currently Critical | 1 | 1500
0898EXT1 | REPLACE EXTERIOR DOORS | 0898 | The east and west exterior metal doors are damaged from heavy use and the hardware and weather stripping are showing signs of wear. This project would provide for two new metal door assemblies including hardware. Painting and removal / disposal of existing door assemblies is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5400
9851SIT1 | SLURRY SEAL PAVING | 9851 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 4- 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 40,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0898EXT2 | EXTERIOR FINISHES | 0898 | It is important to maintain the finish, weather resistance and appearance of the building. This project includes items to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes to the CMU, and sealant and gaskets in and around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55000
9851EXT1 | RELOCATE IRRIGATION SYSTEM | 9851 | The irrigation system is currently wetting the north and south sides of the building and is causing damage to the concrete masonry units (CMU). This may lead to water infiltration into the building. This project would relocate the sprinklers and lawn away from the building and install 36' wide mow strip next to the building along the north and south sides of the building where the lawn abuts the CMU. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0898ADA1 | INSTALL ADA SIGNAGE | 0898 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0898SFT1 | INSTALL GFCI OUTLETS | 0898 | There is one GFCI duplex outlet in a restroom that is broken and two more duplex outlets that need to be GFCI per the 2005 NEC. This project would provide for the installation of three GFCI duplex outlets in the restrooms. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Immediate to Two Years | Currently Critical | 1 | 150
9851SIT2 | TREE REMOVAL | 9851 | There is a large tree on the south side of the building which has shallow roots that may cause damage to the foundation of the building as it continues to grow. This project would provide for the removal of the tree to prevent damage to the building's foundation. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
9851SIT3 | REPLACE DAMAGED CONCRETE WALKWAYS | 9851 | The concrete walkways from the parking lot to the main entrance and the concrete walk along the east side of the building are damaged from freeze / thaw cycles and ice melting chemicals. This project would provide for the removal and replacement of the concrete walkway including disposal of the existing concrete. 400 square feet of concrete was used to generate this estimate. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0898ENR1 | REPLACE WINDOWS | 0898 | The existing dual pane fixed windows are original to the building and are showing signs of failure. Some of the seals have failed and is allowing moisture in between the glazing panels. These old units are no longer energy efficient and should be scheduled for replacement. This project would provide for 34 new energy efficient dual pane window units including frames. Removal and disposal of the old units are included in this estimate. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57800
0898EXT3 | REPLACE ROOF | 0898 | The single-ply roof on this building was in good condition at the time of the survey. This existing roof was installed in about 2000. The statewide roofing program estimates the useful life of an average roof at 20 years. The 15 year roof warranty expires at the end of the this time frame. This building should be schedules for replacement in the next nine years to be consistent with the statewide roofing program guidelines and the warranty period. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 110000
0898EXT4 | REPAIR ROOF SCUPPER DOWN SPOUTS | 0898 | The existing down spouts at the roof scupper locations terminate right at grade and / or were missing the last section. The current configuration encourages water to pool up beside the building foundation and CMU walls. This project would provide for repair of the existing down spouts and extend all of them to a drywell away from the building. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0898INT4 | PAINT INTERIOR FINISHES | 0898 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/20/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/01/2011. | DPS TRAINING FACILITY | 9851 | PubSafe | NHP |  | Carson City | 1985 | 11000 | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 55000
9851SIT4 | PAINT LIGHT POLES | 9851 | There are two light poles in the parking area that are in need of painting. This project would provide for painting of the two light poles including sanding and prep as required. | DPS TRAINING FACILITY SITE | 9851 | PubSafe | NHP |  | Carson City | 0 |  | 2011-12-01 | Four to Ten Years | Long-Term Needs | 3 | 200
9852SIT2 | DRAINAGE / LANDSCAPE IMPROVEMENTS | 9852 | The west side of the building has some areas in need of drainage improvements where the roof drainage down spouts terminate at grade. This project would provide for down spout extensions to a gravel drywell capable of handling runoff from rain and snow melt. This project also addresses the recommended removal of the planter areas on the north side of the facility as the exterior grade is at the same level as the floor and glazing panels. | MARJORIE RUSSELL RESEARCH CENTER SITE | 9852 | CultAffr | M&H | Museums | Carson City | 1968 |  | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9852SIT1 | ASPHALT CONCRETE PAVING REHABILITATION | 9852 | The existing asphalt concrete paving is in poor shape. There are large cracks and areas of alligatoring and is showing signs of failure. This project would provide for the removal and replacement of AC paving and sealing of the entire paved surface. Also included is ADA accessible parking, striping, signage and wheel stops. 30,000 square feet was used to generate this estimate. This project should be implemented within the next two years. | MARJORIE RUSSELL RESEARCH CENTER SITE | 9852 | CultAffr | M&H | Museums | Carson City | 1968 |  | 2013-02-28 | Immediate to Two Years | Currently Critical | 1 | 120000
0208HVA2 | EXHAUST HOOD INSTALLATION | 0208 | The building contains an electric stove top in the kitchen area. The 2012 Uniform Mechanical code requires an exhaust hood to be installed. This project would provide for the purchase and installation of exhaust hood including the required ducting to the exterior of building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006 . It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0208PLM1 | REPLACE WATER HEATER | 0208 | The water heater tank is showing signs of wear and deterioration. It appears this appliance is original to the building and has reached the end of its expected life. This project would provide for the purchase and installation of a new 75 gallon gas fired water heater tank including seismic bracing and drain pan. Removal and disposal of the existing tank is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0208SFT3 | JANITOR CLOSET WALL PROTECTION | 0208 | The mop sink in the Janitor's Closet is mounted adjacent to gypsum board that is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0208EXT2 | REPLACE GUTTERS AND DOWNSPOUTS | 0208 | The building's gutters have been damaged and show wear and tear from environmental conditions. Many are leaking. In several locations, downspouts have been damaged or are missing. This project would provide for the purchase and installation of seamless gutters and down spouts to divert the water away from the building and building entrances and exits. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Four to Ten Years | Long-Term Needs | 3 | 5000
0208SIT2 | REMOVE PLANTERS | 0208 | This building has planters across the front of the building that extend up onto the exterior wall. This practice promotes water infiltration through the side of the building and has been known to cause mold growth along the exterior walls of buildings. This project recommends that the planters be removed as soon as feasible and replaced with xeriscaping. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Immediate to Two Years | Currently Critical | 1 | 2000
0208HVA1 | HVAC SYSTEM REPLACEMENT | 0208 | The three HVAC roof top units are over 20+ years old. They are not energy efficient, need constant repairs and have reached the end of their expected and useful life. This project would provide for installation of three new HVAC packaged units and cleaning of the existing duct work. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
0208EXT3 | EXTERIOR FINISHES | 0208 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finishes on the building is starting to peel and bluster. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will protect the building envelope. This project would not be required if the exterior energy retrofit project is implemented. This project should be completed in the next two years. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0208INT1 | REPLACE COUNTERTOPS | 0208 | The kitchen countertops are plastic laminate and original to the building. Age and constant use have contributed to the deterioration. The laminate is starting to separate from the substrate. This project would provide for the removal and installation of new plastic laminate countertops. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0208ENR1 | EXTERIOR ENERGY RETROFIT | 0208 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation and finish system (EIFS) over the CMU, replacing the storefront window systems and doors with a dual pane insulated storefront window system and removing and replacing the windows in the rear of the building. This work will make the building more energy efficient. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 72000
0208INT2 | INTERIOR PAINTING | 0208 | The interior finishes on the walls are in fair to poor condition. The ceilings show minor water stains from past water leaks. This project would provide for the painting of the interior walls and ceiling. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be completed in the next two years. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0208INT3 | REPLACE CABINETS | 0208 | The wood cabinets located in warehouse are used to store and protects artifacts. These cabinets are in poor shape, prone to fire and water damaged, the plywood is falling apart, doors do not close properly and the artifacts are subject to the environmental elements. Poor-quality storage enclosures accelerate the deterioration of the materials they are intended to protect. This project would provide for the purchase of 30 steel cabinets which will provide a stable environment for archived and stored items. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
0208ADA3 | INSTALL LEVER DOOR HARDWARE | 0208 | The existing doors in this facility have locking knob-type door hardware and do not meet the requirements for ADA accessibility. ICC/ANSI A117.1-12009 section 404.2.7 requires door handles to have a shape that is easy to grasp with one hand and does not require tight grasping, pinching or twisting of the wrist to operate. This project would provide for the purchase and installation of lever action hardware to be placed on all the interior doors. Typical of 5 doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Immediate to Two Years | Currently Critical | 1 | 1500
0208INT4 | WAREHOUSE FLOOR FINISH | 0208 | The warehouse concrete floor area is painted and/or stained and has floor mounted electrical duplex outlets throughout. The painted and/or stained floor in the warehouse is showing signs of wear. The concrete area around the floor mounted electrical outlets has been chipped away causing a tripping hazard. This project would provide for patching the concrete around the electrical outlets and the painting of the floor surface with a paint designed for use on concrete. Included in the estimate is prep work as needed. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0208SFT4 | SEISMIC GAS SHUT OFF VALVE | 0208 | Agreements reached between the Nevada Risk Management Office and the State of Nevada's Insurance Underwriter require Seismic Gas Shutoff Valves (SGSV's) on all gas services to all State buildings. This project would install a SGSV to the gas line serving the building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/28/2013. | MARJORIE RUSSELL RESEARCH CENTER | 9852 | CultAffr | M&H | Museums | Carson City | 1968 | 6000 | 2013-02-28 | Immediate to Two Years | Currently Critical | 1 | 3000
0398SIT1 | REPAIR AND RESEAL ASPHALT PARKING AREAS | 0398 | The existing paving is in fair condition. Climate and constant use will accelerate deterioration. For proper maintenance it is recommended the entire parking area and driveway be resealed. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0398EXT5 | TREATMENT OF EXTERIOR FINISHES | 0398 | It is important to maintain the finish, weather resistance and appearance of the building. This project includes items to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and sealant and gaskets in and around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 54110
0398ENR1 | INSTALL LIGHTING CONTROL | 0398 | The existing entry lights do not shut off during daylight hours. This project would repair an existing or install a new photocell control for the lights. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 500
0398SFT1 | RELOCATE BICYCLE RACK | 0398 | The existing bicycle rack is immediately adjacent to the building gas service. The service has a seismic gas shutoff valve to protect the facility from gas leakage after an earthquake. These valves are sensitive to vibration and impact and there is the possibility that personnel using the bicycle rack can trip the valve and cause a nuisance shut down of gas to the building. This project would relocate the bicycle rack to the East side of the building. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 550
0398EXT4 | INSTALL DOCK BUMPERS AND LIGHTING | 0398 | The loading dock does not have bumpers to protect the building from impact. This project would install rubber bumpers and a loading dock light. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0398EXT3 | REPLACE SIDE WALKS | 0398 | The existing concrete side walks are cracked and present a trip hazard to pedestrians. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 5800
0398INT2 | REPLACE CEILING TILE | 0398 | Ceiling tile in the computer room and in the first floor hall is damaged, dirty, or mismatched. This project would replace the tile in the computer room with a smooth face tile not subject to holding dirt. The project would also replace tile in the first floor hall to provide matching tile throughout. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 3500
0398EXT2 | INSTALL RIGID INSULATION | 0398 | The East side of the basement has an air intake louver currently covered by Masonite. This project would replace the Masonite with rigid insulation to prevent the possibility of freezing water lines. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 2500
0398EXT1 | REPLACE FLASHING OVER GENERATOR ROOM | 0398 | Existing flashing allows wind driven rain to enter the building. This project would replace the flashing with a mastic sealed flashing to protect the building. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0398INT1 | REPLACE CARPET | 0398 | Carpet throughout the facility is worn and stained. This project would replace the existing broadloom carpet with carpet tile. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 87500
0398PLM1 | INSTALL BACKFLOW PREVENTION DEVICES | 0398 | State Health law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a reduced pressure principle backflow preventer on the building service and vacuum breakers at all hose bibs and janitor's sinks. Costs include an above ground vault for the backflow preventer, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Immediate to Two Years | Currently Critical | 1 | 15000
0398INT4 | PAINT INTERIOR FINISHES | 0398 | Based on building use and the passage of time, the interior walls and ceilings of this building should have a new application of paint for proper upkeep and maintenance. | STATE ADMINISTRATIVE OFFICE | 9853 | ETR | ESD |  | Carson City | 1960 | 30920 | 2004-09-28 | Four to Ten Years | Long-Term Needs | 3 | 77300
0393EXT4 | CEILING REPAIRS | 0393 | There are voids in the lath and plaster ceiling in the mechanical room that need to be repaired. This project recommends patch and repair of all holes in the ceiling. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0393EXT3 | ROOF REPLACEMENT | 0393 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty for this building is 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 8-10 years to be consistent with the roofing program and the end of the warranty period. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Four to Ten Years | Long-Term Needs | 3 | 275136
9855ADA1 | ADA RAMP MODIFICATIONS | 9855 | In order to comply with current Americans with Disabilities Act (ADA) requirements, modifications will be necessary for the ADA ramp and stairs on the south side of the building. The standards for a ramp require a 36" clear space. Currently, the handrails encroach on this clearance and reduce the clear space to less than 32". The concrete on the stairs and the ramp is deteriorating. Spalling and cracking have occurred. Exposure to the elements is a contributing factor. This project recommends modifying the steel handrails to comply with ADA guidelines, repairing the concrete on the ramp, and replacing the concrete stairs. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0393INT6 | INTERIOR FINISHES | 0393 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 229280
9855SIT1 | LOADING DOCK MODIFICATIONS | 9855 | The concrete apron leading up to the loading dock is dysfunctional in its current configuration. The slope from the sidewalk to the gate is too steep causing vehicles to scrape bumpers and hitches on it. When trucks pull up to the dock, they are too high and there is no dock leveler. There is not enough space for most trucks to turn and back up in the street adjacent to the loading area. These issues have caused many delivery companies to refuse to use the ramp requiring the staff to unload in the street. It is recommended to procure engineering services to re-design the approach to the loading dock to ensure a functional system. This project would provide for the removal and disposal of the concrete from the sidewalk to the loading dock, re-grading and installing a total of 1,000 square feet of new concrete, removing and re-installing the automatic gate, and installing a new dock leveler. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0393ADA2 | ADA EMPLOYEE LOUNGE UPGRADES | 0393 | In order to comply with current Americans with Disabilities Act (ADA) requirements, modification will be necessary for the employee lounge in the addition and the kitchenette in the conference room. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables, and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0393INT7 | CARPET REPLACEMENT | 0393 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 73500
0393ADA3 | BREAK ROOM REMODEL | 0393 | One of the break rooms in the building dates back to the original construction in 1970. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0393SFT4 | SAFETY CABINETS | 0393 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or International Fire Code for hazardous materials containment. This project would provide for a self-closing hazardous storage container in the building and installation of placards on the building exterior in accordance with OSHA 1910.106 (d) and International Fire Code chapter 57 section 5704.3.2.1.3. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0393EXT5 | ROOF REPLACEMENT | 0393 | The roof above the mechanical room was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed over 20 years ago. It is recommended that this building be re-roofed in the next 1-2 years. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 9000
9855ADA3 | ADA SIGNAGE & STRIPING | 9855 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The ADA parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. There is a missing "No Parking" sign at the ADA parking area and the striping has faded. This project would provide for striping, purchase and installation of the sign, and any other necessary upgrades to the parking area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 3500
0393HVA1 | AIR CONDITIONING REPLACEMENT | 0393 | The current backup air conditioning unit serving the computer room is 40 years old. The air conditioning unit is beyond its useful life expectancy. If the backup air conditioning unit did not turn on or if it stops working, the server room would become too hot, and this could lead to a catastrophic failure of all the statewide servers (due to overheating). It is recommended to install a new backup air conditioning system. This project would provide for the purchase and installation of a new air conditioning unit, to include all required modifications and connections to the utilities. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 125000
0393INT5 | FLOOR TILE REPLACEMENT | 0393 | The 2"x2" floor tiles in the restrooms are reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12"x12" tiles within the next 2-3 years. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27000
0393ENR1 | EXTERIOR LIGHTING REPLACEMENT | 0393 | The building has perimeter lighting on the exterior of the building. The light fixtures are metal halide and not energy efficient. This project would provide for the replacement of the 8 exterior wall pack light fixtures with new LED light fixtures, using existing wiring. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0393HVA2 | HVAC SYSTEM REPLACEMENT | 0393 | The HVAC system (chillers, cooling tower, boilers, heat exchanger and associated equipment) was installed in 2006. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles in the next 8-10 years. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Four to Ten Years | Long-Term Needs | 3 | 573200
0393PLM1 | WATER HEATER REPLACEMENT | 0393 | There is a 75 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. The water heater was installed in 2006. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0393EXT2 | EXTERIOR FINISHES | 0393 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete wall panels, brick and masonry, and caulking of the windows, flashing, fixtures, and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Four to Ten Years | Long-Term Needs | 3 | 229280
9855ENR3 | EXTERIOR LIGHTING REPLACEMENT | 9855 | The 23 perimeter light poles around the site have a total of 28 light fixtures. These fixtures are metal halide and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9855SIT3 | SITE DRAINAGE UPGRADES | 9855 | The grade does not slope away from the building effectively. This is causing water to pool against the foundation. In the winter months, water freezes against the foundation and over time this will cause damage to the foundation. It is recommended per the International Building Code 1804.3 site grading shall be sloped away from the building at a slope of 5-percent for a minimum distance of 10 feet measured perpendicular to the face of the wall. This project would remove the concrete planter wall, excavate the excess soil, install new landscaping, and create positive flow away from the buildings. Additional French drains shall be installed around 450 feet of the building. It is recommended that the this project be completed within 2-3 years. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
9855SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9855 | It is important to maintain the asphalt paving on the site. This project would provide for minor crack filling and striping of the parking lot. This project should be scheduled within 2-3 years to maintain the integrity of the paving and prevent premature failure. | DATA CENTER SITE | 9855 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-06-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19285
0393SFT5 | PANIC HARDWARE IN ELECTRICAL ROOMS | 0393 | The electrical room with the Uninterruptible Power Supply system contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 International Building Code (IBC) 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required at the time of the 2007 remodel but is suggested in this report as an increased safety measure. It is recommended that this project be completed within 1-2 years. The estimate is based on three doors that require panic hardware. | DATA CENTER | 9855 | Admin | PubWorks | B&G | Carson City | 1970 | 22928 | 2016-06-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0401ADA2 | ADA SIGNAGE | 0401 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 1200
0401SFT5 | ROOF HATCH REPLACEMENT | 0401 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 3500
0401EXT5 | EXTERIOR DOOR REPLACEMENT | 0401 | The exterior metal door assembly on the south side public entrance is damaged from age and general wear and tear and has reached the end of it's expected life. This project would provide for the replacement of the south double door entry assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0401INT2 | FLOORING REPAIRS | 0401 | The painted and sealed concrete floor in the addition portion of the building is damaged and reaching the end of its useful life. It is recommended to refurbish the floor by stripping the existing finish, repairing any cracks, painting and sealing in order to extend its useful life. This project would provide for refurbishing the floor in the next 2-3 years. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49500
0401EXT4 | DOOR AWNING INSTALLATION | 0401 | The exterior door on the east elevation is the main entrance for staff and volunteers. They must use this entrance to open the building and disable the alarm. During inclement weather, snow and ice builds up on and around the door and impedes its function. This makes it difficult and dangerous to get in and out of the building. It is recommended to retrofit the door with a metal awning to protect this entrance from the elements. The awning should span the full width of the concrete landing and include a gutter that ties into the adjacent downspout. This project also includes relocating the exterior light from its current location to a position below the awning. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0401SFT7 | EXPLOSION-PROOF REFRIGERATOR/ FREEZER | 0401 | This project would provide for the purchase and installation of two explosion-proof refrigerator/ freezer units. The existing unit has reached capacity and staff reported a need for two additional units. These units protect the chemicals or substances stored inside the unit from explosions outside the unit as well as protecting the exterior environment from explosions inside the unit. The units must be hardwired to the electrical system to prevent a short or overheating a coil which could ignite a flammable or explosive substance stored inside. Additional costs are included for an electrician to hard-wire the units to the electrical system. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
0401SFT6 | HIGH DENSITY STORAGE SYSTEM REPAIRS | 0401 | The existing high density storage system in the archive area is not functioning properly and is a safety hazard. The electrical and mechanical elements of the system are aged, compromising the safety of the staff and volunteers. The system has a safety feature which prevents the shelves from moving when a person is in the aisle. The electronics and sensors for this safety feature are failing and pose a very dangerous situation for a person working in the aisles. There are also shelves at the ends of the system that do not open fully. It is recommended to refurbish the entire storage system. The estimate includes removal and disposal of existing electrical and mechanical parts and purchase and installation of new parts to restore the system to a safe and fully functioning system. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 25000
0401INT4 | HIGH DENSITY STORAGE SYSTEM INSTALLATION | 0401 | The static shelving in the archive area has reached capacity and will no longer be able to meet storage demands. Leased space and other offsite storage space has already been utilized to handle the overflow. In order to maintain control and security of the artifacts it is recommended to replace the existing shelving with a new high density storage system as opposed to utilizing the offsite storage facilities. The new system will store two to three times as much material in the same amount of space. The estimate includes removal and disposal of existing static shelving and purchase and installation of a high density storage system. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
0401PLM1 | WATER HEATER REPLACEMENT | 0401 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0401ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0401 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the janitors equipment and other items currently blocking the working space. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 250
0401ENR2 | LIGHTING UPGRADE | 0401 | There are still some older fluorescent type lighting fixtures in the building including T-12's and older T-8's that are not energy efficient. This project will upgrade these fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
0401INT3 | JANITORS CLOSET REPAIRS | 0401 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0401SEC1 | SECURITY SYSTEM UPGRADE | 0401 | The buildings security system is limited and outdated and the intercom system through the telephones does not meet staff requirements. There a few security cameras and alarmed doors, but this is not sufficient to protect the people, priceless artifacts, manuscripts, photographs and library collections in the building. The only intercom system is the speakerphones on the telephones. Staff noted that the speakers are not loud enough and they are not located in the most necessary areas. This project addresses upgrading the security and communications systems in the building. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 222000
0401INT1 | INTERIOR FINISHES | 0401 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111000
0401SFT4 | EXIT SIGN UPGRADES | 0401 | The existing exit signs in the building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. The estimate is based on purchasing and installing 22 exit signs at $450 each. IBC - 2006 Chapter 10 was referenced for this project. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 9900
0401SFT2 | STAIR LANDING INSTALLATION | 0401 | There are a total of five exterior stairways coming out of the building, not including the one at the south side main entrance. Four of these stairways do not have a bottom landing. This does not comply with 2006 IBC Section 1009.4 which describes the requirements for landings at stairways including that the width and length of the landing shall not be less than the width of the stairway. The fifth stairway has a bottom landing that slopes towards the stairway and the building. This landing is on the east entrance and creates a situation where water pools up and freezes creating a slipping hazard. This project addresses installing four new landings designed to current code and removing and replacing the landing at the east entrance. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 7500
9856ADA1 | ADA ACCESS / ROUTE OF TRAVEL UPGRADES | 9856 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical and mental limitations. There are numerous areas between the sidewalk and the main entry doors that do not comply with ADA guidelines. The sidewalks, stairway and entry landing are not compliant and should be scheduled for repairs. Due to the slope at the entry landing, the adjacent ramps will require modifications to meet the new elevation of the landing. The stairway will need to be completely rebuilt. If the handrails are re-used, proper returns will need to be retrofitted onto them. Directional signage from the parking spaces to the entry should be included as well. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. There are deficiencies in the accessible route from the bus stop and the parking spaces to the entry stairs and accessible ramp. These accessible elements are under the purview of UNR and should be addressed to provide the public with an ADA accessible route from the parking, bus stop and entrance into the building. | NEVADA HISTORICAL SOCIETY SITE | 9856 | CultAffr | M&H | HistSoc | Reno | 0 |  | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 150000
0401SFT3 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0401 | There is a Halon automatic fire suppression system in a portion of the building. This system is outdated and the chemical it uses has been phased out. This project recommends replacing the existing system with a double-interlock pre-action fire suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Immediate to Two Years | Currently Critical | 1 | 250000
0401EXT3 | EXTERIOR FINISHES | 0401 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 8-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA HISTORICAL SOCIETY | 9856 | CultAffr | M&H | HistSoc | Reno | 1968 | 22200 | 2018-08-04 | Four to Ten Years | Long-Term Needs | 3 | 111000
2128INT2 | FLOORING REPLACEMENT - FREIGHT OFFICE | 2128 | The "Battleship" linoleum flooring in the Freight Office is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new "Battleship" linoleum. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
2128ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2128 | This building does not contain a drinking fountain. It is recommended to install a drinking fountain for the comfort of the occupants. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of an accessible fixed high/ low ADA drinking fountain. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2128EXT4 | EXTERIOR DECK REPAIRS | 2128 | The building has a boardwalk on the street side of the building and a loading dock on the track side. They were recently refurbished with new wood planks that were nailed to the framing. The nails are proving to be insufficient and should be replaced with screws. As the wood ages, it pushes the nails out and causes a safety hazard. This project provides for removing the nails and replacing them with deck screws along the entire boardwalk and loading dock. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2128CUL1 | KITCHEN INSTALLATION | 2128 | The building does not have any culinary equipment. There are many special events held in the Freight Barn each year that benefit the museum through exposure and rental fees. Equipping the building with culinary equipment would provide additional accommodations for future special events. This project recommends installing mid range, high quality culinary equipment, a sink, cabinets and the plumbing and electrical utilities that they would require. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 75000
2128INT3 | INTERIOR FINISHES | 2128 | The interior finishes are in fair condition. Most of the walls and ceilings are unfinished wood, but there are painted walls and ceilings in the restrooms and the shop areas. It is recommended that the finished interior walls and ceilings be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2128ADA1 | ADA SIGNAGE | 2128 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required and that the restroom ADA signs be moved to a compliant location. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1500
2128SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2128 | This building houses irreplaceable records for the site dating back to the early 1900s. The square footage of the building exceeds 12,000 square feet and does not have an automatic fire suppression system. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 90055
2128EXT3 | WINDOW REPLACEMENT | 2128 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units including wooden frames and includes additional costs for the unique historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements for this building. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2128HVA1 | HVAC SYSTEM INSTALLATION | 2128 | This building is equipped with a wood burning stove in the freight office and two wall mounted electric heaters in the restrooms and does not have any cooling equipment. The rest of the building is not conditioned space. Future plans for the building include interactive displays, a community center, and special events which would all benefit from adding heating and cooling for the entire building. This project would provide for replacing the existing heaters with roof mounted propane fired packaged units that provide heating as well as air conditioning to the entire building. Propane gas service will be required and is included in the cost. This project should be implemented after or concurrent with the Insulate Building project and coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77190
2227HVA1 | HVAC SYSTEM UPGRADE | 2227 | The existing HVAC system consists of electric baseboard heaters and several window mounted air conditioners. The electric heaters are inefficient and the air conditioners only cover small areas of the building. There is a need for cooling equipment throughout the building to provide a comfortable interior environment in the summer. This project would provide for replacing the existing equipment with a central HVAC system including exterior ground mounted propane fired packaged units that provide heating as well as air conditioning and installing duct work and controls. Propane gas service will be required and is included in the cost. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172000
2128EXT2 | EXTERIOR FINISHES | 2128 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the metal panels and wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 64325
2227EXT4 | SHED ROOF REPLACEMENT | 2227 | The metal roof on the north elevation of the building was in poor condition at the time of the survey and had active leaks. This shed roof partially covers the boarding platform and has a gutter and downspout system that is in poor condition. When the gutters leak, water pools up and freezes on the boarding platform creating a safety hazard. The gutters and downspouts around the rest of the building are also in poor condition with active leaks. It is recommended to re-roof the metal shed roof and repair or replace the gutters and downspouts around the entire building. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 25000
2227STR1 | STRUCTURAL REPAIRS | 2227 | Due to the age of the building and the structural codes at the time, the structural system may be deficient and should be evaluated and repaired. Some shoring work has been done in the basement by applying gunite to the foundation walls, but no other major structural upgrades have taken place since the State acquired the building in 1992. The estimate is a general figure representing a likely scenario of installing blocking, steel structural ties, cables. etc... to increase the lateral and vertical load resistance. An evaluation and design must be conducted by a licensed structural engineer, of which the costs are not included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
2227EXT3 | WINDOW REPLACEMENT | 2227 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 44 units including wooden frames and includes additional costs for the unique historical nature of the building. Removal and disposal of the existing windows is included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements for this building. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/25/2011. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
2128ENR2 | LIGHTING UPGRADE | 2128 | The existing lighting fixtures are the older fluorescent and incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts and compact fluorescent lights are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19297
2227ENR1 | LIGHTING UPGRADE | 2227 | The existing lighting fixtures are the older fluorescent and incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts and compact fluorescent lights are suggested. Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12900
2128ENR1 | INSULATE BUILDING | 2128 | This building has no insulation. The temperature extremes are contributing to accelerated decay of the contents, which include historical artifacts awaiting restoration and/or on display. This project will install batt insulation in the walls and ceilings to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. This project should be implemented before or concurrent with the HVAC System Installation project and coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD FREIGHT BARN | 9857 | CultAffr | M&H | Museums | Ely | 1906 | 12865 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45027
2227INT1 | INTERIOR FINISHES | 2227 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43000
2227ADA1 | ADA AUDIO/ VISUAL PRESENTATION | 2227 | The Railroad Depot is open to the public for tours and train rides. The second floor is home to most of the historical Depot artifacts and where a large portion of the tour takes place. There is no ADA access to this area. This project would provide for an ADA accessible location inside the lower level of the building for an audio / visual (A/V) presentation of the inaccessible portions of the Depot and site. This project includes funds for an audio / visual consultant to outline and document the exhibits and purchase and installation of all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 25000
2227EXT5 | EXTERIOR FINISHES | 2227 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood trim and soffits, power washing and painting the stucco, cleaning and sealing the stone masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | EAST ELY RAILROAD DEPOT | 9857 | CultAffr | M&H | Museums | Ely | 1907 | 8600 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43000
0272INT9 | INTERIOR DOOR REPLACEMENT | 0272 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 40 interior doors was used in this estimate. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0272ELE4 | PANIC HARDWARE IN ELECTRICAL ROOMS | 0272 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required at the time of the 2007 remodel, but is suggested in this report as an increased safety measure. It is recommended that this project be completed within 1-2 years. The estimate is based on three doors that require panic hardware. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 3000
0272SFT5 | SPRINKLER HEAD REPLACEMENT | 0272 | The existing fire suppression sprinkler heads are an older style and are located at the exterior of the building. They are rusted and do not comply with NFPA 25. This project recommends that all of the exterior fire suppression sprinkler heads be removed and replaced with new sprinkler heads. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0272ENR2 | EXTERIOR LIGHTING | 0272 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28500
0272PLM2 | PLUMBING REPLACEMENT | 0272 | The sanitary wastewater and galvanized plumbing systems are showing signs of deterioration. Due to this deterioration, the systems are not working to their full potential. The galvanized lines are rusting from the inside and the sanitary wastewater lines are deteriorated. The lines are original to the site and are in poor condition. The hard water is a contributing factor to this deterioration. Deposits within the pipes have caused restriction, and have slowed the water flow. This project would provide for the complete replacement of the sanitary sewer and galvanized piping system. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720000
0272HVA3 | AIR CONDITIONER INSTALLATION | 0272 | The server rooms are not sufficiently cooled by the existing HVAC system. If the rooms are too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install air conditioning systems in the rooms to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of three air conditioners including all required connections to existing utilities. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0272ELE3 | INTERCOM AND PUBLIC ADDRESS SYSTEM INSTALLATION | 0272 | There is no intercom or public address system for this building. This are a large amount of people in the building at any given time and communications are minimal at best. It is important for the employees to be able to communicate with each other quickly as well as address the customers in order to have a safe working environment. This project would provide for the purchase and installation of an intercom and public address system that would work in concert with the other recommended security system upgrade projects. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0272ENR3 | ASBESTOS ABATEMENT/ ENVIRONMENTAL | 0272 | The building has asbestos and environmental concerns in the floor tile mastic and the linoleum. The floor is reaching the end of its useful life expectancy and will need to be removed and remediated per OSHA Standards (29 CFR 1910.1001) and (29 CFR 1926.58). This project would provide for the abatement and remediation of the floor mastic and the linoleum, removal and disposal of the old flooring and the installation of new flooring. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 30000
0272EXT5 | ROOF REPLACEMENT | 0272 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2007. It is recommended that this building be re-roofed in the next 9-10 years to be consistent with the roofing program and the end of the warranty period. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 432000
0272SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0272 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention. An inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 9000
0272INT8 | FLOORING REPLACEMENT | 0272 | The VCT, sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 230400
0272HVA4 | HVAC EQUIPMENT REPLACEMENT | 0272 | The eight HVAC roof top units and ceiling mounted warehouse heater were installed in 1994. The units are reaching the end of their expected service life and should be scheduled for replacement. This project would provide for the purchase and installation of eight new HVAC packaged units, one new ceiling mounted heater, balancing, DDC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720000
0272EXT8 | WINDOW REPLACEMENT | 0272 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 160 units. Removal and disposal of the existing windows is included in this estimate. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 240000
0272ADA6 | RAMP MODIFICATIONS | 0272 | In order to comply with current ADA requirements, modifications will be necessary for the ADA ramps and stairs on the east and west sides of the building. The standards for a ramp require a 36" clear space. Currently, the handrails encroach on this clearance and reduce the clear space to less than 32". The concrete on the stairs and the ramp is deteriorating and the steel poles are rusting at their bases. Exposure to the elements is a contributing factor. This project recommends replacing the steel handrails to comply with ADA guidelines, repairing the concrete on the ramp, and replacing the concrete stairs. The 2012 IBC, ICC/ANSI A117.1 -2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 120000
0272INT10 | INTERIOR SIGNAGE | 0272 | The current identification and directional signage in the building is in poor condition and does not provide adequate directions for the general public. This project would provide funding for new signage throughout the site including program identification and customer circulation signage. Where applicable, signage shall comply with ADA regulations including mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish regulations. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
9858SIT4 | EXTERIOR SIGNAGE | 9858 | The current site identification and directional signage is in poor condition and does not provide adequate directions for the general public. This project would provide funding for new signage throughout the site including site identification, building identification, directional traffic signage and directional pedestrian signage. Where applicable, signage shall comply with ADA regulations including mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish regulations. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0272SEC2 | SECURITY SYSTEM INSTALLATION | 0272 | The building does not have a security system. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. This project should be implemented concurrently with the Video Security System Upgrade project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144000
2169EXT7 | ROOF REPLACEMENT | 2169 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2007. It is recommended that this building be re-roofed in the next 9-10 years to be consistent with the roofing program and the end of the warranty period. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 18000
0272SFT6 | EMERGENCY GENERATOR REPLACEMENT | 0272 | The existing emergency generator was installed in 1994 and is approaching the end of its useful life. This project would provide for a new diesel powered 300 KVA generator including a new transfer switch, wiring, concrete pad, fencing and protective bollards. The estimate includes demolition and disposal of the old equipment and materials. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 350000
9858SIT3 | SIDEWALK AND CURB REPLACEMENT | 9858 | The sidewalks and curbs serving the buildings on this site are deteriorated and failing. In some areas the concrete has heaved and there is settling in other locations. The concrete is pitted and spalling. This project addresses removal and replacement of existing sidewalks and curbs as needed. 10,000SF of 4" thick concrete sidewalk was used for this estimate. NRS 338.180, IBC 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0272EXT6 | EXTERIOR DOOR REPLACEMENT | 0272 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of eleven exterior door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
2169ADA2 | ADA RESTROOM UPGRADE | 2169 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 15000
0272ADA5 | EXTERIOR HANDRAIL REPLACEMENT | 0272 | The handrails around the sidewalks are older, are rusting at their bases and are not safe. The gripping surfaces are incorrect and they are not continuous from the top to the bottom landings. This project recommends the installation of new handrails at the sidewalks and for the proper returns and supports to be installed. Removal and disposal of the existing handrails is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 80000
0272ENR1 | LIGHTING UPGRADE | 0272 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. A complete removal of the existing system and replacement with LED fixtures is recommended including a lighting control system and occupancy sensors. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 230400
9858PLM1 | BACKFLOW PREVENTION | 9858 | NAC 445A.67185 and the UPC Section 603 require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, storage and irrigation systems, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and at appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 35000
9858ELE1 | EXTERIOR OUTLET REPLACEMENT | 9858 | There is an electrical outlet on the exterior light pole that is broken and does not meet code. This outlet box, cover and GFCI should be changed to comply with NEC 2011. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof box and cover. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
9858ADA1 | ADA PARKING SPACE UPGRADES | 9858 | The ADA provides for accessibility to sites and services for people with physical limitations. The existing ADA parking spaces are no longer compliant and there are not enough of them. Based on the total number of parking spaces at this facility, 11 concrete parking spaces are necessary to comply with ADA requirements. This project would provide for 11 concrete ADA parking spaces and walkways to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 82500
2169EXT4 | EXTERIOR DOOR REPLACEMENT | 2169 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the 6 door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169SFT4 | EXIT SIGN AND EGRESS LIGHTING | 2169 | The building does not have emergency egress lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169ENR1 | EXTERIOR LIGHTING REPLACEMENT | 2169 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169ENR0 | LIGHTING UPGRADE | 2169 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2169PLM1 | WATER HEATER REPLACEMENT | 2169 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0272ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0272 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720000
9858ENR1 | EXTERIOR LIGHTING REPLACEMENT | 9858 | The 6 perimeter light poles around the site have a total of 12 light fixtures. These fixtures are metal halide and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0272SEC1 | VIDEO SECURITY SYSTEM UPGRADE | 0272 | The video security system for the building and the site is outdated and should be scheduled for immediate replacement. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the cameras, conduit and wiring throughout the facility with all digital equipment as well as sufficient storage capacity. This project should be implemented concurrently with the Security System Installation project. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 150000
2169ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2169 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2169SEC3 | VIDEO SECURITY SYSTEM UPGRADE | 2169 | The video security system for the building and the site is outdated and should be scheduled for immediate replacement. The system is over ten years old and it is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. Due to the security level of the facility is imperative that a new system is installed for the safety of the staff, clients and the public. This project addresses replacement of the cameras, conduit and wiring throughout the facility with all digital equipment as well as sufficient storage capacity. This project should be implemented concurrently with the Security System Installation project. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 25000
2169EXT6 | WINDOW REPLACEMENT | 2169 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169ELE2 | WIRING CLEANUP | 2169 | The wiring on the roof from the Reno DMV building is daisy chained to the roof of the Reno DMV Inspection Station without using the proper electrical equipment. This project would disconnect the wires from the Reno DMV Inspection Station and re-run the wires through the proper roofing boots, conduits, eye bolts and weather heads. This project would provide for the wiring to be run per NEC 2011. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2169HVA4 | HVAC EQUIPMENT REPLACEMENT | 2169 | The packaged unit, swamp cooler and heat pump systems were installed in 1994. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of one new packaged unit, new ductwork, grills, air balancing, DDC and cleaning of the existing duct work. This project includes removal and disposal of the existing equipment and all required connections to utilities. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2169EXT5 | GUTTER REPLACEMENT | 2169 | The existing gutter on the Reno DMV Inspection Station eave has numerous joints that have proven impossible to seal against leaks. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with seamless gutter. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0272INT2 | CUSTOMER STATION REPLACEMENT | 0272 | The existing customer stations are damaged and deteriorating due to heavy use and age. The customer service counter spaces do not have adequate room to meet the customers and staff’s needs. This project recommends removing the existing work area counters and installing a modular, ergonomically friendly system which meets the current needs of staff and is movable for future innovations in customer service. Additional costs are included to remove the casework in the public lobby and waiting areas. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Four to Ten Years | Long-Term Needs | 3 | 250000
0272INT7 | BREAK ROOM REMODEL | 0272 | The kitchenette and associated cabinets in the employee break room were replaced in this building in 1994. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. NRS 338.180, IBC -2012, ICC/ANSI A117.1 -2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design and attention to providing an accessible sink is recommended. This estimate includes removal and disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0272ADA4 | DUAL LEVEL DRINKING FOUNTAIN REPLACEMENT | 0272 | The existing accessible drinking fountain was installed in 1994. It is worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the drinking fountain with a new accessible fixed high/ low ADA compliant drinking fountain. The 2012 IBC Chapter 11, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG was used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0272EXT4 | OVERHEAD DOOR REPLACEMENT | 0272 | There is a 10'x10' overhead sectional door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead sectional door and replacement with a motorized overhead sectional door. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0272ADA3 | ADA SIGNAGE | 0272 | ADA regulations pertaining to building access, route of travel and restrooms have established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for the purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 3000
0272EXT1 | EXTERIOR FINISHES | 0272 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, painting where necessary and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 288000
2169INT1 | REPLACE FLOORING | 2169 | The VCT flooring in the office areas is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2169SEC1 | SECURITY SYSTEM INSTALLATION | 2169 | The building does not have a security system. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. This project should be implemented concurrently with the Video Security System Upgrade project. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2169ADA1 | ADA SIGNAGE | 2169 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/05/2003 and 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 1500
9858SIT2 | FENCE INSTALLATION | 9858 | The east side of the property bordering Galletti Way does not have a fence. There have been numerous issues with the public who are not doing business at the DMV offices trespassing on the site and parking and chaining their bikes to the ADA accessible handrails. This project would provide for the installation of a security fence and an electric entrance gate along Galletti Way to deter this activity. This estimate is for 1,600 linear feet of fence at $35 a linear foot and an electric gate. This project should be coordinated with the Asphalt Paving Replacement project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 96000
0272ADA1 | RESTROOM REMODELS | 0272 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 200000
0272INT5 | INTERIOR FINISHES | 0272 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 288000
9858SIT1 | ASPHALT PAVING REPLACEMENT | 9858 | The existing public and employee asphalt paved parking areas are in poor condition. There are numerous asphalt patches, alligator cracking and it has been overlaid to the extent that paving is level with the curbs in some areas causing problems with the drainage. The existing parking spaces provided are at their maximum capacity. This project would provide for the redesign of the parking area to address drainage and overcrowding, removal of the existing landscaped areas, asphalt paving and base as required and installation of new Type II base and valley gutters, 4" of new asphalt paving, striping, and wheel stops. 202,500 square feet was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO SITE | 9858 | MtrVeh | B&G |  | Reno | 0 |  | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2916000
2169SFT3 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2169 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the tool boxes and other items currently blocking the working space. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 250
2169SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2169 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 IFC. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 4800
2169SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2169 | The building is partially a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 16800
2169EXT3 | OVERHEAD DOOR REPLACEMENT | 2169 | There are four 12'x14' overhead sectional garage doors which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. It is recommended to install coiling doors as opposed to sectional doors due to the limited space. This project would provide for the removal and disposal of the overhead sectional overhead doors and replacement with coiling doors with new motors. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
2169HVA2 | VEHICLE EXHAUST EXTRACTION SYSTEM | 2169 | The Reno DMV Inspection Station has an exhaust extraction system that is original and is not providing adequate ventilation. Table 403.7 in the 2012 UMC states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0272PLM1 | WATER HEATER REPLACEMENT | 0272 | There is a 50 gallon gas-fired water heater in the building that was installed in 1996. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. The 50 gallon capacity of the existing water heater is not sufficient for the demands of the building. It is recommended that the water heater be upgraded to a 75 gallon gas-fired water heater. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO OFFICE | 9858 | MtrVeh | B&G |  | Reno | 1975 | 28800 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 3000
2169HVA1 | REPLACE EXHAUST FANS | 2169 | The existing exhaust fans that serve the vehicle inspection garage are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2169INT2 | INTERIOR FINISHES | 2169 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2169EXT1 | EXTERIOR FINISHES | 2169 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2169EXT2 | SOFFIT REPAIR | 2169 | The exterior gypsum board soffit under the roof eave is damaged from exposure to moisture and should be scheduled for replacement. This project would provide for removal of the gypsum board soffit and replacement with a more substantial material such as exterior grade plywood or metal to match the metal fascia on the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/01/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/06/2017. | DMV RENO INSPECTION STATION | 9858 | MtrVeh | B&G |  | Reno | 1975 | 1200 | 2017-03-06 | Immediate to Two Years | Currently Critical | 1 | 14925
0515PLM1 | WATER HEATER REPLACEMENT | 0515 | There is a 85 gallon gas-fired water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 3000
9859SIT2 | EROSION CONTROL | 9859 | On the north side of the building, the dirt bank between the building and McCarran Blvd is eroding considerably. The runoff from McCarran Blvd is exacerbating an already poorly designed drainage area. The dirt bank has spilled over the curb into the access road. There have been several minor improvements accomplished to control the situation, but it is apparent that a major improvement must happen in order to protect the road, parking and the building from permanent damage. This project recommends installing a retaining wall near the curb in order to provide proper drainage and erosion control. The estimate is based on a 300 foot long, 4'-0" high reinforced concrete masonry unit retaining wall. | NEVADA EARLY INTERVENTION SERVICES SITE | 9859 | HHS | ADSD | B&G | Reno | 0 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 30000
9859SIT1 | SLURRY SEAL ASPHALT PAVING | 9859 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 60,000 square feet of asphalt area was used to generate this estimate. | NEVADA EARLY INTERVENTION SERVICES SITE | 9859 | HHS | ADSD | B&G | Reno | 0 |  | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0515INT3 | JANITORS CLOSET REPAIRS | 0515 | The mop sink in the Janitor Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0515ADA3 | ADA KITCHEN REMODEL | 0515 | The kitchen is in fair to poor condition and does not meet the Americans with Disabilities Act (ADA) requirements. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. ADA features such as accessible fixtures, clear floor space and compliant counter heights should be integrated into the new design. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and appliances with mid range, high quality components that comply with ADA requirements. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 20000
0515INT2 | TILE FLOORING REPLACEMENT | 0515 | The ceramic tile flooring in the entry vestibule is damaged and reaching the end of its useful life. It is recommended that the tile flooring be replaced. This project would provide for removal and disposal of the existing tile and installation of new ceramic tile flooring. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0515EXT1 | EXTERIOR FINISHES | 0515 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing the entire building, priming and painting the stucco and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 99000
0515EXT2 | WATERPROOFING UPGRADES | 0515 | The south facing exterior wall experiences water weeping through it during inclement weather. The water infiltration can be seen on the interior of the brick masonry wall and the most extensive weeping occurs directly below the roof scuppers. This project provides for waterproofing the exterior wall and decks by applying sealant and caulking and extending the roof scuppers and deck scuppers to grade rather than draining down the sides of the walls. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 25000
0515INT1 | INTERIOR FINISHES | 0515 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 99000
0515ADA4 | ADA SIGNAGE | 0515 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 3600
0515ENV1 | NONABSORBENT FINISHES | 0515 | 2006 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 04/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | NEVADA EARLY INTERVENTION SERVICES | 9859 | HHS | ADSD | B&G | Reno | 1980 | 19800 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0200INT2 | INTERIOR FINISHES | 0200 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208400
0200EXT2 | EXTERIOR FINISHES | 0200 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete and tile, repairing cracks in the concrete and granite, and caulking of the windows, flashing, fixtures, and all other penetrations. Special attention should be paid to the penthouse where the cooling tower has caused moss and mildew growth. It is recommended that the building be cleaned, sealed, and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208400
0200ELE2 | EMERGENCY GENERATOR REPLACEMENT | 0200 | The existing generator which provides emergency power to the building is old and under-powered for the increased electrical load. This project would provide for the replacement of the generator with a new 550 kw generator including new auto switchgear. It is recommended that this project be done in conjunction with the electrical upgrade project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0200ADA3 | ADA IMPROVEMENTS | 0200 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This building contains a drinking fountain on the second floor that is missing cane detection equipment and elevator car controls that do not meet current codes. The car controls outside and inside the elevator should comply with ADAAG 4.10.12 which describes button sizes, Braille requirements, mounting heights and control locations. This project will provide cane detection and new car controls in accordance with ADA requirements. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 7500
0200SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0200 | The emergency egress lighting is insufficient and most of the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 41680
0200SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0200 | The building is a B occupancy per the 2006 IBC. It does not have a fire suppression system on the first, second or third floors. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. Costs are lower on this project because there is a fire suppression system installed in the basement and a 4" dry standpipe that supplies the fire hoses on the upper floors with fire department connections at the roof, basement, and at grade. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 333440
0200SFT5 | REPLACE EMERGENCY DISCONNECTS | 0200 | There is an emergency shutoff for the boiler and a remote purge control for the chiller located on the east side of the building. These switches are not secured and could be activated by unauthorized persons resulting in loss of building heating and cooling capacity. This project recommends replacing the existing switches with newer models and/or relocating them to a more secure location. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 1500
0200ELE1 | ELECTRICAL UPGRADE | 0200 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the building's electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels, wiring and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. At the time of the 2010 survey, a CIP project 09-M18 to replace the main switchgear and transformer in the basement was funded but not completed. The costs were not included as part of this project. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 625200
0200ENR2 | HVAC SYSTEM REPLACEMENT | 0200 | The building has an older HVAC system, most of which is original to the building. The boiler is approximately 22 years old, with radiant heaters under the windows. This project recommends replacing the HVAC system for improved comfort and efficiency. This project would provide for the removal and disposal of the existing air handler, cooling tower, boiler, radiators and controls, and replacement with new equipment including a new boiler, air handler, cooling tower, controls, all required connections to utilities, ductwork, and required equipment. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1667200
0200INT1 | FLOORING REPLACEMENT | 0200 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 3-4 years. This estimate is for all three floors with the exception of the main floor lobby tile, which is in good shape. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 190000
0200ADA2 | ADA RESTROOM REMODEL | 0200 | The Men's and Women's designated ADA restrooms on the first floor do not fully meet the Americans with Disabilities Act (ADA) requirements. The restrooms on the second and third floors should be remodeled to comply with the ADA as well. A complete retrofit is necessary on all four restrooms on the second and third levels including new partitions, water closets, urinals, lavatories, faucets, handles and any other necessary fixtures and finishes and minor modifications to the first floor designated ADA restrooms. This project would provide funding to bring all of the restrooms into ADA compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 150000
0200INT5 | JANITOR CLOSET REPAIRS | 0200 | The mop sinks in the Janitor Closets are mounted adjacent to painted concrete wall board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. A total for 3 closets was used for this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 4200
0200SFT1 | MODIFY REFRIGERANT ALARM SYSTEM | 0200 | The refrigerant alarm system appears to be improperly installed, with the horn located in the room, and the exhaust system is piped into the chimney for the abandoned incinerator. A project is recommended to provide proper signage, relocate the exhaust system to the exterior, and related repairs. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 6000
0200ENR3 | WINDOW REPLACEMENT | 0200 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 144 units consisting of one large pane with two operable windows below. Removal and disposal of the existing windows is included in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 792000
0200ENR1 | LIGHTING UPGRADE | 0200 | The existing lighting fixtures are the older T-8 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in janitor closets, restrooms, conference rooms, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 145880
0200ADA1 | SIDEWALK REPAIRS | 0200 | The concrete sidewalk on the south side of the building appears to have heaved significantly since it was installed. The transition from the sidewalk concrete to the existing concrete adjacent to the buildings south entrance has an elevation change of more than 1/2". This is on the accessible means of egress and should be remedied immediately. The concrete should be ground down to reduce the elevation change to less than 1/4". NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 1000
0200SFT3 | SEAL PENETRATIONS | 0200 | There are a number of penetrations through the chases and corridor walls for plumbing, data cables and cable trays. Many of these penetrations do not have smoke and fire sealing which corrupts the fire rated wall separations. This project provides funds to hire a qualified contractor to address penetration problems throughout the building. This project or a portion thereof was previously recommended in the FCA report dated 4/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 8/3/2010. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Immediate to Two Years | Currently Critical | 1 | 10000
0200INT4 | INTERIOR DOOR REPLACEMENT | 0200 | The majority of the interior doors in this building are damaged, difficult to operate, and have reached the end of their useful life. This project would provide for the installation of new interior doors including frames, lever action door handles, hardware, and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 100 interior doors was used in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
0200INT3 | CEILING SYSTEM REPLACEMENT | 0200 | The second and third floors of this building have a dated suspended acoustical tile ceiling system. The t-bar framing is bent and rusted in many areas and a number of the ceiling tiles are damaged and stained. This project would provide for the replacement of the suspended acoustical tile ceiling system. Removal and disposal of the existing ceiling system is included in this estimate. | BLASDEL OFFICE BUILDING | 9860 | Admin | PubWorks | B&G | Carson City | 1957 | 41680 | 2010-08-03 | Four to Ten Years | Long-Term Needs | 3 | 200000
0204ENV1 | BACKFLOW PREVENTION | 0204 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of a double check valve or reduced pressure principle backflow preventer for the fire sprinkler system which currently has only a single check valve. Costs include an above ground vault, and allowance for 50 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/24/2012. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 25000
0204EXT2 | GUTTER REPLACEMENT | 0204 | The existing gutters and downspouts around the building are due for replacement. The gutters leak and the downspouts are damaged in many areas. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with seamless gutter and replace the downspouts. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/24/2012. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0204ADA2 | INSTALL LEVER HARDWARE | 0204 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. It is recommended that compliant hardware be installed on all doors in this building to meet these guidelines. The estimate is based on purchase and installation of hardware for 12 doors. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 3000
0204EXT3 | EXTERIOR FINISHES | 0204 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the stucco and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. In addition, this project would repair damaged areas of the stucco and slump stone masonry. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/24/2012. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 25000
0204ADA1 | ADA RESTROOM UPGRADE | 0204 | The designated ADA restroom does not meet the Americans with Disabilities Act (ADA) requirements. For example, the water closet and lavatory are too low, the soap dispenser and mirror are too high, the lavatory is missing under-sink protection and the toilet seat cover dispenser is too high. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include compliant hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/24/2012. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 7500
0204SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0204 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/24/2012. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 4000
0204ENR2 | HVAC SYSTEM REPLACEMENT | 0204 | The HVAC system was installed in 1988 and is original to the building. It consists of two natural gas-fired furnaces and two outdoor condensers. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/24/2012. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0204PLM1 | WATER HEATER REPLACEMENT | 0204 | There is a 30 gallon gas-fired water heater in the building that was installed in 2004. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0204SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0204 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 3987
0204ADA3 | KITCHENETTE / BREAK ROOM REMODEL | 0204 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 7500
0204INT4 | FLOORING REPLACEMENT | 0204 | The carpet, sheet vinyl and painted concrete floors in the building are worn and are reaching the end of their useful life. It is recommended that the flooring be replaced and the concrete be repainted. This project would provide for painting of the concrete, removal and disposal of the existing vinyl and carpet and installation of new 12x12 VCT (vinyl composite tile) with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. Additional costs may be necessary to repair the concrete floor in the shop area. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31896
0204EXT4 | EXTERIOR DOOR / LANDING REPLACEMENT | 0204 | The exterior metal man door on the north side of the building is damaged from wear and tear due to improper grading / AC pavement placement at the landing. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware and proper exterior landing. Removal and disposal of the existing door is included in this estimate. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9862ADA1 | ADA PARKING SPACE | 9862 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CARSON CITY MOTOR POOL SITE | 9862 | Admin | PubWorks | B&G | Carson City | 0 |  | 2012-01-24 | Immediate to Two Years | Currently Critical | 1 | 2500
0204EXT5 | OVERHEAD DOOR REPLACEMENT | 0204 | There are three 10'x14' overhead doors which are damaged from age and general wear and tear. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with new manually operated insulated overhead doors. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9862SIT2 | DRAINAGE IMPROVEMENTS | 9862 | The site has several drainage problems around the site. On the north side the water drains towards the building and into one of the shop bays. On the perimeter of the site the runoff is directed across the public sidewalk creating a slip and fall hazard especially when it freezes. Several areas have standing water which causes premature deterioration of the paving. This project would create positive flow away from the building and to the storm drain system by regrading and installing French drains as needed. This project should be implemented concurrently with the SLURRY SEAL ASPHALT PAVING project. | CARSON CITY MOTOR POOL SITE | 9862 | Admin | PubWorks | B&G | Carson City | 0 |  | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9862SIT1 | SLURRY SEAL ASPHALT PAVING | 9862 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 22,789 square feet of asphalt area was used to generate this estimate. This project should be implemented concurrently with the DRAINAGE IMPROVEMENTS project. | CARSON CITY MOTOR POOL SITE | 9862 | Admin | PubWorks | B&G | Carson City | 0 |  | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17092
0204INT5 | JANITORS CLOSET REPAIRS | 0204 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0204INT3 | INTERIOR FINISHES | 0204 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CARSON CITY MOTOR POOL | 9862 | Admin | PubWorks | B&G | Carson City | 1988 | 3987 | 2012-01-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19935
0394HVA2 | BOILER REPAIRS | 0394 | At the time of the survey, one of the hot water boilers was not operating. The side panel had been removed and it was unclear why the boiler was not online. It is important to have both boilers in working condition to ensure that the building has constant service. This project would provide for labor and parts to repair the boiler. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0394HVA1 | PROVIDE CLEARANCE AROUND BOILER VENT | 0394 | The existing boiler vent is a stainless steel assembly with a clearance label stating clearances to combustibles. The penetration through the gypsum wall must have a "thimble" installed to provide clearance between the vent and the gypsum board. Note that gypsum board is classed as a "limited combustible" in the fire code. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 5000
9863SFT1 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 9863 | There are several sets of stair handrails around the exterior of the building that are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair. There is also a damaged rail near the north basement stairs that should be repaired. This project recommends the installation of handrails as needed in accordance with IBC Section 1012. This project will require the Nevada State Historic Preservation Office approval and excludes the plaza area on the north side of the property. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0394SFT3 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0394 | There are several sets of interior stair handrails throughout the building that are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports in accordance with the 2006 IBC Chapter 10, Section 1012. Approval of this project may be required by the Nevada State Historical Preservation Office. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 5000
0394EXT8 | EXTERIOR FINISHES | 0394 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are sealing and tuck pointing the masonry and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 261100
0394PLM2 | WATER HEATER REPLACEMENT | 0394 | There is a 40 gallon gas-fired water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1500
0394SFT2 | SAFETY CABINETS | 0394 | The storage room in the basement contains many different paints, stains and other hazardous products on open shelves and window sills. This does not meet OSHA standards for hazardous materials storage. This project would provide two hazardous material storage cabinets for the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0394INT4 | VCT FLOORING REPLACEMENT | 0394 | The VCT (vinyl composite tile) flooring in the 1st floor Men's and Women's restrooms is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2700
0394ADA3 | ADA CANE DETECTION BARRIER INSTALLATION | 0394 | The stairwell on the south side of the building has an overhead hazard at the cane detection area under the stairs. This project recommends the installation of a permanent barrier under the stairs. IBC - 2006 Section 1012 and ADAAG 4.4.2 were referenced for this project. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0394EXT10 | WINDOW REPLACEMENT | 0394 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 112 units including wooden frames which will require approval from the State Historical Preservation Office. Removal and disposal of the existing windows is included in this estimate. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 224000
0394EXT9 | ROOF REPAIRS | 0394 | The standing seam metal roof on this building has active leaks on the north and south sides of the building. The roof has been inspected and the cause of the problem has to do with the integral gutter system. The gutters have lost their waterproof coating due to exposure and should be replaced throughout the entire roof system. It is recommended that the gutters be repaired immediately. Additional costs are included in the estimate due to the steep pitch of the roof and the historical nature of the building. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 60000
0394INT2 | INTERIOR FINISHES | 0394 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 130550
9863SFT2 | GUARD INSTALLATION | 9863 | The east side approach to the loading dock area of the site has an elevation change from the concrete driveway to the natural grade below that exceeds 30 inches. This project recommends the installation of a guard to form a protective barrier along the open side in accordance with the 2006 IBC Chapter 10, Section 1013. Approval of this project will be required by the Nevada State Historical Preservation Office. 140 lineal feet was used to generate this estimate. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 7000
9863SIT3 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 9863 | The roof drain downspouts currently terminate within inches of the building and some do not have continuous drainage away from the building. This is causing the water to pool next to the building and causing damage to the building and surrounding concrete. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0394INT1 | REPLACE CARPET | 0394 | The carpet in the building, especially on the second and third floors, is beginning to show significant signs of wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77000
9863SIT2 | REMOVE AND REPLACE CONCRETE PAVING | 9863 | The existing concrete paving on the eastside adjacent to the loading dock and the west side of the building from the sidewalk to the entry stairs has deteriorated and is beginning to fail in some areas. There is cracking and settling which will continue to deteriorate and present potential tripping hazards. This project addresses removal and replacement of existing concrete as required. 3,600 square feet was used to generate this estimate. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
9863ADA1 | LAXALT PLAZA STAIR AND ADA MODIFICATIONS | 9863 | The Laxalt Plaza is constructed with paver stones. There are terraces with steps and a ramp along with seating areas for the public. This area also has the designated ADA accessible route from the parking stall to a platform lift. The platform lift does not have an ADA compliant landing at the lower level and the upper level platform lift door does not have the required forward approach clearance. The ADA ramp also does not have a compliant landing and a portion of the slope exceeds 8.3%. There are also some cross slopes that exceed 2%. There are some stair risers that exceed the 3/8" maximum uniformity requirement and some handrails are missing or non compliant on the stairs and ramp. The public table at the upper terrace is also not ADA compliant. This project would provide for the required modifications mentioned above including removal and reinstallation of the pavers as required, regrading, handrails and table modifications. This project will need to be approved by the Nevada State Historical Preservation Office. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 36000
9863SFT3 | INSTALL SEISMIC GAS SHUTOFF VALVE AND BOLLARDS | 9863 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. In addition, the project would install bollards and horizontal barriers to protect the gas meter and valves from damage. Note that the meter is located in the approach to the loading dock and is currently unprotected from collision. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING SITE | 9863 | Admin | PubWorks | B&G | Carson City | 1891 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 7500
0394EXT2 | REPLACE NORTH BASEMENT DOOR | 0394 | The exterior basement door on the North side is original to the building and is deteriorated with age. This door can no longer be considered secure and must be replaced to prevent unauthorized entry. This project would provide for the purchase and installation of a new hollow metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. Approval of this project may be required by the Nevada State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/05/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2009. | PAUL LAXALT STATE BUILDING | 9863 | Admin | PubWorks | B&G | Carson City | 1891 | 26110 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0397INT5 | INTERIOR FINISHES | 0397 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Four to Ten Years | Long-Term Needs | 3 | 212750
0397ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0397 | This building contains water fountains on each floor that are not accessible. The 2006 IBC Section 1109.5 states that on each floor, "No fewer than two drinking fountains shall be provided. One drinking fountain shall comply with the requirements for people who use a wheelchair and one drinking fountain shall comply with the requirements for standing persons." This project would provide funding for the purchase and installation of three new accessible fixed high/ low ADA drinking fountains to be installed on the 1st, 2nd and 3rd floors. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 12000
0397EXT2 | EXTERIOR FINISHES | 0397 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 212750
0397INT6 | JANITORS CLOSET REPAIRS | 0397 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of four Janitors Closets. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5600
0397ADA2 | ADA SIGNAGE | 0397 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0397ENR1 | WINDOW REPLACEMENT | 0397 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units including frames. This estimate is for the replacement of 10,270 square feet of glazing and associated frames. Removal and disposal of the existing windows is included in this estimate. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 821600
0397PLM1 | WATER HEATER REPLACEMENT | 0397 | There is a 98 gallon gas-fired water heater in the basement that was installed in 2004. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9864SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9864 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 30,000 square feet of asphalt area was used to generate this estimate. | CARSON CITY STATE OFFICES SITE | 9864 | Admin | PubWorks | B&G | Carson City | 1959 |  | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0397ADA3 | ADA ACCESSIBLE COUNTERS | 0397 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front offices on the 2nd and 3rd floors have a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space on the 2nd and 3rd floor in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CARSON CITY STATE OFFICES BUILDING | 9864 | Admin | PubWorks | B&G | Carson City | 1959 | 42550 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 2000
1478ENR1 | WATER HEATER REPLACEMENT | 1478 | The two 80 gallon gas fired water heaters are older units and should be scheduled for replacement. The average life span is 8-10 years. This project would provide for the installation of 2 new natural gas fired water heaters including seismic strapping and connections to utilities. Removal and disposal of the old units is included in this estimate. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1478EXT1 | EXTERIOR FINISHES | 1478 | It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including sealing the concrete precast panels, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Four to Ten Years | Long-Term Needs | 3 | 594500
1478INT1 | INTERIOR FINISHES | 1478 | The interior finishes are in good condition. This project would provide for the cyclical maintenance of the interior finishes including painting, staining, and any required cleaning and preparation of surfaces prior to the application of the finishes to maintain the integrity of the interior walls and ceilings including wood surfaces. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Four to Ten Years | Long-Term Needs | 3 | 594500
9865SIT2 | TERRACE REPAIRS | 9865 | The terrace on the southwest side of the site has a damaged waterproof membrane. Water is penetrating the membrane and leaking into the basement of the building below. Evidence of leaking can be seen in the mechanical room which may damage the walls, floor, and equipment. This project would provide for a general refurbishment of the terrace waterproof membrane including removing the existing stone tiles, repairing the substrate, caulking all penetrations, and reinstalling the tile. | SUPREME COURT SITE | 9865 | SupCourt | B&G |  | Carson City | 0 |  | 2011-04-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1478EXT2 | REPLACE MEMBRANE ROOF | 1478 | The existing single-ply roofing system is original to the construction of the building and should be scheduled for replacement in the next two years. The State wide roofing program's warranty is 15 years and has expired. This project would provide for the removal of the existing single-ply membrane and replacement with a new single-ply roofing system. 10,000 square feet of area was used to generate this estimate. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Immediate to Two Years | Currently Critical | 1 | 120000
1478INT3 | INSTALL FRP IN JANITOR'S CLOSET | 1478 | The mop sink in the Janitor's Closet is mounted adjacent to gypsum board that may cause water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
9865ADA1 | ADA SIGNAGE | 9865 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The site signage is not fully ADA compliant. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | SUPREME COURT SITE | 9865 | SupCourt | B&G |  | Carson City | 0 |  | 2011-04-14 | Immediate to Two Years | Currently Critical | 1 | 2500
1478INT2 | REPLACE RESTROOM FLOORING | 1478 | One of the ADA accessible restrooms on the second floor is damaged. This project would provide for the removal of the existing vinyl composition tile (VCT) and replacement with a new VCT floor in one restroom. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
9865SFT1 | SIDEWALK REPLACEMENT | 9865 | Some of the sidewalks serving the site and building entrances are deteriorated and beginning to fail in several areas. Most of the work needs to be done on the west side of the site where there is extensive spalling and some settling. A few sections have deteriorated enough to expose the reinforcing metal and the settling has created a tripping hazard. This project addresses removal and replacement of existing sidewalks as needed. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. | SUPREME COURT SITE | 9865 | SupCourt | B&G |  | Carson City | 0 |  | 2011-04-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9865SIT1 | PLANTER REPAIRS | 9865 | There are many built-in planters around the building. Several of them leak due to failed waterproof membranes and cracks in the concrete. There are also broken irrigation lines and areas with no vegetation. This project would provide for a general refurbishment of the planters including removing the existing dirt, fixing the cracks and irrigation lines, installing new waterproof membranes, filling the dirt back in and installing new plantings if desired. | SUPREME COURT SITE | 9865 | SupCourt | B&G |  | Carson City | 0 |  | 2011-04-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1478PLM1 | REPLACE TOILET FIXTURES | 1478 | The justices' restrooms date to the original construction of the building. The toilets are first-generation, water saving tank-flush models. Due to variations in the water pressure and other concerns, several of the toilets have had to be replaced. This project recommends the replacement of the remaining fixtures with new, pressure-assisted, low-gallonage models. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1478ADA1 | ADA ACCESSIBLE COUNTER | 1478 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are two offices that have a service counter for the public to approach which do not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space for each of these offices in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Immediate to Two Years | Currently Critical | 1 | 2000
1478ADA2 | ADA SIGNAGE | 1478 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Immediate to Two Years | Currently Critical | 1 | 6000
1478ENR2 | HVAC UPGRADE | 1478 | The central HVAC system in the building was installed in 1991. The equipment is not energy efficient and will be reaching the end of its expected and useful life within the next 10 years. This project would provide for installation of a new HVAC system including boilers, chillers, air handlers, fan coil units, water treatment, all associated equipment and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Four to Ten Years | Long-Term Needs | 3 | 2972500
1478SFT1 | ROOF SNOWMELT & SNOW RETAINMENT SYSTEM | 1478 | This building has a sloped metal roof with a snow melt and gutter system to capture rain water and retain snow from sliding off the roof. The existing snow guards have been sheared off in most locations causing snow to fall from the roof onto pedestrian walkways. This project would provide for the replacement of the snow melt system and installation of snow guards on the metal roofing system. This project or a portion thereof was previously recommended in the FCA report dated 08/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/14/2011. | SUPREME COURT | 9865 | SupCourt | B&G |  | Carson City | 1991 | 118900 | 2011-04-14 | Immediate to Two Years | Currently Critical | 1 | 95000
1675ENR1 | COOLING TOWER REPLACEMENT | 1675 | The building is cooled by a chiller and cooling tower system. The cooling tower and its associated equipment is non-operational and should be scheduled for replacement. Rust and water freezing in the pipes has greatly reduced the efficiency of the equipment. Three incidents of the heat transfer coil freezing have occurred since the tower was installed. This project provides for disposal of the existing equipment and replacement with a new cooling tower, heat exchanger and piping including connections to utilities. This project is currently funded under CIP 09-M01 but the contract had not been executed at the time of the survey of 2011.. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Immediate to Two Years | Currently Critical | 1 | 250000
1675SIT1 | LOADING DOCK REPAIR | 1675 | The existing loading dock on the west side of the building is damaged. There is exposed rebar and severely cracked concrete including the stairs and side retaining walls. This project would provide for the removal and replacement of the damaged steel, concrete walls, sidewalk and handrails. The existing lift is not included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Immediate to Two Years | Currently Critical | 1 | 100000
1675INT3 | CARPET REPLACEMENT | 1675 | The carpet in the Records Management Office is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
1675ADA1 | ACCESSIBLE DRINKING FOUNTAIN INSTALLATION | 1675 | This building contains four water fountains, one on the basement floor, two on the first floor and one on the second floor. Section 4.1.3 (10) of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states where one water fountain is provided on a floor it shall be accessible and where more than one is provided on a floor, 50% of those shall be accessible. This project would provide funding for the purchase and installation of three new accessible fixed high/ low ADA drinking fountains. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Immediate to Two Years | Currently Critical | 1 | 12000
1675PLM1 | WATER HEATER INSTALLATION | 1675 | The building's process hot water is supplied by the two boilers. The main purpose of the boilers is to heat the conditioned spaces during cold weather. The boilers run year round to support this configuration. It would be more economical and energy efficient to install a separate water heater for the process hot water supply. This would enable the boilers to be shut down when building heat is not necessary, reducing utility costs and extending the life of the boilers. There is a 73 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1675ADA4 | ADA SIGNAGE | 1675 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Immediate to Two Years | Currently Critical | 1 | 5000
1675SFT4 | FUME HOOD / VENTING MODIFICATIONS | 1675 | The existing fume hood is non-operational and the existing venting for the microfiche machine does not work properly. This project will provide funds for the repair of the fume hood exhaust fan and microfiche venting system. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Immediate to Two Years | Currently Critical | 1 | 2500
1675INT7 | DOOR HARDWARE REPLACEMENT | 1675 | The interior wood doors are in good shape, but staff has had continuous problems with the hardware. The handles, tumblers and locks on the doors are damaged from age and general wear and tear and have reached the end of their useful life. This project would provide for the replacement of the hardware on 173 doors. Removal and disposal of the existing hardware is included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86500
1675ENR5 | BOILER REPLACEMENT | 1675 | There are two hot water boilers that provide heating and process hot water to the building. They are original to the building and were manufactured in 1991. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 2,000 MBH output steel, natural gas fired, packaged water tube heating boiler. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Four to Ten Years | Long-Term Needs | 3 | 90000
1675EXT2 | EXTERIOR FINISHES | 1675 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, caulking of the windows, flashing, fixtures and all other penetrations and removing all of the climbing vines from the walls. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Re-pointing of the sandstone masonry on an as needed basis is included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 260000
1675ENR4 | LIGHTING UPGRADE | 1675 | The existing lighting fixtures are older T-8's, T-12's and sodium vapor HID's, and are not energy efficient. This project will upgrade T-8 lamps to super T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Occupancy sensors will be installed in restrooms, conference rooms, individual offices and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130000
1675ENR2 | CHILLER REPLACEMENT | 1675 | The building is cooled by a chiller and cooling tower system. The chiller is original to the building and is reaching the end of its useful life. It is recommended to schedule replacement of the chiller in the next 9-10 years. This project provides for disposal of the existing unit and replacement with a new 400 ton water cooled centrifugal chiller including connections to utilities. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Four to Ten Years | Long-Term Needs | 3 | 200000
1675INT8 | JANITORS CLOSET REPAIRS | 1675 | The mop sink in the basement Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Immediate to Two Years | Currently Critical | 1 | 1000
1675ENR3 | TEMPERATURE CONTROLS UPGRADE | 1675 | The existing temperature control system is obsolete and the manufacturer is no longer in business. Spare parts are no longer available, it is increasingly more difficult to maintain the equipment and it is not compatible with current computer operating systems. It is recommended to schedule replacement of the temperature control system in the next 2-3 years. This project provides for disposal of the existing equipment and replacement with a new temperature control system including connections to utilities. This project is currently funded under CIP 09-M14 but the contract had not been executed. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 650000
1675INT9 | SHELVING REPLACEMENT | 1675 | The static shelving in the State Records Center and in the State Archives room is reaching capacity and will no longer be able meet storage demands. In order to maintain control and security of the records it is recommended to replace the existing shelving with a new compact shelving system as opposed to utilizing offsite storage facilities. The new system will store twice as much material in the same amount of space. The estimate includes removal and disposal of existing shelving and purchase and installation of new compact shelving. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1100000
1675ADA2 | ADA RESTROOM UPGRADES | 1675 | The designated ADA restrooms on the first floor of the Library are not compliant. The doors do not meet space requirements, the flush handles are on the wrong side of the water closets and the pipes under the sinks are not protected. This project would provide for an automatic door opener for each door, automatic flush valves for the water closets and pipe protection. A survey by an ADA professional should be conducted to verify these findings and determine whether any additional work is required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Immediate to Two Years | Currently Critical | 1 | 15000
1675ELE1 | ELECTRICAL UPGRADE, CONFERENCE ROOM | 1675 | The electrical outlets in Conference Room A are located on a single breaker. This results in frequent tripping of the breaker when several pieces of equipment are in use. This project will provide additional capacity for branch circuits for the outlets. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1675SFT2 | FM 200 SUPPRESSION SYSTEM | 1675 | The building has Halon extinguishing systems for the Microfilm, Archives and Rare Documents rooms. The EPA banned manufacture of Halon in 1998, and this project addresses the replacement of the system. A water-based fire suppression system is not recommended for this location due to building contents. This project will provide for the design and installation of an FM 200 or equivalent system and disposal of the existing equipment and chemicals. The existing Halon could be sold to help offset the cost of this project. The current area appears to be constructed of fire resistive components but should be field verified prior to installation of this system. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
1675ENR6 | HUMIDIFICATION SYSTEM REPLACEMENT - ARCHIVES | 1675 | The Archives/ Records Center has six individual humidifiers mounted on the wall. They are original to the building, require frequent maintenance and only two or three of them are currently operating. The humidification system should be scheduled for replacement. It is recommended to re-engineer the entire system and install a new system based on the new design. The new design may include integration with the existing HVAC system or utilizing evaporative cooling for increased energy efficiency. This project or a portion thereof was previously recommended in the FCA report dated 07/25/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/11/2011. | NEVADA STATE LIBRARY & ARCHIVES | 9866 | Admin | PubWorks | B&G | Carson City | 1992 | 130000 | 2011-01-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
2450INT1 | INTERIOR FINISHES | 2450 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Four to Ten Years | Long-Term Needs | 3 | 602765
2450EXT2 | CONSTRUCT WIND BREAK | 2450 | The west entrance to the building has automatic sliding doors in an aluminum storefront system. The doors have been damaged and have had operational problems due to strong winds ever since the building was constructed. This project would provide for the installation of a windbreak structure near the west entrance to prevent the wind from damaging the doors. A CIP was requested by the agency for FY 2009 in the amount of $132,000, but it was not known at the time of the survey whether this project would be approved. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Immediate to Two Years | Currently Critical | 1 | 132000
2450HVA1 | HVAC ALTERATIONS | 2450 | The server rooms throughout the building are often overheated which can lead to premature failure of the systems. The rooms are not on a separate HVAC system from the common office areas nearby. This project would provide for alterations to the HVAC system to isolate the server rooms from the common office areas. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9867SIT1 | SLURRY SEAL ASPHALT PAVING - MAIN LOT | 9867 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the main parking lot. Striping is included in this estimate. It is recommended that this project be implemented in the next 2 to 3 years and should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 125,000 square feet of asphalt area was used to generate this estimate. | RICHARD H. BRYAN SITE | 9867 | Admin | PubWorks | B&G | Carson City | 2005 |  | 2018-07-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 93750
9867SIT2 | SLURRY SEAL ASPHALT PAVING - EAST LOT | 9867 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the East parking lot. Striping is included in this estimate. It is recommended that this project be implemented in the next 4 to 5 years and should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 25,000 square feet of asphalt area was used to generate this estimate. | RICHARD H. BRYAN SITE | 9867 | Admin | PubWorks | B&G | Carson City | 2005 |  | 2018-07-31 | Four to Ten Years | Long-Term Needs | 3 | 18750
2450EXT1 | EXTERIOR FINISHES | 2450 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RICHARD H. BRYAN BUILDING | 9867 | Admin | PubWorks | B&G | Carson City | 2005 | 120490 | 2018-07-31 | Four to Ten Years | Long-Term Needs | 3 | 602765
1475ENR1 | LIGHTING UPGRADE | 1475 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in all areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1950
1475SFT1 | FIRE ALARM SYSTEM INSTALLATION | 1475 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 5200
2989EXT1 | EXTERIOR FINISHES | 2989 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HEADQUARTERS & LAB | 9868 | Agricult | Agri |  | Sparks | 2009 | 25913 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129565
1475SFT2 | FIRE EXTINGUISHER INSTALLATION | 1475 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in S occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 1000
1475SFT3 | ELECTRICAL UPGRADE | 1475 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
1475PLM2 | WATER HEATER REPLACEMENT | 1475 | There is a 30 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1475SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1475 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 4000
2989INT1 | INTERIOR FINISHES | 2989 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS & LAB | 9868 | Agricult | Agri |  | Sparks | 2009 | 25913 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129565
2990EXT1 | EXTERIOR FINISHES | 2990 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CENTRAL PLANT | 9868 | Agricult | Agri |  | Sparks | 2009 | 920 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
2990INT1 | INTERIOR FINISHES | 2990 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CENTRAL PLANT | 9868 | Agricult | Agri |  | Sparks | 2009 | 920 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
2991INT1 | INTERIOR FINISHES | 2991 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE/CARPORT BUILDING | 9868 | Agricult | Agri |  | Sparks | 2009 | 7151 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13650
2992INT1 | INTERIOR FINISHES | 2992 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to sealing, all surfaces should be repaired and prepped. | GREEN HOUSE | 9868 | Agricult | Agri |  | Sparks | 2009 | 1274 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6370
1475INT2 | RESTROOM REMODEL | 1475 | The restroom in the building was out of service at the time of the survey. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9868SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9868 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 34,000 square feet of asphalt area was used to generate this estimate. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20400
2991EXT1 | EXTERIOR FINISHES | 2991 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE/CARPORT BUILDING | 9868 | Agricult | Agri |  | Sparks | 2009 | 7151 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35755
0274ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0274 | This building contains a water fountain that is not ADA compliant and is not working. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 4000
2996INT1 | INTERIOR FINISHES | 2996 | The interior finishes are in fair condition. It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PLANT PATHOLOGY/ELECTRICAL | 9868 | Agricult | Agri |  | Sparks | 2009 | 2175 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10875
2996EXT1 | EXTERIOR FINISHES | 2996 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | PLANT PATHOLOGY/ELECTRICAL | 9868 | Agricult | Agri |  | Sparks | 2009 | 2175 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10875
9868ADA1 | ADA SIGNAGE & STRIPING | 9868 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The accessible parking spaces and passenger loading areas in front of the Measurement Standards building are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 2500
0274INT2 | INTERIOR FINISHES | 0274 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33110
0274EXT3 | EXTERIOR DOOR REPLACEMENT | 0274 | The exterior man doors on the original structure are damaged from age and general wear and tear. This includes the front entrance door and three metal man doors on the east elevation. This project would provide for the replacement of four exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0274EXT2 | EXTERIOR FINISHES | 0274 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33110
0274INT3 | EMPLOYEE LOUNGE INSTALLATION | 0274 | The building was not originally equipped with an Employee Lounge for the employees. This project recommends installing cabinets, a sink, GFCI outlets for small appliances and tables and chairs. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1475EXT3 | OVERHEAD DOOR REPLACEMENT | 1475 | There is a 16'x20' overhead door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead door and replacement with a motorized door. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0274SFT1 | EXIT SIGN UPGRADE | 0274 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 3150
0274PLM2 | WATER HEATER REPLACEMENT | 0274 | There is a 30 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0274SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0274 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Immediate to Two Years | Currently Critical | 1 | 4000
1475EXT1 | EXTERIOR FINISHES | 1475 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1300
1475INT1 | INTERIOR FINISHES | 1475 | The interior finishes are in poor condition. It is recommended to repair the insulation and paint the gypsum board walls at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
1475EXT2 | EXTERIOR DOOR REPLACEMENT | 1475 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | AGRICULTURE WAREHOUSE | 9868 | Agricult | Agri |  | Sparks | 1960 | 1300 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0274EXT4 | ROOF REPLACEMENT | 0274 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | MEASUREMENT STANDARDS | 9868 | Agricult | Agri |  | Sparks | 1971 | 6622 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 78504
2992EXT1 | EXTERIOR FINISHES | 2992 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the translucent panels, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GREEN HOUSE | 9868 | Agricult | Agri |  | Sparks | 2009 | 1274 | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6370
9868SIT4 | RELOCATE MAIN ENTRY | 9868 | The main entry to the site is very close to the intersection of Galletti Way and Kietzke Lane. This project would relocate the entry south along Galletti to make access in and out of the site safer during heavy traffic. The project would provide new curb and gutter, concrete apron, fencing, and a new gate. This project should be implemented concurrently with the Fence Replacement project. This project or a portion thereof was previously recommended in the FCA report dated 10/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/05/2014. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9868SIT3 | FENCE REPLACEMENT | 9868 | The majority of the fencing around the Warehouse/ Equipment Yard has failed and is due for replacement. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with two 14' wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. This project should be implemented concurrently with the Relocate Main Entry project. This project or a portion thereof was previously recommended in the FCA report dated 10/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/05/2014. | AGRICULTURE HEADQUARTERS OFFICE SITE | 9868 | Agricult | Agri |  | Sparks |  |  | 2014-11-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
2454ADA1 | ADA RESTROOM UPGRADES | 2454 | The designated ADA restroom does not fully comply with the Americans with Disabilities Act (ADA) requirements. The seat cover dispenser is not in an accessible location and the condensation drain attached to the sink drain interferes with the required clear space under the sink. This project would provide funding for relocating the seat cover dispenser to a compliant location and relocating the condensation drain from under the sink. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV INSPECTION STATION | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 744 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 750
2453HVA1 | COOLING TOWER REPAIRS | 2453 | The cooling tower has extensive scaling on the film fill media and the plastic film fill is brittle and broken in many areas. This will cause underperformance of the cooling tower and premature failure. It is recommended to remove the and replace the film fill media to bring the cooling tower back into prime operating condition. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2454INT1 | INTERIOR FINISHES | 2454 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV INSPECTION STATION | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 744 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3710
2453INT1 | INTERIOR FINISHES | 2453 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118085
2453EXT1 | EXTERIOR FINISHES | 2453 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and EIFS, cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes are addressed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 118085
9869ADA1 | ADA UPGRADES | 9869 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. For example, the 15 existing parking signs indicate a $100 fine which has been raised to a $250 minimum fine. This project would provide for striping, signage and any other necessary upgrades to the parking space. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | NORTH DECATUR DMV SITE | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 |  | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2500
9869SIT1 | SEAL ASPHALT PAVING | 9869 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 300,000 square feet of asphalt area was used to generate this estimate. | NORTH DECATUR DMV SITE | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 |  | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
2453INT3 | LOBBY TILE FLOORING REPLACEMENT | 2453 | The terrazzo tile flooring in the main Lobby is severely damaged throughout and should be scheduled for replacement. The tiles are breaking at the corners, the grout is failing and there are significant cracks across large sections of tiles. This is a heavily used area and could pose a safety issue with potential tripping hazards to the public and employees. This project would provide for removal and disposal of the existing tile and installation of new tile with a 6" cove base. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 135000
2453ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 2453 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 2000
2453INT2 | CARPET REPLACEMENT | 2453 | The carpet in the building is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
2454EXT1 | EXTERIOR FINISHES | 2454 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building finishes are addressed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV INSPECTION STATION | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 744 | 2018-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3720
2453ADA2 | ADA SIGNAGE | 2453 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | NORTH DECATUR DMV SERVICES CENTER | 9869 | MtrVeh | B&G | MtrVeh | Las Vegas | 2006 | 23568 | 2018-12-10 | Immediate to Two Years | Currently Critical | 1 | 1500
2463SFT1 | HANDRAIL INSTALLATION | 2463 | The 2003 International Building Code 1009.11 requires handrails on each side of stairways. The building has a set of stairs to access the residence on the north side and south side which do not have handrails. This project would provide for the purchase and installation of handrails on each side of the stairways. | MOAPA/MESQUITE NHP RESIDENCE | 9873 | PubSafe | NHP |  | Moapa | 0 | 1440 | 2006-03-21 | Immediate to Two Years | Currently Critical | 1 | 4000
2566ADA0 | ACCESSIBLE BUILDING ENTRANCE | 2566 | The building has steps leading into the main entrance. The entrance does not meet the requirements for ADA Accessibility ICC/ANSI A117.1-1998 404.2.4.1. The entry door has a threshold and hardware that does not meet the requirements for ADA accessibility, ICC/ANSI A117.1-1998 404.2.5. This project would provide funding for an accessible ramp, including upper and lower landing areas, handrails, curbing, and replacement of the door hardware and threshold to meet the ADA Accessibility Guidelines. The ramp construction used in this estimate is metal and would be considered a portable type ramp. | MOAPA/MESQUITE NHP OFFICE | 9873 | PubSafe | NHP |  | Moapa | 2000 | 720 | 2006-03-21 | Immediate to Two Years | Currently Critical | 1 | 15000
2566EXT1 | SKIRTING | 2566 | The skirting around the module building protects the pipes and fixtures from the elements, reduces updrafts, helps controls moisture and reduces energy costs. The building does not have skirting around the perimeter. This project would provide for the purchase and installation of skirting around the modular office trailer. This project includes painting to match existing conditions. | MOAPA/MESQUITE NHP OFFICE | 9873 | PubSafe | NHP |  | Moapa | 2000 | 720 | 2006-03-21 | Four to Ten Years | Long-Term Needs | 3 | 14400
9873ADA1 | ADA PARKING AND SIGNAGE | 9873 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A parking area, an adjacent passenger loading area and signage are necessary to comply with ADA requirements. This project would provide for one ADA accessible parking space, including an adjacent passenger loading zone in the existing paved parking area. The project includes signage, striping and marking an accessible route of travel to the building. | MOAPA/MESQUITE NHP SUBSTATION SITE | 9873 | PubSafe | NHP |  | Moapa | 0 |  | 2006-03-21 | Immediate to Two Years | Currently Critical | 1 | 3000
9874SIT3 | SHRUB REMOVAL | 9874 | There are some shrubs and trees along the south side of the building which are too close to the exterior wall. This project would provide for the removal of the shrubs and trimming of the trees along the south side of the facility. | NEVADA STATE MUSEUM INDIAN HILLS SITE | 9874 | CultAffr | M&H | Museums | Carson City | 0 |  | 2013-03-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
2563LGT1 | PAINT WATER TANK | 2563 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior tank envelope, including sand blasting, painting, staining, or other applied finishes and other penetrations to maintain the tank in good, weather tight condition. This project should be performed on a cyclical basis. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WATER TOWER | 9874 | CultAffr | M&H | Museums | Carson City | 1981 | 530 | 2013-03-07 | Four to Ten Years | Long-Term Needs | 3 | 15000
9874SIT2 | ASPHALT CONCRETE REHABILITATION | 9874 | The existing paved parking area is in poor condition. Signs of paving failure are evident with large cracks and alligatoring visible. This project recommends filling in the cracks, remove and replace damaged areas, extend the paved area to the edge of the building and applying a slurry seal and re-striping the onsite parking area and access road. The re-striping should include ADA parking/striping, loading zones and accessible route of travel from parking to the Warehouse Building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | NEVADA STATE MUSEUM INDIAN HILLS SITE | 9874 | CultAffr | M&H | Museums | Carson City | 0 |  | 2013-03-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
0860EXT7 | EXTERIOR PAINTING / FINISHES | 0860 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finishes on the building is starting to peel and blister. This project would provide for protection of the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46320
0860PLM2 | SINK DRAINAGE / WASTE PIPE | 0860 | The 2012 UPC requires "all plumbing fixtures, drains, appurtenances and appliances used to receive or discharge liquid wastes or sewage shall be directly connected to the sanitary drainage system." The sink located in the south warehouse drains directly into the field adjacent to the structure. This project would provide for the drainage system of the sink to be connected to the sanitary drainage line. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 1200
0860EXT1 | EXTERIOR ENERGY RETROFIT | 0860 | The building is constructed of concrete masonry units (CMU) with no insulation. Buildings of this type are not energy efficient. This project would provide for the purchase and installation of adding an exterior insulating finish system (EIFS) over the CMU and replacing the exterior doors. This work will make the building more energy efficient and should concur at the same time the HVAC renovation occurs. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Four to Ten Years | Long-Term Needs | 3 | 310000
0860INT1 | LEVER ACTION DOOR HANDLE INSTALLATION | 0860 | The existing doors in this facility have locking knob-type door hardware. The locks on the doors are sticking and do not operate properly. This project would provide for the purchase and installation of locking lever action door handles to be placed on all the doors in the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 7500
0860PLM1 | SEPTIC TANK SERVICE | 0860 | The septic tank has not been inspected or pumped for the past 10 years according to staff. This project would provide for the septic tank to be inspected and pumped. This project should be done on a cyclical basis. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 750
0860SFT5 | FIRE-RATED DOOR ASSEMBLY | 0860 | The building has a 1-hour fire wall assembly located between the warehouse and staging area. The existing set of double doors are not fire rated. The double door does not meet the criteria of IBC -2012 Chapter 715. This project would provide for purchase and installation of a new 1- hour fire rated double door and frame assembly including smoke seals and all hardware. Removal of the existing door and painting of the new door are included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 3800
0860HVA1 | HVAC UPGRADE / INSTALLATION | 0860 | The warehouse section is equipped with six hanging gas force furnaces and no air-conditioning. Two of the furnaces were not working properly at the time of the survey. During accreditation by the American Association of Museums (AAM) in 2003, it was recommended that the warehouse area have an HVAC system for maintaining a proper interior environment for artifact storage. This project would provide for a complete HVAC system to be installed in the building including air handlers, duct work, connections to existing utilities seismic bracing and an energy managements system. Design of the system is not included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 231600
0859EXT1 | EXTERIOR FINISHES | 0859 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building should be painted in the next year. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS PUMP HOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1981 | 400 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 2000
0860EXT0 | RAIN GUTTER INSTALLATION | 0860 | The building does not have any rain gutters and down spouts to prevent water from flooding around the building especially at entrance and exit pathways. This can cause damage to the exterior finish of the building. This project would provide for the purchase and installation of seamless gutters and down spouts to divert the water away from the building and building entrances and exits. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Four to Ten Years | Long-Term Needs | 3 | 2500
0860SEC1 | INTERCOM AND CAMERA INSTALLATION | 0860 | The building is surrounded by a 6’chain link fence. There is an access gate to enter the site and buildings. The gate is kept locked for security reasons. There should be communication from the gate to the office area. This project would provide funding for the purchase and installation of a surveillance and communication system from the gate to the office area including a camera and intercom with connections to utilities as required. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Four to Ten Years | Long-Term Needs | 3 | 10000
0860SFT4 | CONCRETE REPAIR - EPOXY SYSTEM | 0860 | The concrete floors in the building have cracks, some over an inch wide, in several locations. The cracks create safety issues when pulling/pushing a cart. This project would provide for cleaning and epoxy sealing of the cracks in the concrete floor. This project or a portion there of was previously recommended in the FCA report dated 02/12/2003 and 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0860STR1 | MEZZANINE ASSESSMENT | 0860 | The mezzanine contains numerous code and safety issues including but not limited to access stairs, guardrails and handrails, ceiling height, systems and structural loading of the floor. This project recommends a structural assessment of the entire mezzanine due to lack of drawings or information on the construction. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 1500
0859EXT2 | INSTALL LANDING | 0859 | The entrance door to the pump house does not have an exterior concrete landing. IBC-2003 Chapter 1008.1.4 requires a landing on each side of a door. Landings shall be at the door elevation on each side. This project would provide for the installation of a concrete landing not less than the width of the door and 44 inches for the length in travel. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS PUMP HOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1981 | 400 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 500
0860SFT7 | INSTALL SEISMIC GAS SHUT OFF VALVE | 0860 | The State's Underwriter recommends installing a Seismic Gas Shutoff Valve on each gas service to improve the insurability of State facilities. The valves are installed between the gas meter and the building or equipment served to shut off the gas supply in the event of an earthquake. This project would provide for a seismic gas shutoff valve on the gas line serving the building. This project or a portion there of was previously recommended in the FCA report dated 03/01/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/07/2013. | INDIAN HILLS WAREHOUSE | 9874 | CultAffr | M&H | Museums | Carson City | 1980 | 15440 | 2013-03-07 | Immediate to Two Years | Currently Critical | 1 | 3500
2559PLM1 | INSTALL WATER HEATERS | 2559 | There are two gas fired water heaters that are approaching the end of their useful life and should be scheduled for replacement. This project would provide for the purchase and installation of two gas fired water heaters including required connections to existing utilities. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2559EXT1 | EXTERIOR FINISHES | 2559 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 143965
9875SIT1 | CRACK FILL / SEAL ASPHALT PAVING | 9875 | The existing asphalt concrete paving on site is in good condition. This project would provide for crack filling as needed and sealing and striping the pavement in the next three to four years including striping all loading zones and ADA accessible parking spaces and route of travel. This project should be completed on a cyclical basis based on environmental conditions and use. | CASA GRANDE TRANSITIONAL CENTER SITE | 9875 | Correct |  |  | Las Vegas | 2005 |  | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58242
9875ADA1 | ADA PARKING SIGNAGE | 9875 | The existing ADA accessible parking signage is not up to current standards. This project would provide for new stickers reflecting the most current maximum fine information to be installed on the existing signs. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CASA GRANDE TRANSITIONAL CENTER SITE | 9875 | Correct |  |  | Las Vegas | 2005 |  | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 450
2560PLM1 | INSTALL WATER HEATERS | 2560 | There are two gas fired water heaters that are approaching the end of their useful life and should be scheduled for replacement. This project would provide for the purchase and installation of two gas fired water heaters including required connections to existing utilities. Removal and disposal of the existing equipment is included in this estimate. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2561PLM1 | INSTALL WATER HEATERS | 2561 | There are two gas fired water heaters that are approaching the end of their useful life and should be scheduled for replacement. This project would provide for the purchase and installation of two gas fired water heaters including required connections to existing utilities. Removal and disposal of the existing equipment is included in this estimate. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2561EXT1 | EXTERIOR FINISHES | 2561 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 132540
2560EXT1 | EXTERIOR FINISHES | 2560 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 132540
2559CUL1 | REPLACE STEAM KETTLE | 2559 | The existing steam kettle in the culinary is no longer in service. The unit has failed and is in need of replacement. This project would provide for a new gas fired tilting steam kettle to be purchased and installed. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 16000
2559INT1 | INTERIOR FINISHES | 2559 | The interior finishes are in fair condition. It is recommended that the interior walls, ceilings, doors, frames, steel stairs and exposed steel framing be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION BUILDING A | 9875 | Correct |  |  | Las Vegas | 2005 | 26598 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 143965
2560ADA1 | ADA MODIFICATIONS | 2560 | The restrooms in the building are not 100% ADA compliant. This project would provide for improvements including but not limited to flush valve relocation and ADA compliant shower seat and fixture installation in the restrooms. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 1500
2560INT1 | INTERIOR FINISHES | 2560 | The interior finishes are in fair condition. It is recommended that the interior walls, ceilings, doors, frames, steel stairs and exposed steel framing be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENTIAL BUILDING B | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Four to Ten Years | Long-Term Needs | 3 | 132540
9875ADA2 | ADA ROUTE OF TRAVEL | 9875 | The ADA accessible route of travel at the west parking area ADA parking spaces has a non compliant step or change in elevation from the paving to the sidewalk. This project would provide for necessary repairs to be made to eliminate the step. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CASA GRANDE TRANSITIONAL CENTER SITE | 9875 | Correct |  |  | Las Vegas | 2005 |  | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 500
2561INT1 | INTERIOR FINISHES | 2561 | The interior finishes are in fair condition. It is recommended that the interior walls, ceilings, doors, frames, steel stairs and exposed steel framing be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132540
2561ADA1 | ADA MODIFICATIONS | 2561 | The restrooms in the building are not 100% ADA compliant. This project would provide for improvements including but not limited to flush valve relocation and ADA compliant shower seat and fixture installation in the restrooms. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RESIDENTIAL BUILDING C | 9875 | Correct |  |  | Las Vegas | 2005 | 30484 | 2013-05-02 | Immediate to Two Years | Currently Critical | 1 | 1500
9878SIT4 | SITE DRAINAGE IMPROVEMENTS | 9878 | There are many areas around the site where the grade does not properly slope away from the buildings. Rain accumulates adjacent to the buildings, creating a water problem which may infiltrate the interior during inclement weather. There is soil to wood contact and soil to metal contact which will cause premature deterioration to the building. This project would provide funding to re-grade these problem areas to create a positive slope away from the building and to eliminate any direct soil contact. This project or a portion thereof was previously recommended in the FCA report dated 02/25/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 3000
9878ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9878 | There is no site lighting for the access roads and parking areas which is a security and safety concern. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete base. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 02/25/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
2033HVA1 | AIR CONDITIONER INSTALLATION | 2033 | The server room is not sufficiently cooled by the existing HVAC system. At the time of the survey, a ceiling tile was removed in the room to increase circulation. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2033EXT1 | EXTERIOR FINISHES | 2033 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
9878SIT7 | CRACK FILL & SEAL ASPHALT PAVING | 9878 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 25,000 square feet of asphalt area was used to generate this estimate. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Four to Ten Years | Long-Term Needs | 3 | 15000
9878SEC1 | SECURITY FENCE INSTALLATION | 9878 | The chain link perimeter fence is currently around the rear parking area only. For security purposes, the staff has requested to install a security fence around the rest of the property with card-controlled access gates at the street. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the front perimeter with two 14' wide gates with hardware. | CNR / WILDLIFE OFFICES LAS VEGAS SITE | 9878 | CNR | Forestry |  | Las Vegas | 0 |  | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 50000
1989EXT1 | EXTERIOR FINISHES | 1989 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
1989INT1 | INTERIOR FINISHES | 1989 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13500
1989ELE2 | ENCAPSULATE GROUNDING WIRE | 1989 | There is a copper grounding wire in the north west corner of the warehouse that is laying on the floor and exposed. The maintenance staff was unsure of where the wire came from and what its purpose is. The wire should be encapsulated in conduit and terminated near the wall for safety. This project would provide for a licensed electrician to encapsulate and terminate the wire properly and determine what its purpose is. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 1500
2033INT1 | INTERIOR FINISHES | 2033 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
2033EXT3 | ROOF REPLACEMENT | 2033 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. Repairs have been made recently as shingles have broken or blown off in the wind. The wood eaves have lost their finish and the wood has dried out. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. Additional costs are provided to replace the wood eaves. This estimate includes removal and disposal of the old roofing. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
2033PLM1 | FLOOR DRAIN REPAIRS | 2033 | The floor drain in the Women's restroom constantly emits a foul smell. It is not known whether there is a proper p-trap for the drain. The staff pours buckets of water into the drain to dissipate the smell. This project would provide for a licensed contractor to inspect and repair the drain to prevent any further odors coming from the drain. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 1500
2033PLM2 | WATER HEATER REPLACEMENT | 2033 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1989SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1989 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 4000
2033SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2033 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 4000
2033LGT2 | CARPET REPLACEMENT | 2033 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31500
2033EXT2 | RAIN GUTTER INSTALLATION | 2033 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the dirt planters around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | NDF/STATE PARKS OFFICE BUILDING | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 5974 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1989EXT2 | ROOF REPLACEMENT | 1989 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 5-6 years to be consistent with the roofing program and the end of the warranty period. | WAREHOUSE/SHOP | 9878 | CNR | Forestry |  | Las Vegas | 2000 | 4500 | 2014-01-30 | Four to Ten Years | Long-Term Needs | 3 | 32400
0704SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0704 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
0704SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0704 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 22400
0704SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0704 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7, the 2006 International Fire Code and NAC 477.917. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 11200
0704EXT6 | EXTERIOR FINISHES | 0704 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, sanding, priming and painting the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Four to Ten Years | Long-Term Needs | 3 | 12000
0704INT3 | INTERIOR FINISHES | 0704 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0704PLM3 | WATER HEATER REPLACEMENT | 0704 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0260EXT5 | ROOF ALTERATIONS | 0260 | The tree on the northwest side of the building is touching the roof eave and will eventually damage the roof. The tree will continue to grow and potentially cause leaks in the roof and structural damage. The tree provides shade to the building and is a positive environmental feature for the site. This project would provide for altering the roof in order to accommodate the tree. A structural design will be necessary to ensure that the eave loads are properly transferred and it is recommended that this project be coordinated with the roofing project. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 7500
0704ENR3 | HVAC EQUIPMENT REPLACEMENT | 0704 | The FAU unit is showing signs of wear. It is not energy efficient and has reached the end of its expected and useful life. There is no energy management system (EMS) for the building. This project would provide for installation of an EMS, a new FAU unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. The air conditioning condenser is fairly new and not included in this project. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0260PLM2 | BACKFLOW PREVENTION | 0260 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault and allowance for 200 feet of 1" conduit to provide power for freeze protection. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 25000
0704ADA2 | ADA SIGNAGE | 0704 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 600
0260ENR3 | EXTERIOR DOOR REPLACEMENT | 0260 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project does not include the storefront system doors at the entrance to the building. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0704EXT5 | EXTERIOR DOOR REPLACEMENT | 0704 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0260SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0260 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
0260ADA1 | ADA SIGNAGE | 0260 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 1000
0260SFT4 | EXTERIOR LANDING INSTALLATION | 0260 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing. This does not comply with 2006 IBC Section 1008.1 which requires a proper landing and for the landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 500
0260SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0260 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7, the 2006 International Fire Code and NAC 477.917. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 35924
0260SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0260 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 71848
0260ENR4 | HVAC EQUIPMENT REPLACEMENT | 0260 | The three ground mounted HVAC packaged units are showing signs of wear. They are not energy efficient and have reached the end of their expected and useful life. There is no energy management system (EMS) for the building. This project would provide for installation of an EMS, three new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0704ENR1 | EXTERIOR INSULATION & FINISH SYSTEM | 0704 | The building is constructed of brick masonry with no insulation. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation and finish system (EIFS) over the brick masonry. The estimate is based on $10.00 per square foot for the EIFS. It is recommended that this project be coordinated with the exterior door and window replacement projects. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 16000
0260PLM3 | WATER HEATER REPLACEMENT | 0260 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0260ENR1 | LIGHTING UPGRADE | 0260 | The existing lighting fixtures are the older fluorescent type and are not energy efficient. The existing lighting also needs to be redesigned to accommodate the buildings current usage. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings and fixture locations will be altered based on current needs. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12830
0260EXT4 | EXTERIOR FINISHES | 0260 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, sanding, priming and painting the wood siding, and caulking of the windows, flashing, fixtures, and all other penetrations. It is recommended that the building be sealed, painted, and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35924
0260EXT1 | GUTTER INSTALLATION AND EAVE REPAIRS | 0260 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing flooding and erosion to the flower beds and grade around the building. The fascia, trim and soffits are damaged and should be repaired at the same time. This project would provide funding for the installation of a seamless gutter and downspout system for the building and repairing or replacing the fascia, trim and soffits as needed. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0260ENR2 | WINDOW REPLACEMENT | 0260 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 30 units. Removal and disposal of the existing windows is included in this estimate. It is recommended that this project be coordinated with the EIFS project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0260EXT3 | ROOF REPLACEMENT | 0260 | The ballasted roof on this building was in fair condition at the time of the survey. Based on age it should be scheduled for replacement in the next two to three years with a single-ply roofing membrane system which will bring the roof into the Statewide roofing warranty and preventative maintenance agreement program. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76980
0260PLM1 | RESTROOM REMODEL | 0260 | The restroom fixtures in the four restrooms other than the ADA restroom are older and in overall poor condition. The finishes, fixtures, cabinets, sinks, toilets, mirrors and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0704SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0704 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 2500
0260INT2 | FLOORING REPLACEMENT | 0260 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. It is likely that the mastic used for the VCT and linoleum has asbestos in it. This estimate includes additional funds for proper asbestos abatement including removal, disposal and monitoring. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0260SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0260 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of LED exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 2500
0704EXT1 | INSTALL RAIN GUTTERS REPAIR/REPLACE FASCIA | 0704 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing flooding and erosion to the flower beds and grade around the building. The fascia, trim and soffits should be repaired at the same time. This project would provide funding for the installation of a seamless gutter and downspout system for the building and repairing or replacing the fascia, trim and soffits as needed. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0704ENR2 | WINDOW REPLACEMENT | 0704 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
0704EXT3 | ROOF REPLACEMENT | 0704 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 7-10 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Four to Ten Years | Long-Term Needs | 3 | 24000
0260INT3 | INTERIOR FINISHES | 0260 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25660
0704ADA1 | ADA RESTROOM UPGRADE | 0704 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring, and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | WILDLIFE OFFICE ANNEX | 9878 | Wildlife |  |  | Las Vegas | 1971 | 1740 | 2010-02-25 | Immediate to Two Years | Currently Critical | 1 | 25000
0260ENR5 | EXTERIOR INSULATION & FINISH SYSTEM | 0260 | The building is constructed of brick masonry with no insulation. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation and finish system (EIFS) over the brick masonry. The estimate is based on $10.00 per square foot for the EIFS. It is recommended that this project be coordinated with the exterior door and window replacement projects. This project or a portion thereof was previously recommended in the FCA report dated 1/1/2002. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/25/2010. | NDOW REGIONAL OFFICE | 9878 | Wildlife |  |  | Las Vegas | 1967 | 5344 | 2010-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1964EXT1 | EXTERIOR FINISHES | 1964 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC PAINT BOOTH | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1120 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
9879SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9879 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and maintenance yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 500,000 square feet of asphalt area was used to generate this estimate. | FLOYD EDSALL TRAINING CENTER SITE | 9879 | Military | NNG |  | North Las Vegas | 0 |  | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
1962INT1 | INTERIOR FINISHES | 1962 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC ARMORY STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 2430 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12150
1962EXT1 | EXTERIOR FINISHES | 1962 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC ARMORY STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 2430 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12150
1963INT1 | INTERIOR FINISHES | 1963 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1950 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9750
1964INT1 | INTERIOR FINISHES | 1964 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC PAINT BOOTH | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1120 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5600
2023INT1 | INTERIOR FINISHES | 2023 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC USFPO WAREHOUSE | 9879 | Military | NNG |  | North Las Vegas | 1997 | 5600 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
2023EXT1 | EXTERIOR FINISHES | 2023 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC USFPO WAREHOUSE | 9879 | Military | NNG |  | North Las Vegas | 1997 | 5600 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
2546EXT1 | EXTERIOR FINISHES | 2546 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC GUARD SHACK | 9879 | Military | NNG |  | North Las Vegas | 0 | 64 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
9879SIT4 | SITE DRAINAGE UPGRADES | 9879 | Recent (October 2012) heavy rains exposed drainage problems around the site. The grade does not slope away from the buildings effectively which allowed water to infiltrate all of the buildings to some extent. The perimeter block wall has drainage outlets that quickly clogged up with dirt and debris and prevented water from flowing off property. This project would create positive flow away from the buildings by regrading, paving, installing additional drainage swales as needed and enlarging the outlets in the block wall. | FLOYD EDSALL TRAINING CENTER SITE | 9879 | Military | NNG |  | North Las Vegas | 0 |  | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
2551PLM1 | WATER TOWER MAINTENANCE | 2551 | The tower was installed almost 20 years ago and is due for cyclical maintenance and parts replacement. It provides drinking water for the staff and soldiers as well as water for fire protection. The interior and exterior coatings are breaking down and the pumps and associated controls are unreliable. This breakdown of the coatings can cause the water to become contaminated and the unreliable pumps and controls are a life safety risk. This project would provide for cleaning and sealing the interior and exterior of the tower and replacing the pumps and controls. This project is in design under CIP 11-M45 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC WATER TANK | 9879 | Military | NNG |  | North Las Vegas | 1996 |  | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 250000
3158EXT1 | EXTERIOR FINISHES | 3158 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FETC STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 2009 | 1800 | 2018-05-22 | Four to Ten Years | Long-Term Needs | 3 | 1800
3157EXT1 | EXTERIOR FINISHES | 3157 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FETC VIRTUAL TRAINING FACILITY | 9879 | Military | NNG |  | North Las Vegas | 2012 | 2180 | 2018-05-22 | Four to Ten Years | Long-Term Needs | 3 | 2180
2546EXT2 | EXTERIOR DOOR REPLACEMENT | 2546 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | FETC GUARD SHACK | 9879 | Military | NNG |  | North Las Vegas | 0 | 64 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2546INT1 | INTERIOR FINISHES | 2546 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC GUARD SHACK | 9879 | Military | NNG |  | North Las Vegas | 0 | 64 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
1963EXT1 | EXTERIOR FINISHES | 1963 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS STORAGE BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1950 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9750
9879ENR1 | DIRECT DIGITAL CONTROL SYSTEM UPGRADE | 9879 | Presently the site has two separate direct digital control (DDC) systems, one is an older Siemens system and one is a new Delta system. The Siemens system controls the FMS and the CSMS buildings and is not operating. The Delta system controls the Armory's chiller and boiler. This project would provide for upgrading the Delta system to include all the HVAC systems across the site as well as the lighting and any type of alarm systems. The estimate was provided by the maintenance staff who have procured a quote for this work. | FLOYD EDSALL TRAINING CENTER SITE | 9879 | Military | NNG |  | North Las Vegas | 0 |  | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
1960SIT1 | CONCRETE APRON / LANDING INSTALLATION | 1960 | One of the exterior overhead coiling garage doors does not have a concrete apron in front of it. Also, a concrete landing is missing on the exit door on north side of the building. A concrete landing and apron in front of the doors would reduce the amount of dirt and debris from entering the building and prevent erosion in front of the door. The 2012 IBC requires landings at exit doors. This project would provide for the installation of a new 8" thick concrete slab-on-grade apron at the vehicle garage door and a concrete landing at the exit door. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1960HVA3 | VEHICLE EXHAUST EXTRACTION SYSTEM | 1960 | The vehicle maintenance garage has an exhaust extraction system that is not in use. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". The existing system is not utilized because it is on the floor and most vehicles serviced in the building have exhaust terminations near the top of the vehicle. Also, the existing floor system fills up with water occasionally and does not function. This project would provide for the purchase and installation of eight individual overhead vehicle exhaust extraction systems including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project is in design under CIP 11-M05 and the estimate is based off of that project. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
1960EXT1 | EXTERIOR FINISHES | 1960 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting of the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77945
0036SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0036 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1960HVA2 | HEATING UPGRADE | 1960 | The maintenance shop area is heated by several small wall mounted natural gas fired radiant heaters. They are insufficient in providing heat to the large interior space. Staff noted that the heaters will run continuously, but the temperature at the floor level remains cold. This project would provide for installing new gas fired heating units, preferably closer to the floor of the shop and includes connections to all utilities. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1964SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1964 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC PAINT BOOTH | 9879 | Military | NNG |  | North Las Vegas | 1997 | 1120 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 4000
1961HVA2 | VEHICLE EXHAUST EXTRACTION SYSTEMS | 1961 | The vehicle maintenance garage has an exhaust extraction system that is not in use. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". The existing system is not utilized because it is on the floor and most vehicles serviced in the building have exhaust terminations near the top of the vehicle. Also, the existing floor system fills up with water occasionally and does not function. This project would provide for the purchase and installation of four individual overhead vehicle exhaust extraction systems including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project is in design under CIP 11-M05 and the estimate is based off of that project. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0036EXT3 | EXTERIOR FINISHES | 0036 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 380310
1960EXT2 | EXTERIOR DOOR REPLACEMENT | 1960 | The exterior metal door for the battery charging station room is damaged from being hit by a forklift. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0036INT4 | INTERIOR FINISHES | 0036 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 380310
1961INT2 | RESTROOM COUNTERTOP REPLACEMENT | 1961 | The countertops in the restrooms are showing signs of wear and tear particularly at the laminated edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0036ADA1 | ADA ACCESSIBLE COUNTER | 0036 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 1000
1961SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1961 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 4000
1961INT3 | INTERIOR FINISHES | 1961 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63240
0036EXT1 | EXTERIOR DOOR REPLACEMENT | 0036 | The exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of all of the exterior door assemblies with new metal doors, frames and hardware including paint. Removal and disposal of the existing doors is included in this estimate. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
1961HVA1 | HEATING UPGRADE | 1961 | The maintenance shop area is heated by several small wall mounted natural gas fired radiant heaters. They are insufficient in providing heat to the large interior space. Staff noted that the heaters will run continuously, but the temperature at the floor level remains cold. This project would provide for installing new gas fired heating units, preferably closer to the floor of the shop and includes connections to all utilities. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1961EXT1 | EXTERIOR FINISHES | 1961 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63240
1960INT2 | INTERIOR FINISHES | 1960 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77945
0036PLM2 | WATER HEATER REPLACEMENT | 0036 | There are three 69 gallon automatic circulating tank water heaters in the central plant. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that three new gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | FETC CLARK COUNTY ARMORY | 9879 | Military | NNG |  | North Las Vegas | 1997 | 76062 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1960SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1960 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 4000
1960INT3 | RESTROOM COUNTERTOP REPLACEMENT | 1960 | The countertops in the restrooms are showing signs of wear and tear particularly at the laminated edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1960SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1960 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 7795
1960HVA1 | EXHAUST FAN INSTALLATION | 1960 | The building has a battery charging room. The battery charging room is equipped for flushing and neutralizing spilled electrolytes and charging batteries for vehicles and equipment. The room lacks adequate ventilation for dispersal of fumes from gassing batteries as required by OSHA 1910.178(g) (2). Currently the method of ventilation is to open the exterior door and turn on a portable fan. This project would provide for an exhaust system to be installed with warning alarms. The estimate includes engineering, ducting, wiring, installation and repairs to the roof as required. This project or a portion thereof was previously recommended in the FCA report dated 10/12/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/17/2012. | FETC FMS BUILDING | 9879 | Military | NNG |  | North Las Vegas | 1997 | 15589 | 2018-05-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1961ADA1 | BREAK ROOM REMODEL | 1961 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | FETC CSMS | 9879 | Military | NNG |  | North Las Vegas | 1997 | 12648 | 2018-05-22 | Immediate to Two Years | Currently Critical | 1 | 8000
2298HVA2 | EVAPORATIVE COOLER INSTALLATION | 2298 | The Garage has no central cooling system and is uncomfortably warm in the summer. It is recommended to install four evaporative coolers in the building to ensure a comfortable work environment. This project would provide for the purchase and installation of four evaporative coolers including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9880SIT4 | VALLEY GUTTER REPAIRS | 9880 | The concrete valley gutter running through the parking lot is deteriorated and failing. There is significant spalling in many areas that will require complete replacement. The rest of the gutter requires patching and sealing. This project addresses removal and replacement of damaged areas and repairs as needed. 350 SF of 4" thick concrete gutter was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2297EXT1 | EXTERIOR FINISHES | 2297 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and stone, painting the EIFS and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
2297INT1 | INTERIOR FINISHES | 2297 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
2297ADA1 | ADA SIGNAGE | 2297 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 2500
2297ENR1 | WATER HEATER REPLACEMENT | 2297 | There is a 50 gallon gas-fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. It is recommended that a new energy efficient gas-fired water heater be installed. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 1750
2298SFT5 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2298 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the tables, microwaves and other items currently blocking the working space. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 250
2297EXT2 | ROOF REPLACEMENT | 2297 | The single-ply and standing seam metal roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new single-ply roofing system including installing single-ply roofing directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 108000
2298EXT1 | EXTERIOR FINISHES | 2298 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations and painting of the rollup doors. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
2298ENV1 | LIGHTING UPGRADE | 2298 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41600
2298SFT4 | BATTERY STORAGE | 2298 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. Batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced and a smoke alarm. This project will provide funding for the requirements of Section 608 of the 2012 IFC proper way to store, charge and/or use batteries indoors. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 25000
2297ADA3 | BREAK ROOM REMODEL ADA | 2297 | The kitchenette and associated cabinets in the employee break room are original to the building. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. An ADA accessible sink should be provided. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design. This estimate includes removal and disposal of the existing materials. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 15000
2297ENR3 | LIGHTING UPGRADE | 2297 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 72000
2297ADA2 | ADA SHOWER UPGRADE | 2297 | The current shower pan and surround are cracked and in poor condition at the time of the survey. This project would provide for one ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of one stainless steel ADA compliant shower cabinet unit complete with accessible plumbing fixtures, seat, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 25000
2297ENV3 | GUTTER DOWNSPOUT REPLACEMENT | 2297 | The existing cast iron with no-hub downspouts on the North side of the building are located between the CMU exterior wall and an interior gypsum wallboard. At the time of the survey there was evidence of water leaking from the downspouts. This is due to cracks created when water freezes inside the downspouts. This project would remove the damaged downspouts and no-hubs and reinstall and relocate the downspouts to the outside of the building with a thermostatic controlled heat tape. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 12000
2298SFT6 | HOUSEKEEPING STORAGE | 2298 | The Garage has miscellaneous items stacked in aisles, passageways and blocking egress. Items currently on shelving units are unsafely stacked. OSHA 1926.250(a)(3) states Aisles and passageways shall be kept clear to provide for the free and safe movement of material handling equipment or employees. Such areas shall be kept in good repair 1926.250(c) Housekeeping Storage areas shall be kept free from accumulation of materials that constitute hazards from tripping, fire, explosion, or pest harborage. This project would provide funding to comply with OSHA standards. It is recommended that the employer develop a maintenance and inspection program for storage, which include keeping aisles clear and providing sufficient clearance for material handling equipment, ensuring storage shelves are properly aligned, plum, and level, per manufacturer’s instructions, as well as encouraging employees to promptly report any damage to storage shelves. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 4000
2298SFT7 | HAZARDOUS MATERIALS STORAGE | 2298 | The Garage contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the SFMO and the SPWD. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2298SFT8 | ANCHOR SHELVES | 2298 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1), All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a licensed engineer or architect. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 10000
2297PLM1 | WATER TREATMENT SYSTEM INSTALLATION | 2297 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 annual maintenance fee is suggested. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2297SFT4 | FIRE & SECURITY ALARM SYSTEM REPLACEMENT | 2297 | This building is equipped with an outdated automatic fire detection and alarm system. Due to the age of the systems, parts cannot be obtained and do not comply with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. According to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will comply with the 2012 IBC Chapter 9, Section 907 and the SFMO requirements. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 72000
2297ENR2 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 2297 | The YAMAS energy management system is original to the building and should be scheduled for replacement. Replacement parts for performing routine and emergency maintenance are not made any more , the system has recently had numerous failures and the system is too old to perform software updates. This project would provide for the removal and disposal of the existing YAMAS energy management system and replacement with new equipment including all required connections to utilities and equipment. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2297INT4 | CEILING TILE REPLACEMENT | 2297 | The building has a suspended acoustical tile ceiling system. A number of the ceiling tiles are damaged and stained from leaks in the boiler and roofing systems. This project would provide for the replacement of the suspended acoustical ceiling tiles that are damaged or stained. Removal and disposal of the existing ceiling system is included in this estimate. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2298ENV2 | SPILL CONTAINMENT | 2298 | The Garage does not have a method for containing spills or leakage from drums. This project would add secondary containment pallets for all containers in the building and install placards on the building’s exterior. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 6500
2297SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2297 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 5000
2297INT3 | FLOORING REPLACEMENT | 2297 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 72000
9880SIT5 | PARKING LOT STRIPING | 9880 | It is important to maintain the striping on the pavement at the site. This project would provide for the necessary striping and painting of the curbs and parking spaces. An ADA parking and loading space emblem will be painted on the concrete that is designated for ADA parking. This project should be scheduled on a 2 year cyclical basis to maintain the integrity of the striping, painting and ADA designation. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9880SFT1 | HAZARDOUS COMMUNICATION PROGRAM | 9880 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 2000
9880ADA1 | ADA SIDEWALK REPLACEMENT | 9880 | The concrete sidewalks around the building are in need of replacement. They have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1,500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 22500
2297HVA3 | BOILER REPLACEMENT | 2297 | There are two hot water boilers servicing the building. They are original to the building dating back to 2002. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 300 MBH output hot water boiler. | EASTERN REGION NDOW OFFICE BUILDING | 9880 | Wildlife |  |  | Elko | 2002 | 9000 | 2016-07-05 | Four to Ten Years | Long-Term Needs | 3 | 100000
9880SIT1 | SITE BOLLARDS | 9880 | The site has parking in the rear of the Office building near the AC units. The garage building has five sectional overhead doors. These areas are in need of bollards to protect the AC units and the garage building. This project would provide funding for 18 eight inch diameter bollards to be located on each side of the garage sectional overhead doors and in front of the AC units. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION WILDLIFE OFFICE SITE | 9880 | Wildlife |  |  | Elko | 2002 |  | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
2298SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 2298 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 5000
2298SFT2 | SAFETY CABINETS | 2298 | Flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity, shall have a proper storage container, OSHA 1910.106 (7) (d). This project will provide two OSHA approved storage cabinets for gasoline, aerosol cans and other flammable items. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Immediate to Two Years | Currently Critical | 1 | 10000
2298HVA1 | HEATER INSTALLATION | 2298 | The Garage is currently unheated, making for unpleasant working conditions in colder weather. Natural gas is stubbed up outside of the building. This project would provide for the installation of two 25 KBTU suspended heaters in the shop area. The estimate includes installing a gas meter, seismic gas shut off valve, gas piping and seismic supports, and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005 and 07/22/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/05/2016. | EASTERN REGION NDOW GARAGE | 9880 | Wildlife |  |  | Elko | 2002 | 5200 | 2016-07-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2543EXT1 | EXTERIOR FINISHES | 2543 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF FIRE TRUCK GARAGE | 9881 | CNR | Forestry |  | Ruby Valley | 0 | 714 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 1428
3145EXT1 | EXTERIOR FINISHES | 3145 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the window, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 840 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 1680
3144EXT1 | EXTERIOR FINISHES | 3144 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CONTROL BOX #2 | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 162 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 500
3143EXT1 | EXTERIOR FINISHES | 3143 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CONTROL BOX #1 | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 162 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 500
0923EXT1 | EXTERIOR FINISHES | 0923 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the concrete, sanding, priming and painting the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16230
9881ELE1 | POWER LINE UPGRADE | 9881 | The main power line for the site is on the west side of the road and crosses the road to connect to the Office building. The pole is not tall enough to raise the lines above the height of large trucks and the line has been broken in the past. This project recommends working with the utility company to either provide a taller pole or bury the lines under the road. The estimate is based on the state providing all funding for the work. | GALLAGHER FISH HATCHERY SITE | 9881 | Wildlife |  |  | Ruby Valley | 1940 |  | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0922EXT1 | EXTERIOR FINISHES | 0922 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls and caulking of the windows, flashing, fixtures, cracks in the concrete and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26400
0922INT1 | INTERIOR FINISHES | 0922 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26400
0922ENR1 | LIGHTING UPGRADE | 0922 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts or compact flourescent lamps (CFL's) are suggested. Occupancy sensors will be installed in utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7920
0922EXT3 | EXTERIOR DOOR REPLACEMENT | 0922 | Two of the three exterior metal man doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0922SFT1 | FIRE EXTINGUISHER INSTALLATION | 0922 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in the building. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets, and the hardware necessary to install them. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
0922SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0922 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 21120
0922SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0922 | The building does not have any emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 2000
0922HVA1 | AIR CONDITIONER REPLACEMENT | 0922 | The building is cooled by an older portable air conditioner. The portable air conditioner is not sufficient to cool the entire space in the warmer months of the year. It is recommended to install an air conditioning system in the building to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of a permanent air conditioner including all required connections to existing utilities. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0923ENV1 | BAT AND BIRD ABATEMENT | 0923 | There are numerous bat and bird droppings throughout the inside and outside of the building. Due to the potential risk of disease, this project provides for treatment and clean up of the pests by a licensed pest control business. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 2000
0922PLM2 | WATER HEATER REPLACEMENT | 0922 | There is a 40 gallon electric water heater in the building that is 7 years old and is not seismically braced. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater with seismic bracing be installed. Removal and disposal of the existing equipment is included in this estimate. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
3146EXT1 | EXTERIOR FINISHES | 3146 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the window, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 840 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 1680
0923INT1 | INTERIOR FINISHES | 0923 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. The non-painted walls in the shop area are excluded from the estimate. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
0923ENR1 | WINDOW REPLACEMENT | 0923 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0923EXT2 | OVERHEAD DOOR REPLACEMENT | 0923 | Three of the four 10'x14' overhead coiling doors are damaged and do not function properly. The other overhead door was recently replaced. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated insulated overhead coiling doors. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0923ADA1 | ADA ENTRANCE AND PATH OF TRAVEL | 0923 | The existing exterior entrance door and threshold to the Office are not accessible and there is no accessible path of travel inside the building. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly and a compliant path of travel throughout the upper floor and to the accessible restroom. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 2500
0923ENR2 | LIGHTING UPGRADE | 0923 | The existing lighting fixtures are the older fluorescent type T-12's, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4869
0923SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0923 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1500
0923PLM1 | WATER HEATER REPLACEMENT | 0923 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater with seismic bracing be installed. Removal and disposal of the existing equipment is included in this estimate. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0923SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0923 | The building is partially a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project does NOT include the possible need of a water storage tank for fire protection water storage. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 45444
0923SFT5 | FIRE ALARM SYSTEM INSTALLATION | 0923 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 12984
0922PLM1 | WATER MAIN REPLACEMENT | 0922 | The main water intake for the hatchery is leaking inside the building and is not equipped with a shut-off valve. This project recommends replacing the water line with a new line and shut-off valve. The estimate includes temporary measures to control the water flow from the natural spring and removal and replacement of the piping. This project provides for an engineered system which will conform to all required environmental rules and regulations including NDEP. | GALLAGHER FISH HATCHERY | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 5280 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0927EXT2 | EXTERIOR FINISHES | 0927 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0928SFT2 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0928 | The concrete exterior stairs at the entry are lacking a handrail as required in section R311.7.8 of the 2012 International Residential Code. This project would provide for a tubular steel framed handrail to be installed in accordance with the code. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
3139EXT1 | EXTERIOR FINISHES | 3139 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4-5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 200 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 1000
3142EXT1 | EXTERIOR FINISHES | 3142 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | EMERGENCY GENERATOR BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 640 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 1280
0923SFT6 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0923 | The interior stair handrails are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and they are installed on only one side of the stair. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports in accordance with the 2012 IBC Chapter 10, Section 1012. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
0926SFT1 | SMOKE ALARM INSTALLATION | 0926 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
0926EXT1 | EXTERIOR FINISHES | 0926 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 5500
0928SFT1 | SMOKE ALARM INSTALLATION | 0928 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
0928INT1 | INTERIOR FINISHES | 0928 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0928EXT1 | EXTERIOR FINISHES | 0928 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #2 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 5500
0929EXT1 | EXTERIOR FINISHES | 0929 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY RESIDENCE #2 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0931EXT1 | EXTERIOR FINISHES | 0931 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY RESIDENCE #3 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0932SFT1 | SMOKE ALARM INSTALLATION | 0932 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
0932INT1 | INTERIOR FINISHES | 0932 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0932EXT1 | EXTERIOR FINISHES | 0932 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 5500
2542EXT1 | EXTERIOR FINISHES | 2542 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | METAL STORAGE BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 0 | 201 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 201
3141EXT1 | EXTERIOR FINISHES | 3141 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VEHICLE STORAGE BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 4000 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 4000
0926INT1 | INTERIOR FINISHES | 0926 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #1 | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
3142INT1 | INTERIOR FINISHES | 3142 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | EMERGENCY GENERATOR BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 640 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 3200
0933SFT1 | SMOKE ALARM INSTALLATION | 0933 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
3140EXT1 | EXTERIOR FINISHES | 3140 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REARING BUILDING | 9881 | Wildlife |  |  | Ruby Valley | 2006 | 32264 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 32264
0939EXT1 | EXTERIOR FINISHES | 0939 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DOMESTIC PUMP HOUSE | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 88 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 440
0936EXT1 | EXTERIOR/ INTERIOR FINISHES | 0936 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER HATCHERY SHADE SHELTER #1 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 11000 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0935EXT2 | DEMOLISH STRUCTURE | 0935 | The structure is delapidated and deteriorating and is over 50 years of age. It is no longer in use. This project would provide funding for the demolition and disposal of the structure. | GALLAGHER HATCHERY SHADE SHELTER NORTH | 9881 | Wildlife |  |  | Ruby Valley | 1955 | 804 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 1500
0934EXT1 | EXTERIOR FINISHES | 0934 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 5500
0934INT1 | INTERIOR FINISHES | 0934 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0934SFT1 | SMOKE ALARM INSTALLATION | 0934 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 1000
0933EXT1 | EXTERIOR FINISHES | 0933 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Four to Ten Years | Long-Term Needs | 3 | 5500
0933INT1 | INTERIOR FINISHES | 0933 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5500
0927EXT1 | FASCIA AND SIDING REPLACEMENT | 0927 | The fascia and wood siding on the gables is weather beaten, worn, and twisted, and is showing signs of considerable wear. It is recommended that all the fascia and wood siding be replaced and finished. This project or a portion thereof was previously recommended in the FCA report dated 08/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2012. | GALLAGHER HATCHERY RESIDENCE #1 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0931SIT1 | CONCRETE APRON INSTALLATION | 0931 | The area in front of the garage is a mixture of grass and gravel. To make access to the garage more convenient, it is recommended that a 10' x 16' concrete apron be installed. This project would provide for a 4" thick concrete slab-on-grade including grading and soil compaction. This project or a portion thereof was previously recommended in the FCA report dated 08/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2012. | GALLAGHER HATCHERY RESIDENCE #3 GARAGE | 9881 | Wildlife |  |  | Ruby Valley | 1956 | 288 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
0932SIT1 | CONCRETE REPLACEMENT | 0932 | The existing concrete driveway is cracked, spalling and presents a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a new 4" thick concrete driveway. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 08/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2012. | GALLAGHER FISH HATCHERY RESIDENCE #4 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0934SIT1 | CONCRETE REPLACEMENT | 0934 | The existing concrete driveway is cracked, spalling and presents a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a new 4" thick concrete driveway. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 08/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2012. | GALLAGHER FISH HATCHERY RESIDENCE #6 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0933SIT1 | CONCRETE REPLACEMENT | 0933 | The existing concrete driveway is cracked, spalling and presents a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a new 4" thick concrete driveway. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 08/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2012. | GALLAGHER FISH HATCHERY RESIDENCE #5 | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 1100 | 2012-06-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0923SFT1 | WATER HEATER SEISMIC BRACING | 0923 | The water heater is not seismically anchored to the structure. This project would provide funding for seismic bracing of the water heater to the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/27/2012. | GALLAGHER FISH HATCHERY OFFICE & SHOP | 9881 | Wildlife |  |  | Ruby Valley | 1966 | 3246 | 2012-06-27 | Immediate to Two Years | Currently Critical | 1 | 500
0665EXT4 | OVERHEAD DOOR REPLACEMENT | 0665 | There are two 8'x8' overhead coiling doors in the building which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead garage doors and replacement with new automatic openers and insulated garage doors. Removal and disposal of the existing garage doors is included in this estimate. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0666EXT3 | ROOF REPLACEMENT | 0666 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9216
0666EXT4 | EXTERIOR FINISHES | 0666 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 7680
0666SIT4 | SITE DRAINAGE UPGRADES | 0666 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0666SFT5 | FLUE REPAIRS | 0666 | The flue on this building has an improper support strap, is too close to combustibles and doesn’t have the proper clearances. The heater flue, the support strap and the distances of the flue to the fascia do not comply with IFGC 2012, IBC 2012, IMC 2012 chapter 8, chimneys and vents or the Manufacturers Specification for installation instructions. It is recommended that all flues throughout the building be installed per the manufacturers specifications IFGC 2012, IBC 2012 and IMC 2012. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 2000
0666SFT6 | CONCRETE APRON REPLACEMENT | 0666 | The exterior concrete apron outside of the building has extensive cracking and is due for replacement. This project would provide for the installation of a new 120 square foot 4" thick concrete slab-on-grade apron. Removal and disposal of the existing concrete is included in this estimate. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0665EXT2 | WINDOW REPLACEMENT | 0665 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0665EXT3 | EXTERIOR FINISHES | 0665 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 13430
0665SIT2 | SITE DRAINAGE UPGRADES | 0665 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0949EXT2 | EXTERIOR FINISHES | 0949 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing and fixtures and all other penetrations. It is recommended that the building be painted in the next 2-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0665EXT1 | CONCRETE APRON REPLACEMENT | 0665 | The building is missing an exterior concrete apron outside the roll up door bays. This project would provide for the installation of two new 120 square foot 4" thick concrete slab-on-grade aprons. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0666ADA1 | ADA RESTROOM UPGRADE | 0666 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 15000
0665HVA1 | HEATER INSTALLATION | 0665 | The building is currently unheated, making for unpleasant working conditions in colder weather. This project would provide for the installation of two 25KBTU suspended heaters in the building. The estimate includes installing a gas meter, seismic gas shut off valve, gas piping and seismic supports and electric connections. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0665ENR1 | LIGHTING UPGRADE | 0665 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10744
0664EXT2 | EXTERIOR FINISHES | 0664 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
0664EXT3 | ROOF REPLACEMENT | 0664 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12096
0664INT2 | INTERIOR REMODEL | 0664 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim, baseboards, kitchen and any other interior finishes and fixtures in need of replacement. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50400
0664SIT2 | SITE DRAINAGE UPGRADES | 0664 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0664SIT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0664 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0664PLM1 | WATER HEATER REPLACEMENT | 0664 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 1750
0664HVA1 | HVAC EQUIPMENT REPLACEMENT | 0664 | The 84,000 BTUs heating system was installed in 1993. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0665SFT1 | EXTERIOR LANDING INSTALLATION | 0665 | The landing at the door on the building does not comply with code and poses a safety hazard. Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door and the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. This project would provide for the installation of compliant landing for the door. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 2500
0947SIT4 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0947 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate the sprinklers so they do not wet the house. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0949ELE1 | WIRING CLEANUP | 0949 | The wiring in the Domestic Well Shed is disorganized and not in proper electrical boxes. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed electrical boxes per NEC 2011. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0949ELE2 | GFCI OUTLETS | 0949 | The existing receptacle in the Domestic Well Shed is a standard duplex receptacle. The 2011 NEC 210.8 requires this location to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacle and installing GFCI receptacle. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
0949SFT1 | EXTERIOR LANDING INSTALLATION | 0949 | There is an exterior door on the building that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 1500
0949EXT3 | ROOF REPLACEMENT | 0949 | The asphalt roll roofing on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S.C. REARING STATION DOMESTIC WELL SHED | 9882 | Wildlife |  |  | Baker | 1980 | 120 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0948ENR1 | LIGHTING UPGRADE | 0948 | The existing lighting fixture is the older incandescent type, and is not energy efficient. This project will upgrade the fixture to a higher efficiency LED unit with a longer life cycle. An occupancy sensor will be installed for additional savings. Any electrical wiring upgrades are not included in this estimate. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 144
0948INT2 | CONCRETE FOUNDATION | 0948 | At the time of this survey, the shed’s floor was unfinished and was dirt. This project would provide for the installation of a 4" thick concrete floor and a landing outside the front door of the building. The 2012 IBC Section 1008.1 was used as a reference for this project. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0948EXT2 | EXTERIOR FINISHES | 0948 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
0947EXT2 | EXTERIOR FINISHES | 0947 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
0947EXT3 | ROOF REPLACEMENT | 0947 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12096
0666SFT4 | SAFETY CABINETS | 0666 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide for two self-closing hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 10000
0947SIT3 | SITE DRAINAGE UPGRADES | 0947 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0666ADA2 | ADA SHOWER UPGRADE | 0666 | This project would provide for an ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of a stainless steel ADA compliant shower cabinet unit complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 25000
0947PLM1 | WATER HEATER REPLACEMENT | 0947 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 1750
0667SIT3 | SITE DRAINAGE UPGRADES | 0667 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the building. Additional drainage swales and French Drains shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0667ENR1 | INSULATE BUILDING | 0667 | The building is not insulated and is not energy efficient. This project will install batt insulation (R19) in the walls and (R38) on the ceilings and will be covered with impermeable vinyl interior surface to help moderate temperature fluctuations. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
0667EXT3 | GUTTER INSTALLATION | 0667 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently drains off the roof causing extensive erosion to the built-up dirt slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0667ENR2 | WINDOW REPLACEMENT | 0667 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 6000
0667EXT4 | EXTERIOR FINISHES | 0667 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1536
0667HVA1 | HEATER INSTALLATION | 0667 | The building is currently unheated, making for unpleasant working conditions in colder weather. This project would provide for the installation of two 25KBTU suspended heaters in the building. The estimate includes installing a gas meter, seismic gas shut off valve, gas piping and seismic supports and electric connections. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0666SFT3 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0666 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 3840
9882PLM1 | WELL INSTALLATION | 9882 | The 19 fish raceways receive water from both Spring Creek and Snake Creek. The water flows through the raceways and eventually flows back into Snake Creek. At times during the summer months and during droughts, the water from the creeks are unable to meet demands. This project recommends drilling a new well and installing new pumping equipment to serve the water demands of the site. Estimates are based on a maximum of 300 feet of drilling. | SPRING CREEK FISH REARING STATION SITE | 9882 | Wildlife |  |  | Baker | 0 |  | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400000
0947INT1 | INTERIOR REMODEL | 0947 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for the removal and replacement of the flooring, doors and frames, cabinetry, trim, baseboards, kitchen and any other interior finishes and fixtures in need of replacement excluding the bathroom. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50400
0948EXT3 | EXTERIOR SIDING REPLACEMENT | 0948 | The existing Lap siding is in poor condition and will no longer hold paint and is due for replacement. This project recommends removing the Lap siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0947SIT2 | TREE REMOVAL | 0947 | A deciduous tree is growing next to the foundation of the residence. The tree in time will cause damage to the foundation. This tree should be removed before damage occurs to the foundation. This project would provide funding for the removal of the tree and roots. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 4000
0665INT1 | BUILDING INSULATION | 0665 | The building is not insulated and is not energy efficient. This project will install batt insulation (R19) in the walls and (R38) on the ceilings and will be covered with impermeable vinyl interior surface to help moderate temperature fluctuations. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION STORAGE/SHOP | 9882 | Wildlife |  |  | Baker | 1964 | 1343 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20145
0664SIT1 | REPLACE CONCRETE WALK | 0664 | The existing concrete sidewalks are cracked, spalling and present a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a 42" wide x 25' long section of concrete sidewalk. This project should coincide with other concrete work recommended for the site. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION RES. #1, NORTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0666SFT1 | SMOKE/ CARBON MONOXIDE ALARM INSTALLATION | 0666 | There are no smoke detectors or carbon monoxide detectors in the building. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with the applicable building codes. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 2000
0666ENR1 | REPLACE WINDOWS | 0666 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 14 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION OFFICE & GARAGE | 9882 | Wildlife |  |  | Baker | 1949 | 768 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0667SIT1 | TREE REMOVAL | 0667 | A deciduous tree is growing next to the garage foundation between the two roll up doors. The tree in time will cause damage to the foundation and flooring. This tree should be removed before damage occurs to the foundation and flooring. This project would provide funding to remove the tree and its roots. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Immediate to Two Years | Currently Critical | 1 | 4000
0947SIT1 | SIDEWALK REPLACEMENT | 0947 | The existing concrete sidewalks are cracked, spalling and present a tripping hazard to pedestrians. Exposure to the weather has contributed to the damage and deterioration. It is believed the concrete is part of the original construction. This project would provide funding for the removal and disposal of the existing concrete and the installation of a 42" wide x 25' long section of concrete sidewalk. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION RES. #2, SOUTH | 9882 | Wildlife |  |  | Baker | 1950 | 1008 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0948EXT1 | REPLACE ROOF | 0948 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S.C. REARING STATION SHED #1 | 9882 | Wildlife |  |  | Baker | 1950 | 144 | 2016-07-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1728
0667EXT2 | CONCRETE APRON | 0667 | The area in front of the garage doors is grass. To make garage access more convenient, it is recommended that a 24' x 20' concrete apron be poured in front of the garage doors. This project would provide for the funding to pour a 24' x 20' concrete apron including any required grading and soil preparation. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | S. C. REARING STATION RESIDENCE GARAGE | 9882 | Wildlife |  |  | Baker | 1972 | 768 | 2016-07-06 | Four to Ten Years | Long-Term Needs | 3 | 12000
0477EXT1 | EXTERIOR FINISHES | 0477 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WELL HOUSE | 9883 | CNR | Parks |  | Rye Patch SRA | 1980 | 84 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 420
1298ENR2 | WATER HEATER REPLACEMENT | 1298 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1298ENR1 | LIGHTING UPGRADE | 1298 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1620
1298SIT1 | CONCRETE APRON UPGRADE | 1298 | The exterior concrete apron in front of the overhead doors has extensive cracking, is too small and is due for an upgrade. This project would provide for the installation of a new 4" thick concrete slab-on-grade apron at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1298INT2 | INTERIOR FINISHES | 1298 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5400
9883SIT2 | IRRIGATION UPGRADES | 9883 | The existing landscape irrigation lines for the Group Use area are reaching the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 2,000 linear feet was used to generate this estimate. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0479ADA4 | ADA SHOWER UPGRADE | 0479 | The designated ADA shower does not fully comply with the ADA accessible guidelines. This project would provide for new ADA compliant plumbing fixtures, shower seat and any other necessary upgrades to bring the restroom into compliance. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 2500
1298SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1298 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. Additional costs may be needed to provide for a water storage tank. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 15120
1298SFT3 | FIRE ALARM SYSTEM INSTALLATION | 1298 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 4320
1297EXT1 | EXTERIOR FINISHES | 1297 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 48 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 240
1309PLM1 | WATER HEATER REPLACEMENT | 1309 | There is a 40 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 7-8 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 1750
1297INT1 | INTERIOR FINISHES | 1297 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | ENTRANCE STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 48 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 240
1298ADA2 | ADA DOOR & THRESHOLD REPLACEMENT | 1298 | The existing exterior entrance door and threshold to the Park Office is not accessible. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 2500
1298ADA3 | ADA PARKING SPACE | 1298 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area for the Park Office & Garage are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 2500
1309EXT3 | DECK REPLACEMENT | 1309 | The wood deck on the rear of the house is damaged and has reached the end of its expected life. The lumber is cracked and warped, there are no handrails or proper steps and the gaps between the lumber pose a tripping hazard. This project would provide for the removal and disposal of the deck and replacement with a new wood framed deck with composite decking which complies with safety codes. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9883ADA1 | ADA ACCESS UPGRADES | 9883 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Park Office and the Comfort Station #4 are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the entrance of the Park Office and the Comfort Station #4. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 15000
1298EXT2 | WINDOW REPLACEMENT | 1298 | The 6 windows in the building are original uninsulated windows and are not energy efficient. This project would provide for the removal and replacement of the old windows with new dual pane insulated windows in vinyl frames. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1298HVA2 | HEATER REPLACEMENT | 1298 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0479ADA1 | ADA SIGNAGE | 0479 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 750
1299ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 1299 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Group Ramada are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the Group Ramada. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | GROUP RAMADA | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 968 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 7500
1299EXT1 | EXTERIOR FINISHES | 1299 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP RAMADA | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 968 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1936
1307EXT1 | EXTERIOR FINISHES | 1307 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and painting the steel framing. It is recommended that the building be sealed and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | FISH CLEANING STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1980 | 60 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
1309EXT2 | ROOF REPLACEMENT | 1309 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
1298EXT4 | EXTERIOR FINISHES | 1298 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted around 5-7 years after the new siding is installed and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 5400
1309HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1309 | An evaporative cooler is installed on the roof of this building and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9883SIT4 | SITE HANDRAIL PAINTING | 9883 | Existing painted finishes on the hand and safety railings in the park are showing signs of deterioration and are in need of repainting. This project recommends the preparation and repainting of all the hand and safety railings. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1298EXT1 | EXTERIOR SIDING REPLACEMENT | 1298 | The building has painted wood siding that is due for replacement. The existing siding is in poor condition and will no longer hold paint. This project recommends removing the existing siding and replacing it with T1-11 panels finished with an oil-based stain. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21600
1298ELE1 | EXTERIOR GFCI OUTLET REPAIR | 1298 | The building has three exterior electrical outlets which are not GFCI protected and are missing the safety covers. This project would provide for replacement of the electrical outlets with new code-compliant outlets. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 900
1298EXT3 | ROOF REPLACEMENT | 1298 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12960
1308EXT1 | DEMOLISH STRUCTURE | 1308 | The Storage Building is dilapidated and deteriorating and has reached the end of it's useful life. There is a considerable amount of rust on the metal panels, the plywood doors are cracked and worn and there is no flooring in the building to protect the equipment stored in it or the structure itself. This project would provide funding for the demolition of the structure. | STORAGE BLDG #1 - OFFICE/SHOP AREA | 9883 | CNR | Parks |  | Rye Patch SRA | 1980 | 192 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
1297EXT2 | ROOF REPLACEMENT | 1297 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | ENTRANCE STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 48 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 576
9883SFT1 | PICNIC TABLE REPLACEMENT | 9883 | The weather in the Rye Patch SRA is extreme, creating maintenance issues throughout the park. Extreme cold winters and hot summer months are causing premature wear and deterioration to the wood picnic tables. This project would provide for the replacement of the wood picnic tables with powder coated metal frame and resin composite tables. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1309INT1 | CARPET REPLACEMENT | 1309 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
9883SIT5 | FIRE PIT RING REPLACEMENT | 9883 | The Rye Patch SRA has fire rings located in the camping area to allow campers to have a safe place to enjoy an open fire. The wet winters and continuous use of the fire rings has caused deterioration of the metal fire rings. This project would provide for the purchase and installation of 25 new fire rings for the Rye Patch SRA campsites. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1298HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1298 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1298SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1298 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 1000
1298ADA1 | ADA RESTROOM UPGRADE | 1298 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | PARK OFFICE & GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1978 | 1080 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 15000
0479ADA3 | ADA RESTROOM UPGRADE | 0479 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 2000
3114EXT1 | EXTERIOR FINISHES | 3114 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CABIN #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 400
2532EXT2 | EXTERIOR FINISHES | 2532 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RESIDENCE GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 400 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1309EXT1 | EXTERIOR FINISHES | 1309 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
3114INT1 | INTERIOR FINISHES | 3114 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CABIN #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 400
3115INT1 | INTERIOR FINISHES | 3115 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CABIN #2 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 400
3115EXT1 | EXTERIOR FINISHES | 3115 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 6-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CABIN #2 | 9883 | CNR | Parks |  | Rye Patch SRA | 2012 | 80 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 400
1309INT2 | INTERIOR FINISHES | 1309 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1309ADA1 | RESTROOM REMODEL | 1309 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom including compliance with ADA regulations. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1309INT3 | KITCHEN REMODEL | 1309 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | RESIDENCE #1 | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 1440 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0477EXT2 | ROOF REPLACEMENT | 0477 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 2-3 years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | WELL HOUSE | 9883 | CNR | Parks |  | Rye Patch SRA | 1980 | 84 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1008
0545EXT2 | DEMOLISH STRUCTURE | 0545 | The structure is dilapidated and deteriorating and has reached the end of its useful life. The structure is approaching 50 years of age, has had continuous roof leaks and the wood has rotted. This project would provide funding for the demolition and disposal of the building. | STORAGE BUILDING #2 | 9883 | CNR | Parks |  | Rye Patch SRA | 1966 | 200 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0479EXT2 | ROOF REPLACEMENT | 0479 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
0479ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0479 | There is a water fountain attached to the exterior of the building that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 4000
3118EXT1 | EXTERIOR/ INTERIOR FINISHES | 3118 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - GROUP USE | 9883 | CNR | Parks |  | Rye Patch SRA | 2006 | 204 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2040
0476EXT1 | EXTERIOR FINISHES | 0476 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | BOAT RAMP COMFORT STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 2000 | 264 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1320
0476INT1 | INTERIOR FINISHES | 0476 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | BOAT RAMP COMFORT STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 2000 | 264 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1320
0476EXT2 | EXTERIOR DOOR REPLACEMENT | 0476 | Two of the exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | BOAT RAMP COMFORT STATION | 9883 | CNR | Parks |  | Rye Patch SRA | 2000 | 264 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2532EXT1 | ROOF REPLACEMENT | 2532 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RESIDENCE GARAGE | 9883 | CNR | Parks |  | Rye Patch SRA | 1995 | 400 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
9883PLM1 | WATER STORAGE TANK INSTALLATION | 9883 | There is a 150 gallon water storage tank in the Park Office building. The existing capacity is not enough to support the demand in this area of the park. It is recommended to purchase and install a new larger tank to meet the demand. This project would provide for a new 500 gallon water storage tank to be installed near the Park Office including connections to existing utilities and the radio telemetry system. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9883ADA2 | LOWER CAMPGROUND ADA UPGRADES | 9883 | According to proposed US Access Board regulations, a campground with 51-100 camping spaces should have 4 accessible spaces spaced throughout the campground to provide as many accessible campsite options as possible. The Upper Campground currently has two accessible spaces and the Lower campground does not have any. Other regulations include 20'-0" wide drive aisles for RV/ tent trailer sites and accessible amenities on an accessible route including grills, picnic tables, fire rings and water & electric utilities. This project provides for upgrading two existing campsites at the Lower Campground to accessible campsites. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Immediate to Two Years | Currently Critical | 1 | 35000
9883EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9883 | There are 28 steel shade ramadas in different locations throughout the site which are either 144 s.f., 264 s.f. or 400 s.f. for a total of 9,272 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/31/2012. | RYE PATCH SRA SITE | 9883 | CNR | Parks |  | Rye Patch SRA | 1971 |  | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18544
0479INT1 | INTERIOR FINISHES | 0479 | The interior finishes are in fair condition. It is recommend to power wash the interior walls and ceilings and replace the Fiberglass Reinforced Panels where necessary at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3117EXT1 | EXTERIOR/ INTERIOR FINISHES | 3117 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - LOWER CAMPGROUND | 9883 | CNR | Parks |  | Rye Patch SRA | 2007 | 204 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2040
3116EXT1 | EXTERIOR/ INTERIOR FINISHES | 3116 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION - DAY USE | 9883 | CNR | Parks |  | Rye Patch SRA | 2006 | 120 | 2012-05-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0479EXT1 | EXTERIOR FINISHES | 0479 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9883 | CNR | Parks |  | Rye Patch SRA | 1976 | 400 | 2012-05-31 | Four to Ten Years | Long-Term Needs | 3 | 2000
2530LGT1 | LONG-TERM NEEDS | 2530 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all maintenance but is a budgetary estimate for future maintenance. The cyclical treatment of the building exterior is important to help maintain the finish, weather proofing, integrity, and appearance of the building. This project does not include the roofing system, but includes items related to water proofing the building envelope, including painting, sealing, repairing, and caulking where applicable. | HAZARDOUS MATERIALS BUILDING | 9884 | Military | NNG |  | Winnemucca | 0 | 66 | 2005-07-28 | Four to Ten Years | Long-Term Needs | 3 | 2500
9884SIT3 | REPAIR RETAINING WALL | 9884 | The site has a retaining wall that runs along the rear of the Armory building parking area that separates the lower and upper part of the facility. The wall is constructed of CMU and precast concrete and has numerous cracks due to water infiltration and age. This may be compromising the structural integrity of the wall. This project would provide for repairs to the wall and the application of a sealer to prevent further damage. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
9884SIT1 | WEED ABATEMENT | 9884 | The Nevada National Guard - Winnemucca Site is overgrown with weeds. This project would provide for the removal and disposal of the weeds on the site and treatment of the area with an herbicide to prevent future weed growth. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9884SIT5 | REPLACE CONCRETE SIDEWALKS AND PARKING AREA | 9884 | The concrete sidewalks and parking appear to be part of the original construction. Deterioration, spalling, and cracking has occurred mainly from exposure to the weather and possible water accumulation. This project would provide for the removal and replacement of the concrete sidewalks in front of the Armory and the concrete parking area in the rear of the Armory. Disposal of the old concrete is included in this estimate. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Four to Ten Years | Long-Term Needs | 3 | 140000
9884SIT4 | SITE ACCESSIBILITY | 9884 | The accessible parking, travel route, and public entrance are not clearly defined. Currently, the public parks in the rear of the building and must utilize the side entrance for the accessible route of travel from the parking area to the building. The travel route from the parking area to the accessible door is a concrete walk that is in need of replacement. This project would provide for accessible parking, striping, signage and removal and replacement of about 50 lineal feet of a three foot wide concrete accessible route of travel to the building. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 25000
0688INT1 | WALL/FLOOR REPAIRS | 0688 | The gypsum board and vinyl tile are separating in the men's restrooms and some damage has already occurred. The separation may be caused from moisture. This project would provide funding for the investigation, repairs and replacement of the damage gypsum board and vinyl tile. Other projects may be developed from the findings of where the moisture source may be coming from and any suggestions on prevention of the moisture infiltration. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 7500
0688SFT3 | SEISMIC GAS SHUT OFF VALVE | 0688 | Agreements reached between the Nevada Risk Management Office and the State of Nevada's Insurance Underwriter require Seismic Gas Shutoff Valves (SGSV's) on all gas services to all State owned buildings. This project would install a SGSV to the gas line serving the building. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 3000
0688HVA1 | AIR HANDLER FILTER UPGRADE | 0688 | The existing HVAC system is equipped with an economizer cycle and enthalpy control for "free cooling" of the building. The air-handlers have large gaps in the duct work located around the economizers. The gaps are allowing insects and gnats access inside the building. This project would provide funding to modify the duct work system to eliminate the gaps. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0688LGT1 | LONG TERM NEEDS | 0688 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Four to Ten Years | Long-Term Needs | 3 | 150000
0688SFT2 | INSTALL EMERGENCY EGRESS LIGHTING | 0688 | There is no emergency egress lighting in the hallway. This project recommends the installation of egress lighting along the exit pathway in the building. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 500
9884SIT2 | FENCING | 9884 | The Nevada National Guard - Winnemucca Site is currently fenced off to the general public for security and safety reasons. There is a chain link fence dividing the upper level from the lower level located adjacent to the retaining wall. There are some areas of the fence that are damaged and should be replaced. This project would provide for replacement of the 6 foot tall industrial chain link fence. | WINNEMUCCA ARMORY SITE | 9884 | Military | NNG |  | Winnemucca | 0 |  | 2005-07-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4910
0688SFT1 | SERVICING FIRE SUPPRESION EQUIPMENT | 0688 | The existing fire extinguishers and fire sprinkler system are in need of servicing. Under the NAC 477.460 and 477.410 these items must be serviced and tagged annually. This project would provide funding to inspect and service all the fire extinguishers and fire sprinkler system. | ARMORY | 9884 | Military | NNG |  | Winnemucca | 1959 | 9877 | 2005-07-28 | Immediate to Two Years | Currently Critical | 1 | 1000
0678PLM2 | WATER HEATER REPLACEMENT | 0678 | There are two large gas-fired water heaters in the building. One unit was installed in 1993 and the other in 1999. The average life span of a water heater is eight to ten years. With the passage of time and lack of water treatment, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. Due to the inconsistent usage of the facility, it is recommended to replace these units with an on demand water heating system to reduce energy costs. Removal and disposal of the existing equipment is included in this estimate. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0678INT3 | JANITORS CLOSET REPAIRS | 0678 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0678INT4 | INTERIOR FINISHES | 0678 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Four to Ten Years | Long-Term Needs | 3 | 52020
0678CUL1 | CULINARY FIXTURES REPLACEMENT | 0678 | The existing plumbing fixtures in the culinary are worn and damaged and should be scheduled for replacement. Corrosion and mineral buildup has caused premature deterioration of the fixtures. This project recommends the replacement of the existing fixtures including the sprayers, faucets, handles, valves, filters, injectors and any other piping or equipment which has deteriorated or has signs of corrosion or mineral buildup. This project should be implemented concurrently with the WATER TREATMENT SYSTEM REPLACEMENT project. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0678PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0678 | The existing water softening/ treatment systems in the building are currently not operational. They have not been maintained and have reached the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project should be implemented concurrently with the CULINARY FIXTURES REPLACEMENT project. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0678ELE2 | EXTERIOR OUTLET REPLACEMENT | 0678 | There is an electrical outlet on the south side exterior of the building that does not meet code. This outlet should be changed to a GFCI type outlet per the 2005 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet with a weatherproof cover. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 300
0678EXT1 | EXTERIOR FINISHES | 0678 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Four to Ten Years | Long-Term Needs | 3 | 52020
0678SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0678 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/19/2012. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 4000
0678ADA1 | ADA SIGNAGE | 0678 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | FALLON ARMORY | 9885 | Military | NNG |  | Fallon | 1962 | 10404 | 2012-01-19 | Immediate to Two Years | Currently Critical | 1 | 750
9885SEC1 | CHAIN LINK FENCE UPGRADE | 9885 | The existing chain link fencing around the site has reached the end of its expected life and is due for an upgrade. It currently does not have a deterrent device such as barbed wire and the swinging vehicle gates require constant maintenance. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with barbed wire and two 14' wide sliding gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/19/2012. | FALLON ARMORY SITE | 9885 | Military | NNG |  | Fallon | 1962 |  | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65500
3087EXT1 | EXTERIOR FINISHES | 3087 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9885 | Military | NNG |  | Fallon | 0 | 960 | 2012-01-19 | Four to Ten Years | Long-Term Needs | 3 | 960
9885SIT1 | SLURRY SEAL ASPHALT PAVING | 9885 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 45,000 square feet of asphalt area was used to generate this estimate. | FALLON ARMORY SITE | 9885 | Military | NNG |  | Fallon | 1962 |  | 2012-01-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33750
2528EXT1 | EXTERIOR FINISHES | 2528 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZARDOUS MATERIAL STORAGE BUILDING 2 | 9886 | Military | NNG |  | Yerington | 1959 | 252 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1260
9886SIT3 | SLURRY SEAL ASPHALT PAVING | 9886 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and the parking lot. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 55,000 square feet of asphalt area was used to generate this estimate. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 41250
0996EXT2 | OVERHEAD DOOR REPLACEMENT | 0996 | There are two 16'x14' motorized overhead coiling doors which are damaged and do not function properly. Staff noted that the doors bind and get stuck when rolling up and down and have been serviced many times. They are original to the building, dating back to 1995 and should be scheduled for replacement. This project would provide for the removal and disposal of the motorized overhead coiling doors and replacement with two new motorized doors. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0692EXT2 | EXTERIOR FINISHES | 0692 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD OMS - WEIGHT ROOM | 9886 | Military | NNG |  | Yerington | 1959 | 1640 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 8200
0996EXT3 | EXTERIOR DOOR REPLACEMENT | 0996 | The exterior metal man door on the north side of the building is damaged from age and general wear and tear and has reached the end of its expected life. The threshold and door sweep have deteriorated and allow water to flow under the door. This project would provide for the replacement of the door assembly with a new metal door, frame, hardware, threshold and door sweep to ensure that water cannot get under the door. Removal and disposal of the existing door is included in this estimate. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0996ADA1 | ADA RESTROOM UPGRADES | 0996 | The ADA restrooms in the building do not entirely meet the Americans with Disabilities Act (ADA) requirements. It is necessary to make some specific upgrades to the restrooms to comply with the requirements. This project would provide funding for moving the water closet handle in the Men's restroom, moving the toilet paper dispensers, replacing the faucet handles and any other necessary upgrades to bring the restrooms into compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0692INT1 | INTERIOR FINISHES | 0692 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OLD OMS - WEIGHT ROOM | 9886 | Military | NNG |  | Yerington | 1959 | 1640 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 8200
0996INT2 | VCT FLOORING REPLACEMENT | 0996 | The VCT (vinyl composite tile) flooring in the office side of the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0996EXT4 | GUTTER INSTALLATION | 0996 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the dirt grade around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the standing seam metal roof over the shop. Drywells are included at downspout locations. Another option would be to install a gravel filled infiltration trench at drip edges to help mitigate erosion. Costs may vary depending which system is used. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0996SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0996 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 2200
0996SFT4 | FIRE ALARM SYSTEM INSTALLATION | 0996 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 17600
0996SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0996 | Approximately half of the building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system throughout the entire building and backflow prevention in the event the building is remodeled or an addition is undertaken. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 61600
0996ADA2 | ADA EMPLOYEE LOUNGE UPGRADES | 0996 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at the dining table and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 2000
0691EXT1 | EXTERIOR FINISHES | 0691 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 52020
0691INT1 | INTERIOR FINISHES | 0691 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 52020
0996EXT1 | EXTERIOR FINISHES | 0996 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0691ENR3 | HVAC REPLACEMENT | 0691 | Two of the four HVAC roof top units are 15 years old and the other two are 10 years old. They are not energy efficient and have reached or will soon reach the end of their expected and useful life. This project would provide for installation of new HVAC packaged units, cleaning of the existing duct work and grilles and a water treatment system for the supply water. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156060
2058ENR1 | LIGHTING UPGRADE | 2058 | The existing lighting fixtures are the older T-12 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested as well as an occupancy sensor. Any electrical wiring upgrades are not included in this estimate. | TIRE REPAIR/STORAGE BUILDING | 9886 | Military | NNG |  | Yerington | 1995 | 480 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
2527EXT1 | EXTERIOR FINISHES | 2527 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MCOFF RAMADA | 9886 | Military | NNG |  | Yerington | 0 | 800 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
9886SIT5 | LANDSCAPE UPGRADES | 9886 | The landscaping currently consists of shrubs and trees around the buildings which are difficult to maintain. The planting areas are overgrown and leaves and debris have built up over time. Maintenance personnel is understaffed and it is recommended to install less maintenance intensive landscape features. This project would provide for removing most of the shrubs and trees, altering the irrigation as needed and installing more landscape rock for coverage. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9886SIT4 | ASPHALT PAVING INSTALLATION | 9886 | The majority of the site is covered with dirt and has poor drainage. Other than the front parking lot there is no asphalt paving for vehicle and equipment circulation throughout the yard. Due to the large and heavy equipment commonly on site, the dirt and mud areas quickly become rutted and uneven. Poor drainage in the dirt areas also leaves large areas of standing water further exacerbating the problem. This project would provide asphalt cement paving to cover the majority of the site that is used for vehicle or equipment, circulation or storage. The estimate includes grading, base, compaction and installation of asphalt cement paving. If asphalt is not provided, it is recommended to regrade the site to ensure proper drainage. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
0996INT1 | INTERIOR FINISHES | 0996 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the office areas be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0691ENR1 | WINDOW REPLACEMENT | 0691 | The windows in the Drill Hall are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2057EXT1 | EXTERIOR FINISHES | 2057 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZARDOUS WASTE STORAGE BUILDING 1 | 9886 | Military | NNG |  | Yerington | 1990 | 252 | 2012-01-26 | Four to Ten Years | Long-Term Needs | 3 | 252
2058SFT1 | EGRESS LIGHTING INSTALLATION | 2058 | There is no emergency egress lighting in the building. Section 1006 of the 2006 IFC states that illumination is required for the means of egress at all times the building space is occupied. This project would provide for the purchase and installation of emergency egress lighting with battery backup in accordance with requirements stated in the code. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | TIRE REPAIR/STORAGE BUILDING | 9886 | Military | NNG |  | Yerington | 1995 | 480 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 450
9886ELE1 | ELECTRICAL REPAIRS | 9886 | The main site electrical equipment is in disrepair and should be scheduled for replacement. Much of the equipment is original to the site dating back more than 50 years, including the transformers and main switchgear. Insects and rodents have infested some exterior boxes due to missing cover plates and the in-ground electrical boxes are missing proper covers and do not drain water effectively. There are also numerous loose and/or exposed electrical wires and damaged electrical outlets, disconnects, switches and wrong identifying covers for electrical pull boxes. This project would provide for replacement of the main electrical switchgear, transformers, in-ground boxes, trenching and backfill, repairs to the damaged electrical outlets, disconnects, new pull box cover lids with the proper identification indicated, and termination of loose or exposed electrical wires. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | YERINGTON ARMORY SITE | 9886 | Military | NNG |  | Yerington | 1959 |  | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 150000
0996SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0996 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | OMS #2 | 9886 | Military | NNG |  | Yerington | 1995 | 4400 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 4000
0691SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0691 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 07/21/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/26/2012. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Immediate to Two Years | Currently Critical | 1 | 4000
0691INT2 | JANITORS CLOSET REPAIRS | 0691 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0691ENV1 | VCT FLOORING REPLACEMENT | 0691 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. There is asbestos containing material (ACM) in the mastic and tiles so additional costs for abatement and disposal have been added to the estimate. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0691ENR2 | LIGHTING UPGRADE | 0691 | The existing high bay lighting fixtures in the Drill Hall are the older metal halide type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle such as LED fixtures. Any electrical wiring upgrades are not included in this estimate. | YERINGTON ARMORY | 9886 | Military | NNG |  | Yerington | 1959 | 10404 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2058EXT1 | EXTERIOR FINISHES | 2058 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TIRE REPAIR/STORAGE BUILDING | 9886 | Military | NNG |  | Yerington | 1995 | 480 | 2012-01-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2516EXT1 | EXTERIOR FINISHES | 2516 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHADE RAMADA | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 400 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2516ADA1 | ADA PICNIC TABLE INSTALLATION | 2516 | The Shade Ramada provides an employee break area outside including picnic tables. While access to this area appears to be ADA compliant, there are no accessible spaces provided at any of the picnic tables. This project would provide for the purchase and installation of a new accessible picnic table for the Shade Ramada. The table should be placed on an accessible path of travel from the building exit to the accessible space at the picnic table. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | SHADE RAMADA | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 400 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 1000
2170SFT1 | SECURITY LADDER GUARD | 2170 | The roof access ladder is a standard fixed steel ladder with the bottom rung 6 feet above the exterior concrete slab-on-grade sidewalk that is attached to the exterior of the building. The ladder currently does not have a ladder guard to prevent the public from using it and gaining access to the roof. This project would provide for a lockable ladder guard to be installed on the existing ladder to prevent unauthorized use by the public. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2011. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 3000
2000ADA1 | ADA SIGNAGE | 2000 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2011. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
2000ADA2 | ADA EMPLOYEE LOUNGE UPGRADES | 2000 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 2000
2170HVA1 | HVAC EQUIPMENT REPLACEMENT | 2170 | The four HVAC roof top units were installed in 1997. They are not energy efficient and will soon reach the end of their expected and useful life. This project would provide for installation of one new HVAC package unit, three new evaporative coolers and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 11475
2170INT3 | CARPET REPLACEMENT | 2170 | The carpet in the staff office is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1085
2170EXT3 | EXTERIOR DOOR REPLACEMENT | 2170 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the metal man door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2170ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2170 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the desk, refrigerator and other items currently blocking the working space. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 250
2170INT2 | INTERIOR FINISHES | 2170 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3825
2170EXT2 | EXTERIOR FINISHES | 2170 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the EIFS and stucco, sealing the CMU, repairing grout for the tile and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the exterior finishes are addressed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DMV INSPECTION STATION | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 765 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 8775
2000HVA1 | HVAC SYSTEM REPLACEMENT | 2000 | The two hot water boilers and the roof mounted evaporative cooler were installed in 1997. They are not energy efficient and will soon reach the end of their expected and useful life. This project would provide for installation of new HVAC equipment and cleaning of the existing duct work and grilles in the next 6-7 years. This project includes removal and disposal of the existing equipment and all required connections to utilities. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 278100
2000ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2000 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the floor cleaning machine and other items currently blocking the working space. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 250
2000EXT4 | ROOF REPLACEMENT | 2000 | The single-ply membrane portion of the roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that the single-ply membrane portion of the roof be re-roofed in the next 5-6 years to be consistent with the roofing program and the end of the warranty period. This project does not include replacing the standing seam metal portion of the roof which has a longer life span. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 150000
2000INT4 | INTERIOR FINISHES | 2000 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 92700
2000EXT3 | EXTERIOR FINISHES | 2000 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the EIFS, sealing the CMU, repairing grout for the tile and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the exterior finishes are addressed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HENDERSON DMV OFFICE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 1997 | 18540 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 92700
9888SIT3 | SEAL ASPHALT PAVING | 9888 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and testing courses. Striping is included in this estimate. This project should be scheduled on a 4 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt area was used to generate this estimate. | HENDERSON DMV SITE | 9888 | MtrVeh | B&G | MtrVeh | Henderson | 0 |  | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 120000
9889ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9889 | There are 25 existing light poles around the site with 34 total light fixtures attached. The existing light fixtures are the older 400 watt metal halide type and are not energy efficient. This project will upgrade the fixtures to higher efficiency LED exterior lights with solar panels for power. | SOUTHERN NEVADA VETERANS HOME SITE | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
2106INT3 | DOOR HARDWARE REPLACEMENT | 2106 | The panic hardware mechanisms on the interior doors are reaching the end of their expected life and should be scheduled for replacement. The mechanisms are damaged from age and general wear and tear and are beginning to fail. This project would provide for the replacement of the panic hardware throughout the building with new panic hardware. Removal and disposal of the existing mechanisms is included in this estimate. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9889SIT3 | CRACK FILL & SEAL ASPHALT PAVING | 9889 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including the access road, parking areas and the vehicle storage area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 90,000 square feet of asphalt area was used to generate this estimate. | SOUTHERN NEVADA VETERANS HOME SITE | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 |  | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 54000
2106ENR1 | ENERGY MANAGEMENT SYSTEM REPLACEMENT | 2106 | The YAMAS energy management system is original to the building and should be scheduled for replacement. Replacement parts for performing routine and emergency maintenance are not made anymore and the system has recently had numerous failures. In a facility of this type, it is imperative that the conditioned spaces are properly controlled at all times. This project would provide for the removal and disposal of the existing YAMAS energy management system and replacement with new equipment including all required connections to utilities and equipment. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 30000
2106SFT6 | FIRE ALARM SYSTEM UPGRADE | 2106 | This building is equipped with an automatic fire detection and alarm system that was installed in 2000. It is recommended that the system be scheduled to be upgraded in approximately 10 years to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the version of the IBC that is adopted at the time and the State Fire Marshal's requirements at the time. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Four to Ten Years | Long-Term Needs | 3 | 335840
2106INT2 | INTERIOR FINISHES | 2106 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 419800
2106EXT6 | DRIP EDGE INSTALLATION | 2106 | There are areas around the perimeter of the building where the foundation does not line up properly with the exterior insulation and finish system (EIFS) and there is no drip edge at the bottom of the EIFS. In many of these areas, there are gaps large enough to allow rodents and insects to enter the walls and infest the building. This condition also allows moisture to penetrate the walls which will lead to premature failure of the walls and possibly mold related issues. This project recommends installing a drip edge to direct water away from the building and flashing and caulking as needed around the entire perimeter of the building to close all of the gaps. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9400
2106EXT7 | ROOF REPAIRS | 2106 | The metal roofing system has leaks in the valleys, at roof penetrations, translucent skylights and other areas where the caulking and sealant has deteriorated. This project would provide for sealing and caulking of these areas particularly the 183 boots around the pipe penetrations. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2106EXT5 | EXTERIOR FINISHES | 2106 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 419800
3112EXT1 | EXTERIOR FINISHES | 3112 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VEHICLE SHADE STRUCTURE | 9889 | VetSvc | VetSvc |  | Boulder City | 2009 | 2160 | 2012-04-10 | Four to Ten Years | Long-Term Needs | 3 | 2160
2106SFT1 | JANITORS CLOSET REPAIRS JANITORS CLOSET REPAIRS | 2106 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of 24 Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 06/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33600
2106SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2106 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 06/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Immediate to Two Years | Currently Critical | 1 | 4000
2106EXT1 | GUTTER AND DOWNSPOUT INSTALLATION | 2106 | The building does not have rain gutters and down spouts at all building entrances and patios. During times of inclement weather, water pours off of the metal roof down onto public and private entrances and patios causing concerns for safety. Water damage to certain areas of the building may occur if the water is not directed away from the building exterior. This project would provide for the purchase and installation of seamless gutters and down spouts to divert the water away from the building entrances and patios and the exterior finishes of the building. This project or a portion thereof was previously recommended in the FCA report dated 06/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | SOUTHERN NEVADA VETERANS HOME | 9889 | VetSvc | VetSvc |  | Boulder City | 2000 | 83960 | 2012-04-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0614EXT1 | EXTERIOR FINISHES | 0614 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE SHELTER | 9889 | VetSvc | VetSvc |  | Boulder City | 2001 | 624 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 624
2997EXT1 | EXTERIOR FINISHES | 2997 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 22220
2997ENR1 | CANOPY INSTALLATION | 2997 | The south facing elevation has no protection from the sun. Staff noted that the metal doors get so hot that you cannot touch them with bare hands and that there is an enormous heat load coming through the windows and doors even in winter months. This project would provide for installing a canopy along the entire south elevation to block the direct sunlight against the building. The new structure will have new concrete footings, steel framing and a metal standing seam roof. Design fees are not included in this estimate. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 135000
2997INT1 | INTERIOR FINISHES | 2997 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 22220
2997PLM1 | WATER TREATMENT SYSTEM INSTALLATION | 2997 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | MAINTENANCE/OFFICE BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4444 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9890SIT5 | ASPHALT PAVING REPAIRS | 9890 | There are several areas of asphalt paving that are damaged and in need of repairs. The asphalt is rolling up on itself as cars push it against the curb creating a thick mass of extra asphalt on the edge of the road. The cause of the problem may be a poor asphalt mix or too much asphalt placed in these areas. This project would provide for removing and replacing the damaged areas of asphalt. Disposal of the existing asphalt is included in this estimate. | SOUTHERN NV. VETERANS MEMORIAL CEMETERY | 9890 | VetSvc | VetSvc |  | Boulder City | 0 |  | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9890SIT6 | CONCRETE SWALE INSTALLATION | 9890 | The site has a drainage problem at the southwest corner of the new maintenance yard. During inclement weather, the rain accumulates in several areas adjacent to the perimeter fence and where materials are stored within the fence. This standing water also causes premature deterioration of the paving and other landscape improvements in the area. This project would provide for installation of a concrete swale outside of the perimeter fence to sufficiently carry the water away from the property. | SOUTHERN NV. VETERANS MEMORIAL CEMETERY | 9890 | VetSvc | VetSvc |  | Boulder City | 0 |  | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2998EXT2 | ROOF REPAIRS | 2998 | The standing seam metal roof on this structure had active leaks at the time of the survey. The leaks were evidenced by broken light fixtures under the roof which were filled with water. It is recommended that the roof structure is repaired immediately to prevent further damage to equipment which it is supposed to protect. | OPEN METAL CANOPY | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4200 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 7500
2998EXT1 | EXTERIOR FINISHES | 2998 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OPEN METAL CANOPY | 9890 | VetSvc | VetSvc |  | Boulder City | 2009 | 4200 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 8400
9890SIT4 | CRACK FILL & SEAL ASPHALT PAVING | 9890 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 225,000 square feet of asphalt area was used to generate this estimate. | SOUTHERN NV. VETERANS MEMORIAL CEMETERY | 9890 | VetSvc | VetSvc |  | Boulder City | 0 |  | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 135000
3150EXT1 | EXTERIOR FINISHES | 3150 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OUTDOOR COMMITTAL BLDG | 9890 | VetSvc | VetSvc |  | Boulder City | 2012 | 691 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 3455
2105EXT5 | EXTERIOR DOOR HARDWARE REPLACEMENT | 2105 | The sliding glass doors on the south side of the building are damaged from age and general wear and require new hardware. The doors are used frequently by the staff and the public and are currently very difficult to operate. This project would provide for the replacement of the sliding glass door hardware including the handles, rollers, strikes and bumpers. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2105EXT4 | WINDOW REPLACEMENT | 2105 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. Several panes have detached from the aluminum frames and are sliding down. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of approximately 100 units. Removal and disposal of the existing windows is included in this estimate. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
2105ADA3 | KITCHEN ADA UPGRADE | 2105 | The kitchenette does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 2000
2105ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2105 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 4000
3147EXT1 | EXTERIOR FINISHES | 3147 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2012 | 2741 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 13705
2105EXT2 | ROOF REPAIRS | 2105 | The standing seam metal roofing and the single ply roof membrane on this building have active leaks on the north side of the building. The roof is 12 years old and should be under warranty. If the warranty is no longer valid, the estimate would provide for a licensed roofing contractor to repair the leaks. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 7500
2105INT3 | CEILING TILE REPLACEMENT | 2105 | The ceiling in the building is mostly covered with a suspended ceiling system. The ceiling tiles in the system are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2105INT2 | FLOORING REPLACEMENT | 2105 | The VCT (vinyl composite tile) and carpet in the building are damaged and have reached the end of their useful life. It is recommended that the flooring be replaced immediately. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 1-2 years. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 33600
2105EXT3 | ROOF REPLACEMENT | 2105 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1999. It is recommended that this building be re-roofed in the next 6-8 years to be consistent with the roofing program and the end of the warranty period. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 57600
2105ADA1 | ADA SIGNAGE | 2105 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Immediate to Two Years | Currently Critical | 1 | 1500
2105INT1 | INTERIOR FINISHES | 2105 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2105EXT1 | EXTERIOR FINISHES | 2105 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
3147INT1 | INTERIOR FINISHES | 3147 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION BUILDING | 9890 | VetSvc | VetSvc |  | Boulder City | 2012 | 2741 | 2012-04-12 | Four to Ten Years | Long-Term Needs | 3 | 13705
2105SIT1 | SITE BOLLARDS | 2105 | There is a loading/unloading area for visitors along the north side of the building. There are two pillars that have one or two 4" diameter roof drain downspouts protruding beyond the edge of the curb. This project recommends the installation of 4-8" diameter pipe bollards filled with concrete on each side of the pillars to protect the downspouts. This project or a portion thereof was previously recommended in the FCA report dated 06/09/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2012. | CHAPEL | 9890 | VetSvc | VetSvc |  | Boulder City | 1999 | 4800 | 2012-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2199EXT1 | EXTERIOR FINISHES | 2199 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 398690
2199INT1 | INTERIOR FINISHES | 2199 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 398690
2520EXT1 | EXTERIOR FINISHES | 2520 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MATERIAL STORAGE #4 | 9891 | Military | NNG |  | Carson City | 0 | 500 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 500
2523EXT1 | EXTERIOR FINISHES | 2523 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9891 | Military | NNG |  | Carson City | 0 | 2500 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2521EXT1 | EXTERIOR FINISHES | 2521 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the metal and sealing the concrete and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VEHICLE RAMADA #1 | 9891 | Military | NNG |  | Carson City | 0 | 1575 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1575
2987EXT1 | EXTERIOR FINISHES | 2987 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE GUARD STATION | 9891 | Military | NNG |  | Carson City | 2009 | 518 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 2590
2199EXT2 | WINDOW REPAIRS | 2199 | There are several windows around the building that are due for repair or replacement. Two windows have a broken seal and moisture has penetrated between the panes. These will need to be replaced. There may be additional windows throughout the building with the same problem. Also, several windows are showing signs of leaks around the frames and should be repaired to maintain a water proof building envelope. These windows were observed in the fitness room. This project would provide funding to repair or replace windows as needed. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 7500
2987INT1 | INTERIOR FINISHES | 2987 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ENTRANCE GUARD STATION | 9891 | Military | NNG |  | Carson City | 2009 | 518 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 2590
0271INT2 | CARPET REPLACEMENT | 0271 | The carpet tile floor covering in the building is showing signs of extreme wear. It is original to the building and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet tiles in the next 2-3 years. The estimate is based on 10,000 square feet of carpet. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1676EXT1 | EXTERIOR FINISHES | 1676 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208095
2199ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 2199 | There are two employee lounges in the building that do not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout each room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 4000
2199ADA2 | ADA CANE DETECTION BARRIER INSTALLATION | 2199 | The stairwell in the east corridor does not have 80" of clear head room under the stairs. This project recommends the installation of a permanent barrier under the stairs to warn blind or visually impaired persons of the low head room. NRS 338.180, IBC - 2006 Section 1012 and ADAAG 4.4.2 were referenced for this project. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 1000
0271EXT2 | EXTERIOR FINISHES | 0271 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 163700
0271INT1 | INTERIOR FINISHES | 0271 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting and sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. In the entry foyer, there is significant efflorescent damage on the brick masonry. This area should be dry-brushed to remove the minerals. With a thorough sealing on the exterior, this problem should be eliminated. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 163700
0271ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 0271 | The two employee lounges in the building do not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout each room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 4000
9891SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9891 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and maintenance yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 500,000 square feet of asphalt area was used to generate this estimate. | NEVADA NATIONAL GUARD CARSON CITY | 9891 | Military | NNG |  | Carson City |  |  | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
1453EXT1 | EXTERIOR FINISHES | 1453 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MATERIAL STORAGE #2 | 9891 | Military | NNG |  | Carson City | 2004 | 240 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 1200
1676ADA3 | ADA SHOWER UPGRADE | 1676 | The men's and women's locker rooms each have two shower stalls. The stalls are showing signs of aging and none of the shower stalls are ADA accessible or compliant. This project would provide for one ADA compliant stainless steel shower cabinet and one standard shower stall to be installed in each locker room. Included in this estimate is removal of the existing shower stalls and installation of new stainless steel shower stalls including two ADA compliant shower units complete with accessible plumbing fixtures, seat, etc. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 16000
0271ELE1 | ROOFTOP ELECTRICAL DUPLEX OUTLETS | 0271 | The building is equipped with several heating, ventilation and air-conditioning (HVAC) units on the roof. There are no electrical duplex outlets on the roof for servicing the rooftop equipment. The 2005 National Electrical Code Section 210.63 and 210.8 requires that a 125-volt, single-phase, 15 or 20 amps -rated GFCI duplex outlet shall be installed at an accessible location for the servicing of HVAC equipment. The receptacle shall be located on the same level and within 25 feet of the unit or units. This project would provide for the installation of eight 125-volt, 20 amp GFCI outlets within 25 feet of the HVAC equipment by a licensed electrical contractor. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | USPFO | 9891 | Military | NNG |  | Carson City | 2003 | 32740 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 5000
2518EXT1 | EXTERIOR FINISHES | 2518 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MAT STORAGE #3 | 9891 | Military | NNG |  | Carson City | 0 | 100 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 500
1452EXT1 | EXTERIOR FINISHES | 1452 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZ MATERIAL STORAGE #1 | 9891 | Military | NNG |  | Carson City | 2004 | 240 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 1200
2199SIT1 | SITE BOLLARDS | 2199 | There is a concrete loading/unloading tarmac along a portion of the west elevation of the building. There are seven brick columns that are unprotected and have the potential of being damaged by trucks running into them. This project would provide for 14 - eight inch diameter pipe bollards, filled with concrete at each side of the brick columns. This project or a portion thereof was previously recommended in the FCA report dated 06/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | OTAG BLDG./LAWRENCE E. JACOBSEN CENTER | 9891 | Military | NNG |  | Carson City | 2002 | 79738 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 11500
1676PLM4 | GATE VALVE REPLACEMENT | 1676 | The 6" main water line coming into the building is equipped with a gate valve to control flow. It has reached the end of its expected life and should be replaced in the next one to two years. This project would provide for replacing the valve and installing a new precast concrete vault around the valve with a solid cover and solid walls. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 4000
1676ADA4 | ADA RESTROOM UPGRADE | 1676 | The men's and women's locker rooms/ restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A significant retrofit is necessary. This project would provide funding for construction of accessible restroom facilities in the employee locker rooms/ restrooms. These items may include new sinks, toilets, hardware, mirrors, fixtures, flooring, lockers and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 25000
1676HVA1 | FUME HOOD EXHAUST SYSTEM INSTALLATION | 1676 | The building has a battery charging room which is equipped for flushing and neutralizing spilled electrolyte. Oxygen and hydrogen gasses are leaked into the air when the batteries are charging and in the right concentrations, these gasses can be highly explosive. The room does not have adequate ventilation for dispersal of these fumes from gassing batteries which is required by OSHA 1910.178(g) (2). This project would provide for a fume hood exhaust system to be installed with warning alarms. The estimate provides for the purchase and installation of an appropriate fume hood exhaust system including the hood, roof exhaust fan, ducting, wiring and any other necessary repairs. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1676INT1 | INTERIOR FINISHES | 1676 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 208095
1676ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 1676 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 2000
1676ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1676 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Immediate to Two Years | Currently Critical | 1 | 4000
1676PLM3 | WATER HEATER REPLACEMENT | 1676 | There is a 50 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Four to Ten Years | Long-Term Needs | 3 | 1500
1676ENR1 | HVAC EQUIPMENT REPLACEMENT | 1676 | The HVAC system was installed in 1992 and is original to the building. It consists of heating and air conditioning units with ducting to certain areas as well as ceiling mounted unit heaters in the garages and shops. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2012. | CSMS BUILDING | 9891 | Military | NNG |  | Carson City | 1992 | 41619 | 2012-02-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 499428
2494PLM2 | WATER HEATER REPLACEMENT | 2494 | There is a 50 gallon electric water heater in the building. It does not have seismic straps or an expansion tank. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2198EXT1 | EXTERIOR FINISHES | 2198 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2198INT1 | INTERIOR FINISHES | 2198 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2198EXT2 | ROOF REPLACEMENT | 2198 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 13500
2198EXT3 | EXTERIOR DOOR REPLACEMENT | 2198 | The 2 exterior wood man-doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2198HVA1 | HVAC REPLACEMENT | 2198 | The existing HVAC system consists of a roof mounted evaporative cooler and does not have any heating equipment. The evaporative cooler is failing and should be replaced. There is a need for heating equipment as well to provide a comfortable work environment in the winter. This project would provide for replacing the existing evaporative cooler with an exterior ground mounted packaged unit that provides propane fired heating as well as air conditioning. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2198EXT4 | OVERHEAD DOOR REPLACEMENT | 2198 | There are two 10'x10' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with new manually operated overhead doors. | CONSERVATION CAMP STORAGE | 9892 | CNR | Forestry |  | Jean | 2002 | 1500 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2494ENR1 | HVAC REPLACEMENT | 2494 | The HVAC roof top units were installed in 1992. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC packaged unit for the offices and a new evaporative cooler for the converted garage area. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2494SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2494 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 5184
2517INT1 | INTERIOR FINISHES | 2517 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2494ADA1 | ADA RESTROOM REMODEL | 2494 | The unisex restroom is original to the building and in overall poor condition. It does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 15000
2494PLM1 | WATER SOFTENER INSTALLATION | 2494 | The existing water softening system in the building stopped working and was removed. Untreated water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the installation of a new water softening system. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2494EXT3 | EXTERIOR DOOR REPLACEMENT | 2494 | The two exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2494EXT4 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 2494 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2494INT1 | INTERIOR FINISHES | 2494 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Four to Ten Years | Long-Term Needs | 3 | 6480
2494SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2494 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 18144
2517EXT1 | EXTERIOR FINISHES | 2517 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2517EXT2 | ROOF REPLACEMENT | 2517 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. There were several missing shingles and the plywood underlayment was exposed to the elements. It is recommended that this building be re-roofed immediately with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 960
2494EXT2 | WINDOW REPLACEMENT | 2494 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2517EXT3 | EXTERIOR DOOR REPLACEMENT | 2517 | The exterior wood man-door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | NDF FUEL BUILDING | 9892 | CNR | Forestry |  | Jean | 0 | 96 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2494EXT1 | EXTERIOR FINISHES | 2494 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | JEAN CC NDF OFFICE | 9892 | CNR | Forestry |  | Jean | 1992 | 2400 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1296
0883EXT2 | DEMOLISH STRUCTURE | 0883 | The building is an old Guard Tower that is no longer in use. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the Guard Tower. | JCC GUARD TOWER | 9892 | Correct | JCC |  | Jean | 0 | 288 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2125EXT2 | EXTERIOR DOOR REPLACEMENT | 2125 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the purchase and installation of eight new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
0663INT1 | INTERIOR FINISHES | 0663 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19670
0663EXT2 | EXTERIOR FINISHES | 0663 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11802
0663HVA1 | HVAC SYSTEM INSTALLATION | 0663 | The Intake area and the Medical area do not currently have any cooling equipment and are uncomfortably hot in the summer. The electric heaters are not energy efficient and have reached the end of their expected life. It is recommended to install HVAC equipment in these occupied areas to ensure a comfortable work environment. This project would provide for the purchase and installation of roof mounted HVAC units including all required connections to existing utilities. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 36000
1987INT2 | INTERIOR FINISHES | 1987 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
1986INT2 | INTERIOR FINISHES | 1986 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
1897INT3 | INTERIOR FINISHES | 1897 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
0663PLM1 | WATER HEATER REPLACEMENT | 0663 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit will be showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 1000
0662INT3 | INTERIOR FINISHES | 0662 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
0663ADA2 | ADA RESTROOM UPGRADES | 0663 | The ADA restroom does not entirely meet the current accessibility requirements. There is no under sink protection and the clear space required under the sink is blocked by the water heater. This project provides for installing under sink protection and relocating the water heater. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 500
0663ADA1 | ADA SIGNAGE | 0663 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 1500
1987PLM4 | WATER HEATER REPLACEMENT | 1987 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1986PLM2 | WATER HEATER REPLACEMENT | 1986 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2125LGT1 | ROOF REPLACEMENT | 2125 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 56800
1987SEC1 | EXTERIOR DOOR REPLACEMENT | 1987 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1986SEC1 | EXTERIOR DOOR REPLACEMENT | 1986 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0662PLM2 | WATER HEATER REPLACEMENT | 0662 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1897PLM2 | WATER HEATER REPLACEMENT | 1897 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0663INT2 | FLOORING REPLACEMENT | 0663 | The VCT (vinyl composite tile), carpet and painted concrete floors in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base, heavy duty commercial grade carpet and applying a new paint or sealant to the concrete in the next 2-3 years. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19670
0663SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0663 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 4000
0632INT3 | INTERIOR FINISHES | 0632 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 19660
2125EXT1 | EXTERIOR FINISHES | 2125 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28400
2125INT1 | INTERIOR FINISHES | 2125 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28400
1987EXT1 | EXTERIOR FINISHES | 1987 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
1987EXT2 | ROOF REPLACEMENT | 1987 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 9600
1987PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1987 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 5 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
1897PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1897 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
1986PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1986 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
0632PLM2 | WATER HEATER REPLACEMENT | 0632 | There are two 80 gallon propane-fired water heaters in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0662EXT1 | EXTERIOR FINISHES | 0662 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
1986EXT1 | EXTERIOR FINISHES | 1986 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 4 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
0662PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0662 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
0632SEC1 | EXTERIOR DOOR REPLACEMENT | 0632 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0632PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0632 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 20000
0632EXT2 | ROOF REPLACEMENT | 0632 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 9600
0632EXT1 | EXTERIOR FINISHES | 0632 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 1 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
2125PLM1 | WATER HEATER REPLACEMENT | 2125 | There are two 100 gallon propane-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2125CUL1 | CULINARY EQUIPMENT REPLACEMENT | 2125 | The culinary cooking equipment is original to the building and has reached the end of its lifetime. It is recommended that the equipment be scheduled for replacement in the next two to three years, including ovens and hoods, skittles, kettles, sinks, the icemaker, refrigerator and freezer cooling units and dishwasher. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
2125ADA1 | ADA RESTROOM UPGRADE | 2125 | The designated ADA restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | CULINARY/CANTEEN/DINING HALL | 9892 | Correct | JCC |  | Jean | 2000 | 5680 | 2011-11-03 | Immediate to Two Years | Currently Critical | 1 | 10000
1897EXT2 | ROOF REPLACEMENT | 1897 | The single-ply roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within ten years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Four to Ten Years | Long-Term Needs | 3 | 9600
0663INT4 | DOOR REPLACEMENT | 0663 | The existing metal door assemblies are in poor shape from age and wear and tear. This project would provide for the replacement of 11 metal door assemblies including all hardware and painting. Removal and disposal of the old door assemblies is included in this estimate. | ADMINISTRATION OFFICE/MEDICAL | 9892 | Correct | JCC |  | Jean | 1987 | 3934 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27500
1897EXT1 | EXTERIOR FINISHES | 1897 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the doors, window frames and other painted metal surfaces and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/03/2011. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19660
1897SEC1 | EXTERIOR DOOR REPLACEMENT | 1897 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 3 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0662SEC1 | EXTERIOR DOOR REPLACEMENT | 0662 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | HOUSING UNIT 2 | 9892 | Correct | JCC |  | Jean | 2000 | 3932 | 2011-11-03 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1898PLM1 | WATER HEATER REPLACEMENT | 1898 | There is a 40 gallon propane-fired water heater in the MPR and a 15 gallon electric water heater in the NDF Shop. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1898SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1898 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 4500
1898INT2 | FLOORING REPLACEMENT | 1898 | The VCT (vinyl composite tile), sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1898HVA2 | HVAC EQUIPMENT REPLACEMENT | 1898 | Some of the HVAC equipment servicing the building has recently been upgraded. This project addresses the remaining work to be done. The chapel, restrooms and second floor education rooms are heated by electric baseboard heaters and cooled by window mounted evaporative coolers. The NDF shops have older ceiling mounted heaters and roof mounted evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. The new equipment shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1898ADA3 | ADA SIGNAGE | 1898 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 750
1898ADA2 | ADA RESTROOM UPGRADE | 1898 | The building does not have an accessible restroom. The existing restrooms in the NDF shop, Visitation and Gymnasium do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of 3 restrooms is necessary. This project would provide funding for construction of three unisex accessible restrooms. These items may include a new sink, toilet, shower, hardware, mirrors, fixtures, flooring and paint in each restroom. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 45000
1898EXT5 | EXTERIOR DOOR REPLACEMENT | 1898 | The exterior metal doors are damaged from age, abuse and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the 5 exterior metal man-doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1898EXT4 | WINDOW REPLACEMENT | 1898 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1898INT1 | INTERIOR FINISHES | 1898 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
1898EXT3 | EXTERIOR FINISHES | 1898 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is replacing damaged metal panels and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. It is recommended that the earth to metal siding contact be mitigated to prevent further damage to the metal siding panels. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
1898SFT3 | STAIR REPLACEMENT | 1898 | The three sets of stairs and handrails between the first floor and the second floor do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. The stairs do not have the correct rise and run, one stairway is less than 44" wide and they are either missing handrails altogether or have handrails that do not meet code. This project would provide funding to remove and replace the stairways and handrails. This project or a portion thereof was previously recommended in the FCA report dated 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 15000
1898ELE2 | ELECTRICAL UPGRADE | 1898 | There are numerous instances of broken, outdated and non-code compliant electrical elements in the building. These include exposed wiring on a water heater, broken or missing outlet covers, broken receptacles, and wiring not in proper conduit. Also, this building was constructed before the high demand for electrical services were needed for computers, vehicle repair equipment and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. It is recommended the entire system be upgraded for safety and code compliance and to meet the evolving needs of the building including three-phase power. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 91000
9892SFT1 | EXTERIOR STAIR / HANDRAIL INSTALLATION | 9892 | The concrete exterior stairs leading from the Visitors parking area to the MPR/ Visitation Building are lacking handrails as required in the 2012 IBC Chapter 10, Section 1012. There is also a stairway constructed with railroad ties which is lacking handrails and is not compliant with current building codes. This project would provide for a tubular steel framed handrail to be installed on both sets of stairs. This project recommends reconstructing the railroad tie stairs to meet current building codes or eliminating them. The construction cost includes handrails and new stairs. This project or a portion thereof was previously recommended in the FCA reports dated 05/03/2005 and 11/03/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/30/2014. | JEAN CONSERVATION CAMP SITE | 9892 | Correct | JCC |  | Jean | 2000 |  | 2014-01-30 | Immediate to Two Years | Currently Critical | 1 | 10000
1898EXT6 | OVERHEAD DOOR REPLACEMENT | 1898 | There are two 10'x14' overhead coiling doors for the building. One has recently been replaced, the other does not function properly. Exposure and wind have caused the door to bend, crack and lose its finish. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. | MPR/VISITATION/NDF SHOP | 9892 | Correct | JCC | Forestry | Jean | 1987 | 9100 | 2014-01-30 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2512EXT1 | EXTERIOR FINISHES | 2512 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
2512INT1 | INTERIOR FINISHES | 2512 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
2512SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2512 | The building does not have an exit sign or emergency lighting. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 800
2512HVA1 | HVAC EQUIPMENT REPLACEMENT | 2512 | The packaged roof top unit was installed in 1997. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | FMWCC ARMORY | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 320 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 3500
2457HVA7 | CULINARY MAKE-UP AIR REPLACEMENT | 2457 | There are two roof mounted make-up air units for the culinary equipment that are reaching the end of their useful life and should be scheduled for replacement. This project would provide for the installation of two new roof mounted make-up air units including variable frequency drive fan motors for energy efficiency. Removal and disposal of the old equipment and connections to existing utility and ductwork is included in this estimate. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 40000
2457PLM1 | WATER SHUT OFF VALVES | 2457 | The original building has a 2" domestic water line that circles the interior of the building. There is no way to shut off the water supply to the individual wings without shutting off water service to the whole building. This project will provide four 2" brass gate valves to be installed in 4 strategic locations recommended by facility staff. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2786EXT1 | EXTERIOR FINISHES | 2786 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting of the doors, window frames and other painted metal surfaces and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FMWCC DORM HOUSING UNIT #9 | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 23780 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 118900
2786INT1 | INTERIOR FINISHES | 2786 | The interior finishes are in fair condition. It is recommended that the interior CMU and gypsum board walls be sealed and painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FMWCC DORM HOUSING UNIT #9 | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 23780 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 47560
2457EXT3 | EXTERIOR FINISHES | 2457 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the control joints, windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 996060
2457INT5 | INTERIOR FINISHES | 2457 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 996060
2457EXT4 | ROOF REPLACEMENT | 2457 | The roof on the 1997 portion of the building was in fair to poor condition at the time of the survey. The built-up ballasted roof system is 15 years old and numerous leaks have occurred recently. It is recommended that this older ballasted roof be replaced with a single-ply membrane system in the next 2-3 years. The new membrane will have a 20 year warranty with a preventative maintenance agreement to ensure that any future leaks will be repaired by the manufacturer. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1706544
2457INT6 | SHOWER REPLACEMENT | 2457 | The shower ceilings, walls, floors and fixtures in Housing Units A & B are in poor condition and should be scheduled for replacement. The gypsum board ceiling has been removed and the ceramic tile walls and painted concrete flooring are damaged and failing. The exposed pipes at the ceiling are rusting and should not be exposed to the wet environment and is also a safety concern for inmates. This project would provide for removing the walls, ceilings, flooring and fixtures and replacing them with a uniform ceramic tile finish or stainless steel units. Removal and disposal of the existing materials is included in the estimate. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 170000
2457CUL1 | SERVING TRAY REPLACEMENT | 2457 | The hot and cold serving trays in the culinary are original to the building and are no longer operating. Considering the age of the equipment and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the 6-well steam table and the 6-well cold table with new equipment. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2457PLM3 | DRYER EXHAUST DUCT UPGRADE | 2457 | Each of the four clothes dryers are vented with one 90 degree elbow and goes vertically 25’ through the roof and protrudes above the ceiling by another 2 feet. The IMC 504.6.1 states the maximum length of a clothes dryer exhaust duct shall not exceed 25 ft from the dryer location to the outlet terminal. The maximum length of duct shall be reduced 2 ½ feet for each 45-degree bend and 5 feet for each 90-degree bend. This project recommends the installation of a booster fan installed on each of the four exhaust ducts per manufacture’s specifications to insure proper exhaust is obtained. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2513EXT1 | EXTERIOR FINISHES | 2513 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHADE RAMADA 1 | 9893 | Correct | FMWCC |  | North Las Vegas | 2004 | 484 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2457ADA1 | ADA SIGNAGE | 2457 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 3500
2457PLM4 | WASHER / EXTRACTORS & DRYER REPLACEMENT | 2457 | Two of the four commercial washer / extractors and tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility, it is recommended to replace them. This project provides for removal and disposal of the existing washer / extractors and tumbler dryers with new units. A total of 2 washers and 2 dryers was used for this estimate. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76000
2457HVA6 | HVAC REPLACEMENT | 2457 | The existing HVAC system in the original 1997 portion of the building consists of (6) 1,281 MBH output Lochinvar hot water boilers and approximately 38 roof top evaporative coolers and packaged units. They are not energy efficient and have reached the end of their expected and useful life. This equipment is original to the building and should be scheduled for replacement. This project would provide for replacing the boilers, the boiler controls, mixing valves, evaporative coolers and packaged units with new equipment and includes removal and disposal of the existing HVAC units and all required connections to utilities. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 2000000
2457ELE1 | TRANSFORMER REPLACEMENT | 2457 | There is an electrical transformer located inside the main electrical room. The transformer is original to the building dating to 1997 and creates excessive heat. This project recommends replacing the transformer with a new 225 kVA three phase power transformer. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2457SEC2 | SECURITY EQUIPMENT UPGRADES | 2457 | This building is equipped with a security system including monitoring equipment, door controls, video surveillance and communications. The new touch screen controls in the original building were installed in 2010. They were connected to the existing 1980's CCTV and Intercom electronics racks. This has caused problems with security because the new technology does not function properly with the old technology. Also, the new touch screen controls installed in 2010 have different functionality than the touch screen controls installed in the addition in 2008. This causes confusion with the operators who move from one system to the other on a day to day basis. This project would provide for the purchase and installation of CCTV and Intercom equipment to replace the original 1980's racks and upgrading the 2008 touch screen software to match the newer 2010 controls. Removal and disposal of the existing equipment and all required connections to existing utilities are included in this project.0 | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
2457PLM5 | WATER TREATMENT SYSTEM REPLACEMENT | 2457 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
2457HVA4 | REPLACE FREEZER COMPRESSORS | 2457 | There are two low velocity unit compressors servicing the culinary freezer. They are original to the building dating back to 1997. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. This project would provide for the removal and disposal of the existing compressors with new equipment including all required connections to utilities and equipment. The estimate is based on two 13,400 BTUH low velocity unit compressors. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9893PLM1 | SEWAGE GRINDER INSTALLATION | 9893 | The main sewage line exiting the facility is connected to the city sewer system. There is a lift station before the connection to the city line, but no sewage grinder. This has caused blockages and clogging of the lift station and piping requiring costly maintenance and repairs. It is recommended to install a sewage grinder on the main line before it reaches the lift station to remedy this problem. This project would provide for the purchase and installation of a sewage grinder on the existing sewer line. | FMWCC SITE | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 |  | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2457HVA5 | AIR CONDITIONER INSTALLATION | 2457 | The main electrical room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the electrical equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
3108EXT1 | EXTERIOR FINISHES | 3108 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHADE RAMADA 2 | 9893 | Correct | FMWCC |  | North Las Vegas | 2010 | 240 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 300
3107EXT1 | EXTERIOR FINISHES | 3107 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the metal siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SALLY PORT GUARD STATION | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 128 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 640
3107INT1 | INTERIOR FINISHES | 3107 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | SALLY PORT GUARD STATION | 9893 | Correct | FMWCC |  | North Las Vegas | 2008 | 128 | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 640
2457SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2457 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2457SFT2 | FIRE ALARM SYSTEM UPGRADE | 2457 | This building, excluding the recent addition, is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. At the time of the survey, the main fire alarm panel had a "trouble" status and staff indicated that they could not remedy the problem. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Immediate to Two Years | Currently Critical | 1 | 568848
2457INT2 | CARPET REPLACEMENT | 2457 | The carpet in the Administration/ Office wing is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/02/2011. | ADMINISTRATION/HOUSING UNITS | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 199212 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
2514EXT1 | EXTERIOR FINISHES | 2514 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior polycarbonate panels and caulking around the panels, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | FMWCC GREENHOUSE | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 | 360 | 2018-12-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
9893SIT4 | SLURRY SEAL ASPHALT PAVING | 9893 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 90,000 square feet of asphalt area was used to generate this estimate. | FMWCC SITE | 9893 | Correct | FMWCC |  | North Las Vegas | 1997 |  | 2018-12-11 | Four to Ten Years | Long-Term Needs | 3 | 67500
2510EXT1 | EXTERIOR FINISHES | 2510 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the stucco and metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RAWSON-NEAL HOSPITAL BUILDING 2 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 54146 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270730
2510INT2 | RESTROOM REMODELS | 2510 | The 12 restrooms in the client living areas are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. The original ceramic water closets pose a safety hazard and should be replaced with stainless steel fixtures. There is also a need for anti-ligature fixtures including the faucets. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RAWSON-NEAL HOSPITAL BUILDING 2 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 54146 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 180000
2508PLM1 | WATER HEATER REPLACEMENT | 2508 | There is a 100 gallon natural gas-fired water heater in the building that was installed in 2006. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2508ADA1 | ADA EMPLOYEE LOUNGE UPGRADES | 2508 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2508INT2 | RESTROOM REMODELS | 2508 | The 7 restrooms in the client living areas are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. The original ceramic water closets pose a safety hazard and should be replaced with stainless steel fixtures. There is also a need for anti-ligature fixtures including the faucets. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
2508INT1 | INTERIOR FINISHES | 2508 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 309690
2508EXT1 | EXTERIOR FINISHES | 2508 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the stucco and metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RAWSON-NEAL HOSPITAL BUILDING 1 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 61938 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 309690
9894SIT2 | GATE OPERATOR REPLACEMENT | 9894 | The site has a secured access gate for ambulances and other secured deliveries or pick ups. The hydraulic gate operator is 10 years old and has difficulty opening and closing the gates. This project recommends replacing the hydraulic swing gate operator and twin posts with a similar high quality operator as well as servicing the gates and related hardware to ensure prolonged operation. The gate operators will be required to meet UL Standard 325, per NRS 405.270. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
9894ADA1 | ADA PARKING SIGNAGE | 9894 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The 4 accessible parking areas on the south and east sides of the building are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking spaces. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Immediate to Two Years | Currently Critical | 1 | 6000
9894SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9894 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 164,000 square feet of asphalt area was used to generate this estimate. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 98400
2510INT1 | INTERIOR FINISHES | 2510 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RAWSON-NEAL HOSPITAL BUILDING 2 | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 | 54146 | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270730
9894SIT3 | STORAGE BUILDING INSTALLATION | 9894 | There is a major lack of storage on the site to support the various functions conducted by the facility. The Snack Bar is used exclusively as a storage space for the facility maintenance and janitorial personnel. Items stored here include paper goods, light bulbs, cleaning supplies, medical supplies and medical equipment. There is not enough storage space anywhere else in the building for these items. This project would provide for the purchase and installation of a 40' x 60' engineered steel building on a concrete foundation including connection to the existing electrical, water, sewer and propane services. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
9894ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9894 | There are approximately 16 existing light poles around the site with sodium halide fixtures. The older fixtures are not energy efficient and are due for an upgrade to a higher efficiency unit with a longer life cycle. This project would provide for the installation of 16 solar powered LED exterior light fixtures on the existing poles. | RAWSON-NEAL PSYCHIATRIC HOSPITAL SITE | 9894 | HHS | DPBH | SNAMHS | Las Vegas | 2006 |  | 2015-03-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
2486EXT2 | GUARDRAIL | 2486 | The NFPA 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an AWWA D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | MARLETTE LAKE 1 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1984 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2489ENR1 | LIGHTING UPGRADE | 2489 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4096
2504EXT1 | EXTERIOR FINISHES | 2504 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. Additional recommendations are to conduct inspections and testing on a cyclical basis based per NAC 445. | MARLETTE 1.5 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 2600 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
2504INT1 | INTERIOR FINISHES | 2504 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include inspection and cleaning of the interior walls and would also include: welding, sandblasting, repair work and to add protective coatings, if needed. It is important to follow ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | MARLETTE 1.5 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 2600 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2504INT2 | CONCRETE FOUNDATION | 2504 | The storage tank floor is made of concrete and was in poor condition at the time of the survey. This project would provide for the removal of the spalling and cracking concrete floor and the installation of a 4" thick concrete floor inside the walls of the water tank. | MARLETTE 1.5 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 2600 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 260000
2503EXT2 | EXTERIOR FINISHES | 2503 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE STORAGE SHED | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 48 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2503INT1 | INTERIOR FINISHES | 2503 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MARLETTE LAKE STORAGE SHED | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 48 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2503ENV1 | PEST CONTROL | 2503 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project would provide for the treatment and cleanup of the rodent droppings by a licensed pest control business. | MARLETTE LAKE STORAGE SHED | 9895 | Admin | PubWorks | B&G | Carson City | 0 | 48 | 2016-08-17 | Immediate to Two Years | Currently Critical | 1 | 5000
2489ENV1 | PEST CONTROL | 2489 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project would provide for treatment and cleanup of the rodent droppings by a licensed pest control business. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Immediate to Two Years | Currently Critical | 1 | 5000
2485EXT1 | EXTERIOR FINISHES | 2485 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. Additional recommendation is to conduct inspections and testing on a cyclical basis based per NAC 445. | MARLETTE LAKE 3 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1979 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
2489INT1 | INTERIOR FINISHES | 2489 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 512
2487EXT1 | EXTERIOR FINISHES | 2487 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE WATER TREATMENT BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1984 | 3500 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2486INT1 | INTERIOR FINISHES | 2486 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | MARLETTE LAKE 1 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1984 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2486EXT1 | EXTERIOR FINISHES | 2486 | It is important to maintain the finish, weather resistance and appearance of the tank. This project recommends work to protect the exterior of the tank to include; preparation for painting, caulk and paint. It is recommended for this project to be implemented in the next 2-3 years. Additional recommendation is to conduct inspections and testing on a cyclical basis based per NAC 445. | MARLETTE LAKE 1 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1984 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2485INT1 | INTERIOR FINISHES INTERIOR FINISHES | 2485 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | MARLETTE LAKE 3 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1979 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2489EXT3 | EXTERIOR FINISHES | 2489 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5120
2485EXT2 | GUARDRAIL | 2485 | The NFPA 22 standard designates the requirements for water tanks used for private fire protection. This tank is used to store water for fire protection and is an AWWA D100 tank that is required to have 360° guardrails. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | MARLETTE LAKE 3 MIL GALLON STORAGE TANK | 9895 | Admin | PubWorks | B&G | Carson City | 1979 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9895SIT1 | SIGNAGE | 9895 | The Waterfall Fire of 2004 burned the areas surrounding this site and damaged or destroyed signage. This project would provide for new signage to be installed in accordance with NRS. 207.200. This project or a portion thereof was previously recommended in the FCA report dated 03/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/17/2016. | MARLETTE LAKE/ ASH CANYON SITE | 9895 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2487ENV1 | PEST CONTROL | 2487 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project would provide for treatment and cleanup of the rodent droppings by a licensed pest control business. | MARLETTE LAKE WATER TREATMENT BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1984 | 3500 | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9895SIT2 | FENCING | 9895 | The Marlette Lake/ Ash Canyon Site is currently fenced off to the general public for safety. There are some areas of the fence that are damaged and should be repaired. This project would provide for repairs to the existing 6 foot tall industrial chain link fence. This project or a portion thereof was previously recommended in the FCA report dated 03/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/17/2016. | MARLETTE LAKE/ ASH CANYON SITE | 9895 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-08-17 | Four to Ten Years | Long-Term Needs | 3 | 8750
9895SIT4 | IRRIGATION SYSTEM | 9895 | The existing irrigation system’s sprinkler heads spray and wet the buildings. Much of the control wiring to the irrigation valves and some of sprinkler pipes are broken. The underground control values are worn and leaking. This project would provide funding for the repair and replacement of the necessary irrigation systems, water conservation and to move the irrigation to prevent the water from spraying on the building. This project or a portion thereof was previously recommended in the FCA report dated 03/03/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/17/2016. | MARLETTE LAKE/ ASH CANYON SITE | 9895 | Admin | PubWorks | B&G | Carson City | 0 |  | 2016-08-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85000
2489EXT2 | ROOF REPLACEMENT | 2489 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | MARLETTE LAKE CHLORINE BUILDING | 9895 | Admin | PubWorks | B&G | Carson City | 1989 | 512 | 2016-08-17 | Four to Ten Years | Long-Term Needs | 3 | 6144
0668LGT1 | EXTERIOR FINISHES | 0668 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, and integrity of the building. This project includes painting of exterior door assembly, weather stripping, and sealant around the roof penetrations. | AMMO BUNKER #1 | 9896 | Military | NNG |  | Carson City | 1973 | 600 | 2005-03-03 | Four to Ten Years | Long-Term Needs | 3 | 3000
2502LGT1 | EXTERIOR FINISHES | 2502 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, and integrity of the building. This project includes painting of exterior door assembly, weather stripping, and sealant around the roof penetrations. | AMMO BUNKER #3 | 9896 | Military | NNG |  | Carson City | 1973 | 600 | 2005-03-03 | Four to Ten Years | Long-Term Needs | 3 | 3000
2501LGT1 | EXTERIOR FINISHES | 2501 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, and integrity of the building. This project includes painting of exterior door assembly, weather stripping, and sealant around the roof penetrations. | AMMO BUNKER #2 | 9896 | Military | NNG |  | Carson City | 1973 | 600 | 2005-03-03 | Four to Ten Years | Long-Term Needs | 3 | 3000
0655EXT1 | EXTERIOR FINISHES | 0655 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Approximately 1/8 of the exterior of the building is sealed concrete masonry units, the rest is steel framing with metal siding. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52524
2466EXT1 | EXTERIOR FINISHES | 2466 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY SHOP / FEED STORAGE | 9897 | Wildlife |  |  | Boulder City | 2005 | 5360 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5360
0907SFT1 | FIRE SEPARATION UPGRADE | 0907 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
2466HVA1 | CONDENSATE LINE REPAIRS | 2466 | The building has two roof-mounted evaporative coolers that are leaking water and damaging the roof. The condensate lines have leaks in them and since the water is untreated, it is staining the standing seam metal roof and will cause corrosion and rusting if left unrepaired. This project would provide for replacement of the condensate lines to prevent any further damage. | HATCHERY SHOP / FEED STORAGE | 9897 | Wildlife |  |  | Boulder City | 2005 | 5360 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 1000
2466INT1 | INTERIOR FINISHES | 2466 | The interior finishes are in fair condition. It is recommended that the painted interior walls be painted at least once in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. The open framed walls and ceilings with exposed insulation should be covered by netting to prevent the birds from destroying the insulation. Alternatively, the walls could be covered by gypsum board and painted at an increased cost. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY SHOP / FEED STORAGE | 9897 | Wildlife |  |  | Boulder City | 2005 | 5360 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26800
0656EXT1 | EXTERIOR FINISHES | 0656 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | LOWER REARING SHADE SHELTER | 9897 | Wildlife |  |  | Boulder City |  | 23760 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 23760
2468EXT1 | EXTERIOR FINISHES | 2468 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide funding to protect the exterior of the structure. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the structure be painted and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY FEED BINS | 9897 | Wildlife |  |  | Boulder City | 2005 | 500 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2469EXT1 | EXTERIOR FINISHES | 2469 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | UPPER REARING BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 34000 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34000
2465INT1 | INTERIOR FINISHES | 2465 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2464INT1 | INTERIOR FINISHES | 2464 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2465EXT1 | EXTERIOR FINISHES | 2465 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2464EXT1 | EXTERIOR FINISHES | 2464 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
0913EXT1 | EXTERIOR/ INTERIOR FINISHES | 0913 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY WATER AERATION TOWER | 9897 | Wildlife |  |  | Boulder City | 2005 | 400 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2464SFT1 | FIRE SEPARATION UPGRADE | 2464 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
0906EXT1 | EXTERIOR FINISHES | 0906 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | FILTER BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 417 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2085
0654EXT1 | EXTERIOR FINISHES | 0654 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2464PLM1 | WATER HEATER REPLACEMENT | 2464 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #3 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
0907PLM1 | WATER HEATER REPLACEMENT | 0907 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
0907INT1 | INTERIOR FINISHES | 0907 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
0907EXT1 | EXTERIOR FINISHES | 0907 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #2 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
0654SFT1 | FIRE SEPARATION UPGRADE | 0654 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
0654PLM1 | WATER HEATER REPLACEMENT | 0654 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
0654INT1 | INTERIOR FINISHES | 0654 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY RESIDENCE #1 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11750
2465PLM1 | WATER HEATER REPLACEMENT | 2465 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
0657EXT1 | EXTERIOR FINISHES | 0657 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | HATCHERY FIRE PUMP STATION | 9897 | Wildlife |  |  | Boulder City | 2005 | 176 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176
2465SFT1 | FIRE SEPARATION UPGRADE | 2465 | Section R309.2 of the 2012 International Residential Code states that, "The garage shall be separated from the residence and its attic area by not less than 1/2" Type X gypsum board applied to the garage side." The attic access in the ceiling of the garage is only covered by a piece of plywood which does not meet this requirement. Without the proper fire-rated assembly between the garage and the attic, the safety of the occupants and the protection of the structure are compromised. This project would provide for the purchase and installation of the gypsum board at the attic access to meet the requirements of the code. | HATCHERY RESIDENCE #4 | 9897 | Wildlife |  |  | Boulder City | 2005 | 2350 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 500
0655SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0655 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/06/2016. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 6715
0655SFT1 | DIESEL FUEL TANK SHUTOFF REPLACEMENT | 0655 | The existing emergency shutoff switch for the diesel fuel tank and delivery system is due for replacement. The switch is over 30 years old, does not have a sign to identify it, and is difficult to locate. This project would replace the existing switch with a new mushroom switch and install clear signage to identify and locate the switch. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Immediate to Two Years | Currently Critical | 1 | 1500
0914EXT1 | EXTERIOR FINISHES | 0914 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | NORTH EQUIPMENT STORAGE | 9897 | Wildlife |  |  | Boulder City |  | 1050 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
9897LGT1 | CRACK FILL & SEAL ASPHALT PAVING | 9897 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and maintenance yards. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 162,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | LAKE MEAD FISH HATCHERY SITE | 9897 | Wildlife |  |  | Boulder City | 1972 |  | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97200
0655INT1 | INTERIOR FINISHES | 0655 | The interior finishes are in fair condition. Approximately 3,500 square feet of the building is finished with painted gypsum board. It is recommended that the painted interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
0912EXT1 | EXTERIOR FINISHES | 0912 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | OUTFLOW SHED | 9897 | Wildlife |  |  | Boulder City | 1975 | 176 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 352
0655ELE1 | GENERATOR REPLACEMENT | 0655 | The raceways have automatic monitors controlling the PH levels, oxygen levels and automatic fish feeders. Water is apportioned between the hatchery and residences after it enters the system through an aeration tower. During power outages, water is re-circulated back to the aeration tower and a portion of this contaminated water eventually ends up at the tap of the residences and the water in the raceways becomes potentially deadly for the fish. The building has a back-up generator system to prevent this hazard that was installed in 1973. The generator is constantly breaking down and has been rebuilt several times. The exhaust mufflers are within 6" from the wood timbers on the exterior of the building and should be re-routed. This project would provide for a new diesel powered 375 KVA generator including required connections to utility systems and relocating the exhaust mufflers. This project or a portion thereof was previously recommended in the FCA report dated 10/11/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/11/2012. | VISITATION/HATCHERY BUILDING | 9897 | Wildlife |  |  | Boulder City | 2005 | 26430 | 2012-04-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
2500INT1 | INTERIOR FINISHES | 2500 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the office and restroom be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MAINTENANCE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 1872 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2499LGT1 | EXTERIOR FINISHES | 2499 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | ADMINISTRATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 2160 | 2011-12-08 | Four to Ten Years | Long-Term Needs | 3 | 10800
2500EXT1 | EXTERIOR FINISHES | 2500 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | MAINTENANCE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 1872 | 2011-12-08 | Four to Ten Years | Long-Term Needs | 3 | 28000
9898SIT2 | SLURRY SEAL PAVING | 9898 | It is important to maintain the asphalt concrete paving for the site. This project would provide for minor crack filling and slurry sealing of the paving . Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 65,000 square feet of asphalt area was used to generate this estimate. This project also recommends that the parking and loading area at the Pavilion and Information Office be scheduled for sealing and striping within the next one to two years as this area is heavily used and some area are showing signs of failure. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | NORTHERN VETERANS MEMORIAL CEMETERY SITE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 |  | 2011-12-08 | Immediate to Two Years | Currently Critical | 1 | 48750
9898SFT1 | CONCRETE REPAIR - PAVILION AREA | 9898 | The concrete sections and expansion joints in the concrete patio between the Pavilion and the Public Information Building have become tripping hazards due to heaving, frost freeze cycles and possibly from roots of the trees in the planters. This project would provide for the replacement of the damaged sections and affected expansion joints with new concrete. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | NORTHERN VETERANS MEMORIAL CEMETERY SITE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 |  | 2011-12-08 | Immediate to Two Years | Currently Critical | 1 | 10000
1943EXT1 | STOREFRONT / SLOPED GLAZING REPLACEMENT | 1943 | The storefront glazing system shows signs of failure due to age, exposure, broken seals around the glazing panels and water infiltration. This project would provide for new tempered glazing panels to be installed. Removal and disposal of the existing system in included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | CEMETERY PAVILION | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1944EXT1 | EXTERIOR FINISHES | 1944 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. | CEMETERY PUBLIC INFORMATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
2036EXT1 | EXTERIOR DOOR REPLACEMENT | 2036 | The existing double door assembly is damaged from heavy use and age. This project would provide for a new 6'-0"x7'-0" metal double door assembly including hardware, door stops and painting of door and frame. Included in this package price is the removal of a portion of the 6" concrete curb that interferes with the door operation on the south side. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | CEMETERY STORAGE 2 | 9898 | VetSvc | VetSvc |  | Fernley | 1997 | 144 | 2011-12-08 | Immediate to Two Years | Currently Critical | 1 | 2500
1944INT2 | INTERIOR FINISHES | 1944 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CEMETERY PUBLIC INFORMATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
2035EXT1 | EXTERIOR FINISHES | 2035 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and caulking around flashing, fixtures, and other penetrations to maintain the metal building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. | CEMETERY STORAGE 1 | 9898 | VetSvc | VetSvc |  | Fernley | 1994 | 1152 | 2011-12-08 | Four to Ten Years | Long-Term Needs | 3 | 2304
1943EXT2 | EXTERIOR FINISHES | 1943 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the pavilion, other than the roof, including painting, staining, sealing of the wood structure or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the pavilion in good, weather tight condition. It is recommended that this project be implemented in the next 2 years and is recommended on a cyclical basis based on environmental conditions. | CEMETERY PAVILION | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 576 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
1942SIT3 | INSTALL PIPE BOLLARDS | 1942 | The building is surrounded by asphalt paving. This project would add 8" diameter pipe bollards at areas of and to protect the exterior of the building and external utility riser connections. 12 pipe bollards was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | CEMETERY WELDING/STORAGE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 1152 | 2011-12-08 | Four to Ten Years | Long-Term Needs | 3 | 3600
1942EXT2 | OVERHEAD DOOR REPLACEMENT | 1942 | There is an exterior man door and infill framing where an overhead coiling door was once located. It is damaged and staff indicated that they would like the overhead door re-installed. This project would provide for installation of a new overhead coiling door and required framing. Removal of the existing wall and door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | CEMETERY WELDING/STORAGE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 1152 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2499INT2 | INTERIOR FINISHES | 2499 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION OFFICE | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 2160 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10800
2500INT2 | REPLACE FLOORING IN OFFICE | 2500 | The sheet vinyl in the office area is showing signs of wear due to age and heavy use. This project would provide for new vinyl floor tile to be installed in the office area of the building. Removal and disposal of the old sheet vinyl is included in this estimated. | MAINTENANCE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 2004 | 1872 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2036EXT2 | EXTERIOR FINISHES | 2036 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing of CMU or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented within the next 2 years and is recommended on a cyclical basis based on environmental conditions. | CEMETERY STORAGE 2 | 9898 | VetSvc | VetSvc |  | Fernley | 1997 | 144 | 2011-12-08 | Immediate to Two Years | Currently Critical | 1 | 720
1942ENR2 | LIGHTING UPGRADE | 1942 | The building lighting fixtures are older fluorescent units and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Sensors should be installed in low occupancy areas for additional savings. This project or a portion thereof was previously recommended in the FCA report dated 02/23/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/08/2011. | CEMETERY WELDING/STORAGE SHOP | 9898 | VetSvc | VetSvc |  | Fernley | 1990 | 1152 | 2011-12-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1728
2488PLM1 | WATER HEATER REPLACEMENT | 2488 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 3500
2488ADA2 | UNISEX ADA RESTROOM | 2488 | The building does not have an ADA accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. Relocation of the water heater is also part of this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 12400
2484EXT4 | EXTERIOR FINISHES | 2484 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 11500
2498EXT2 | EXTERIOR FINISHES | 2498 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | WATER MASTER HOUSE SHED | 9899 | Admin | PubWorks | B&G | Carson City | 1992 | 120 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 600
9899SIT4 | CRACK FILL & SEAL ASPHALT PAVING | 9899 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 15,000 square feet of asphalt area was used to generate this estimate. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2488ENR1 | LIGHTING REPLACEMENT | 2488 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom, office and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2488EXT3 | EXTERIOR FINISHES | 2488 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2484INT2 | INTERIOR FINISHES | 2484 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 11500
9899SEC1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9899 | There is no site lighting for the property which is a security and safety concern. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Four to Ten Years | Long-Term Needs | 3 | 65000
9899SIT5 | ASPHALT PAVING INSTALLATION | 9899 | The site has several areas with inadequate drainage due to erosion and clogged drains. A majority of the site is not paved allowing runoff to erode the dirt. Installing asphalt and drainage swales would allow for control of the runoff and prevention of flooding. This project would provide asphalt cement paving for the dirt areas of the site. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 217800
2488INT2 | INTERIOR WALL UPGRADE | 2488 | The interior walls have open framing with exposed batt insulation between the steel framing. It is recommended to install gypsum board to the interior walls along with taping, texturing and painting. There are public presentations held in this building and the exposed insulation is ripped and falling out in some places. This upgrade will improve the insulating properties of the building and provide a more finished look for the staff and visitors. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2484SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2484 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
2488SEC1 | SECURITY SYSTEM INSTALLATION | 2488 | The existing office storage building currently does not have a security system installed. Because the small office area contains the computer-controlled water distribution system for Virginia City, a security system is recommended. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2488HVA1 | HVAC EQUIPMENT REPLACEMENT | 2488 | The existing HVAC system consists of a wall mounted air conditioner and a wall mounted heater for the office along with an older ceiling mounted heater for the warehouse area. The electric heaters are inefficient and should be replaced with natural gas fired heaters. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide natural gas fired heating as well as air conditioning. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
2488INT1 | INTERIOR FINISHES | 2488 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings of the office and restroom at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2488SFT3 | NONABSORBENT FINISHES | 2488 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 3000
2498SIT1 | CONCRETE REPLACEMENT | 2498 | The concrete slab-on-grade in the shed is deteriorating. Spalling and cracking have occurred. Exposure to the weather is a contributing factor. This project addresses removal and replacement of the existing concrete slab. 120 SF of 4" thick concrete was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | WATER MASTER HOUSE SHED | 9899 | Admin | PubWorks | B&G | Carson City | 1992 | 120 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
9899SIT2 | FENCE REPLACEMENT | 9899 | The Marlette Lake site has several types of fencing surrounding the perimeter, all of which are in poor condition. Some sections are completely missing or have been blown down by the wind. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence around the entire site with two 14 foot wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. An agency approval of fencing design and/or material may be required and is not reflected in this project. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE WATER SYSTEM OFFICE SITE | 9899 | Admin | PubWorks | B&G | Carson City | 0 |  | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
2488SFT5 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2488 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 4000
2488SFT2 | SAFETY CABINETS | 2488 | The storage building contains gasoline, aerosol cans and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 10000
2484SFT1 | SMOKE ALARM INSTALLATION | 2484 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of smoke alarms in accordance with these codes. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 2000
2484SFT2 | EXTERIOR STAIR HANDRAIL INSTALLATION | 2484 | The exterior stairs and wrap around porch are lacking handrails and guardrails as required in section R311.7.8 of the 2012 International Residential Code. This project would provide for wood framed handrails and guardrails to be installed in accordance with the code. This project is contingent upon the approval of the State Historic Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | LAKEVIEW HOUSE | 9899 | Admin | PubWorks | B&G | Carson City | 1873 | 2300 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 5000
2488EXT1 | ROOF REPLACEMENT | 2488 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
2488ENR2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2488 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/18/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/25/2015. | MARLETTE LAKE OFFICE/STORAGE BUILDING | 9899 | Admin | PubWorks | B&G | Carson City | 1986 | 2400 | 2015-02-25 | Immediate to Two Years | Currently Critical | 1 | 6000
9900SIT1 | SLURRY SEAL ASPHALT PAVING | 9900 | It is important to maintain the asphalt concrete paving on the site. This project would provide for crack filling and slurry sealing of the paving site wide including access roads, parking areas and the helicopter apron. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 250,000 square feet of asphalt area was used to generate this estimate. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187500
2491ELE1 | ELECTRICAL UPGRADE | 2491 | This building was constructed before the high demand for electrical services were needed for computers, mechanical equipment and tools and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 77000
2491EXT1 | EXTERIOR FINISHES | 2491 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7700
2491SFT1 | FIRE SPRINKLER SYSTEM UPGRADE | 2491 | The Hangar has had an addition built on the taxiway side of the hangar that did not receive sprinkler protection. Also, a combustible shed roof has been constructed on the East side of the building over the existing emergency generator exhaust and the indoor fuel tank vent. This project would design and install sprinkler protection throughout the building. The cost does not include a possible fire pump or equipment storage building for the facility. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 25000
2490INT5 | KITCHENETTE REPLACEMENT | 2490 | The small kitchenette for the sleeping quarters is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. The sink and refrigerator are no longer operating. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
2490PLM3 | WATER HEATER REPLACEMENT | 2490 | There is a 100 gallon gas-fired water heater in the building that was installed in 1991. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2491INT1 | CARPET REPLACEMENT | 2491 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11900
9900SIT4 | PUMP-OUT LIFT STATION | 9900 | The sanitary sewer lift station is clogged with dirt submerging the pumps. This project would pump-out and clean the lift station. It is recommended that this project be scheduled on a cyclical basis based on usage. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 1500
2491HVA2 | EXHAUST FAN REPLACEMENT | 2491 | The existing exhaust fan that serves the restroom on the second floor is original equipment and is not operating. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of a new exhaust fan assembly including connections to utilities. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 1500
2490EXT5 | ATTIC ACCESS DOOR REPLACEMENT | 2490 | The north east attic access door has a broken hinge and the lock is not operational. This project would replace the door and hardware. In addition, the project would install a barrel bolt on the roof access hatch for security. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2490INT4 | JANITORS CLOSET REPAIRS | 2490 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
9900PLM1 | IRRIGATION SYSTEM REPLACEMENT | 9900 | The existing landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 4,000 linear feet was used to generate this estimate. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2490ENR1 | OCCUPANCY SENSOR INSTALLATION | 2490 | There are no occupancy sensors installed in the building to control lighting. It is recommended to install sensors in order to reduce energy costs. Occupancy sensors will be installed in restrooms, conference rooms, utility rooms and other low occupancy areas for additional savings. This project provides for purchase and installation of 10 sensors. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2490ELE3 | ELECTRICAL UPGRADE | 2490 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit and several of the exterior lighting fixtures are no longer operating. It is recommended the entire system be upgraded to meet the evolving needs of the building including repairing the exterior lighting. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130000
2490ELE2 | ATTIC LIGHTING INSTALLATION | 2490 | The building has HVAC equipment in the attic that requires maintenance. Section 210.70(C) of the 2012 Uniform Mechanical Code states that attics containing equipment requiring servicing, at least one lighting outlet containing a switch or controlled by a wall switch shall be installed in such places. This project would add permanent lighting in the attic to support maintenance. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2490SEC1 | SECURITY SYSTEM INSTALLATION | 2490 | The building does not have a security system. This project recommends video surveillance, motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
2490ADA3 | BREAK ROOM REMODEL | 2490 | The employee lounge does not meet the Americans with Disabilities Act (ADA) requirements. It is recommended to upgrade some of the features of the room for compliance with accessibility standards for employees (Title I). This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 2000
2490HVA1 | HVAC REPLACEMENT | 2490 | The HVAC system was installed in 1991 and is original to the building. It consists of a natural gas-fired boiler and chiller system with fan coil units in the attic. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 97500
9900SIT2 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9900 | There is very little site lighting for the access road, parking area and around the buildings which is a security and safety concern. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
2490ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2490 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 4000
2490ADA2 | ADA ENTRANCE REPAIRS | 2490 | The main ADA entrance is no longer compliant possibly due to the concrete settling and causing the elevation change into the building to exceed the limits. This project would provide for removing the concrete in front of the door and installing new concrete within the accessible limits to approach the entrance door. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 5500
2490INT2 | INTERIOR FINISHES | 2490 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2490SIT5 | PATIO UPGRADES | 2490 | The patio on the west side of the building is due for upgrades to protect the integrity of the building. The patio is not sloped away from the building allowing water to pool up next to the building, infiltrate the windows and damage the concrete foundation walls. In cold weather, the water freezes at the entrance door and is a slipping hazard. A temporary ramp has been installed at the entrance door which is not compliant with the building code. There is a roof drain that terminates near the entrance and contributes to the problems. This project would create positive flow away from the building by removing the existing concrete, regrading, installing French drains as needed, installing a new concrete patio and extending the roof drains away from the building. The new patio elevation should meet the threshold of the entrance door and allow the temporary ramp to be removed. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2491INT3 | INTERIOR FINISHES | 2491 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings in the office areas at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
2490EXT2 | EXTERIOR FINISHES | 2490 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2491EXT2 | FOLD-UP DOOR REPAIRS | 2491 | The large fold-up door on the north side of the Hangar is no longer operating and due for maintenance. The cables are fraying and the pulleys and other hardware are worn. This project would provide for the inspection and maintenance of the door including replacing the cables, greasing the hardware and replacing any other parts as necessary. | SIERRA FRONT INTERAGENCY HANGAR | 9900 | CNR | Forestry |  | Minden | 1991 | 7700 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
9900SIT3 | SITE BOLLARDS | 9900 | There is a filling station on the helicopter apron to distribute water or fire retardant. It is not protected by concrete bollards and has been backed into at least once. This area is in need of bollards to protect the filling station equipment. This project would provide funding for 8 - eight inch diameter bollards to be located on each corner of the filling station. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 4000
2490INT1 | FLOORING REPLACEMENT | 2490 | The carpet and floor tiles in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new heavy duty commercial grade carpet and padded carpet tiles for the raised floor in the Dispatch area in the next 2-3 years. This project excludes porcelain floor tile in restrooms. This project or a portion thereof was previously recommended in the FCA report dated 12/14/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 1991 | 6500 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49500
9900ENV1 | ABOVE GROUND FUEL TANK UPGRADES | 9900 | The existing above ground fuel tanks are located on a concrete slab with no curbs or proper drains to contain spills, no lighting and the emergency shut-off switch is in the wrong building. This project would install a concrete curb around the tanks to prevent soil contamination, a drain with a sand/ oil separator, outdoor lighting around the tanks and provisions to relocate the emergency shut-off switch from the Wildlife hangar to the Forestry hangar. | SIERRA FRONT INTERAGENCY DISPATCH CENTER | 9900 | CNR | Forestry |  | Minden | 0 |  | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 31000
0661ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0661 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 4000
0661ADA1 | ADA PARKING SPACE | 0661 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 2500
0661EXT1 | EXTERIOR FINISHES | 0661 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
0661ADA3 | ADA RESTROOM UPGRADE | 0661 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 1000
0661PLM1 | DOUBLE CHECK VALVE RELOCATION | 0661 | The existing double check valve serving the fire protection system is located in an underground vault. The valve is difficult to test and service. In addition, the test connections on the valve are corroding due to ground moisture. This project would raise the valve, install it in an above ground heated enclosure that will provide access for annual testing. Relocating the valve will require a new hydraulic analysis of the water supply. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0661INT2 | INTERIOR FINISHES | 0661 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/07/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/12/2013. | NDOW AIRCRAFT HANGAR | 9900 | Wildlife |  |  | Minden | 1996 | 6400 | 2013-11-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0520ADA2 | ADA SIGNAGE | 0520 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 2500
0338ADA3 | ADA SIGNAGE | 0338 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 5600
0520INT1 | INTERIOR FINISHES | 0520 | The interior finishes are in fair condition. It is recommended that the interior gypsum board walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. There are also damaged areas from forklifts that need repairs. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018 | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 108898
0520ADA1 | ADA RAMP UPGRADES | 0520 | This facility has an ADA accessible ramp located on the south side of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have proper handrails, signage or edge protection. This project would provide for an upgrade to the ramp to make it fully ADA compliant. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 35000
0520HVA3 | HVAC REPLACEMENT - OFFICES | 0520 | There are 2 wall-mounted packaged heating and cooling units installed in the offices. They are original to the building and have reached the end of their useful and expected life. This project would provide for 2 new packaged units to be installed including all required connections to utilities. The estimate includes removal and disposal of the old units. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 16800
0366INT1 | INTERIOR FINISHES | 0366 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 10080
0366ENR2 | EXTERIOR LIGHTING UPGRADE | 0366 | The existing exterior lighting fixtures are original to the building and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. Light emitting diode (LED) fixtures are suggested. The estimate is for the replacement of six fixtures which are located under the canopy structure and two porch lights, one by each exterior door. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 3528
0338HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0338 | An evaporative cooler is installed in the mechanical room that is no longer operational. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 3360
9901ADA4 | ACCESSIBLE ENTRANCE RAMP | 9901 | This facility has an ADA accessible ramp located on the east side of the building. This ramp is on the accessible path of travel from the accessible parking space to the rear entrance of the building. The ramp itself does not have compliant slopes and landings due to sub-grades shifting, settling and heaving. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO ROAD SITE | 9901 | MtrVeh | B&G |  | Las Vegas | 0 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 35000
0338INT4 | LIGHTING UPGRADE | 0338 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111300
0520HVA4 | EVAPORATIVE COOLER REPLACEMENT | 0520 | There are currently six evaporative coolers mounted on the roof of the warehouse. They are severely scaled and have reached the end of their serviceable life. This project would provide for six new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 26880
0338PLM2 | WATER HEATER REPLACEMENT | 0338 | There is a 40 gallon gas-fired water heater serving the customer restrooms. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 1680
0338INT3 | RESTROOM REMODEL | 0338 | The restroom is original to the building and in overall poor condition. The finishes, fixtures, toilet and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom and tile floor replacement. The removal and disposal of the existing fixtures and finishes is included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9901SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9901 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and driving test areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 228,382 square feet of asphalt area was used to generate this estimate. the curb stops are cracked and rebar is exposed causing a safety hazard. this project would provide for the replacement of 100 curb stops. | DMV FLAMINGO ROAD SITE | 9901 | MtrVeh | B&G |  | Las Vegas | 0 |  | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 329735
0338PLM3 | WATER HEATER REPLACEMENT | 0338 | There is a 40 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 1500
0338INT5 | JANITORS CLOSET REPAIR | 0338 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 1400
0366PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0366 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 22400
0366SFT1 | ROOF HATCH REPLACEMENT | 0366 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 5600
9901SIT3 | SIDEWALK REPLACEMENT | 9901 | The sidewalks serving the buildings on this site are deteriorated and failing. 400 SF of 4" thick concrete sidewalk was used for this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | DMV FLAMINGO ROAD SITE | 9901 | MtrVeh | B&G |  | Las Vegas | 0 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 4000
0338EXT1 | EXTERIOR FINISHES | 0338 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the concrete masonry units, repairing and painting the stucco and caulking of the metal panels, windows, flashing, fixtures and all other penetrations. Attention should be paid to the stucco which has extensive cracking and may need to be scheduled for repair. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/02/2004 and 04/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 356160
0338PLM1 | GAS METER ENCLOSURE REPAIRS | 0338 | The gas meter has a steel fence enclosure that has been damaged by a fork lift truck. This project would repair and repaint the enclosure. This project or a portion thereof was previously recommended in the FCA report dated 11/02/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/24/2018. | DMV FLAMINGO OFFICE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 31800 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0366EXT1 | EXTERIOR FINISHES | 0366 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/02/2004 and 04/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/24/2018 | DMV FLAMINGO INSPECTION STATION | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 900 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 10080
0520EXT1 | EXTERIOR FINISHES | 0520 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 11/02/2004 and 4/25/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 5/24/2018. | DMV FLAMINGO WAREHOUSE | 9901 | MtrVeh | B&G |  | Las Vegas | 1995 | 9723 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108898
1438ENR1 | LIGHTING UPGRADE | 1438 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
9902SFT1 | BACKFLOW PREVENTION | 9902 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | NDOW WESTERN REGION FALLON OFFICE | 9902 | Wildlife |  |  | Fallon | 0 |  | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 25000
0633EXT3 | EXTERIOR FINISHES | 0633 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 31200
0633INT1 | INTERIOR FINISHES | 0633 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 15600
1438EXT2 | EXTERIOR FINISHES | 1438 | It is important to maintain the finish, weather resistance, energy efficiency and appearance of the building. This project would provide funding to protect the exterior of the metal building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0633SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0633 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 43680
0633ADA1 | ADA SIGNAGE | 0633 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 1200
9902SIT1 | SLURRY SEAL ASPHALT PAVING | 9902 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 3,500 square feet of asphalt area was used to generate this estimate. | NDOW WESTERN REGION FALLON OFFICE | 9902 | Wildlife |  |  | Fallon | 0 |  | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2625
0633SFT1 | FIRE RATED DOOR REPAIRS | 0633 | Two fire rated doors have been removed from their original locations on the two north-west offices. The doors should be reattached to ensure the safety of the occupants by maintaining the original fire separations. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 500
0633EXT5 | EXTERIOR DOOR REPLACEMENT | 0633 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. There have been continuous maintenance problems with the connections between the door closers and the frames. This project would provide for the replacement of four exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0633ENR4 | WINDOW REPLACEMENT | 0633 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0633ENR1 | LIGHTING UPGRADE | 0633 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6240
0633ENV1 | PEST CONTROL | 0633 | There are numerous signs throughout this building of insect infestation including ants. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 1000
1438SFT1 | EXTERIOR LANDING INSTALLATION | 1438 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the west side of the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 500
0633STR1 | STRUCTURAL ASSESSMENT | 0633 | The foundation wall on the north facing elevation is showing significant water damage. The moisture has been weeping through the concrete from below the floor slab. The saturated concrete is crumbling and may be compromising the integrity of the structural system. This project recommends that a licensed structural engineer perform a structural investigation to assess the extent of the damage and recommend a plan to mitigate it. Future projects would be based on this report. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 2500
0633SFT3 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0633 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 3500
0633ENR3 | WATER HEATER REPLACEMENT | 0633 | There is a 28 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new energy efficient gas-fired water heater be installed. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 1500
9902SIT2 | ASPHALT PAVING INSTALLATION | 9902 | The gravel parking areas on the site should be scheduled for paving. The inclement weather in the area causes deterioration to the grade including potholes and negative drainage areas. This project would provide asphalt concrete paving to replace the gravel areas. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt concrete paving. 11,500 square feet of gravel area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | NDOW WESTERN REGION FALLON OFFICE | 9902 | Wildlife |  |  | Fallon | 0 |  | 2009-06-11 | Four to Ten Years | Long-Term Needs | 3 | 57500
1438PLM1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 1438 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Immediate to Two Years | Currently Critical | 1 | 3500
1438EXT1 | REPLACE OVERHEAD COILING DOORS | 1438 | Three of the four 10'x12' overhead coiling doors are damaged and do not function properly. Exposure, wind and vehicle collisions have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | DEPT. OF WILDLIFE BOAT STORAGE FACILITY | 9902 | Wildlife |  |  | Fallon | 1993 | 2250 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0633EXT2 | ROOF REPLACEMENT | 0633 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 46800
0633ENR2 | HVAC EQUIPMENT & SUPPORT REPLACEMENT | 0633 | The two HVAC roof top units are original to the building dating back to 1981. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units with an economizer system and cleaning of the existing duct work and grilles and recommisioning. This project also would provide for the investigation and repairs if needed for the HVAC support structure. It is recommended that a licensed engineer review existing conditions and make recommendations for remediation. The estimate also includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 10/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/11/2009. | WESTERN REGION FALLON FIELD OFFICE | 9902 | Wildlife |  |  | Fallon | 1974 | 3120 | 2009-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
9904ADA1 | INSTALL ADA ACCESSIBLE PARKING SPACE / ROUTE OF TRAVEL | 9904 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and route of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require placement of P.C. concrete, regrading, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 9000
2477EXT1 | DEMOLISH STRUCTURE | 2477 | The Quonset Hut is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA QUONSET HUT | 9904 | Wildlife |  |  | Mason Valley | 0 | 3000 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 15000
2982EXT1 | DEMOLISH STRUCTURE | 2982 | The Storage Building contains numerous code and safety issues including but not limited to damaged windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age of the building. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA STORAGE BUILDING | 9904 | Wildlife |  |  | Mason Valley | 0 | 96 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
2478EXT1 | EXTERIOR FINISHES | 2478 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for painting and sealing of the interior and exterior of the structure. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA EQUIPMENT MAINTENANCE BUILDING | 9904 | Wildlife |  |  | Mason Valley | 0 | 1500 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3000
9904SIT2 | ASPHALT PAVING INSTALLATION | 9904 | The parking area in front of the Office/ Headquarters is not paved. This project would provide asphalt cement paving for a 30,000 square foot parking lot. The estimate includes grading, 6" base, compaction, installation and striping of 4" thick asphalt cement paving. Design is not included in this estimate. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9904PLM2 | WATER LINE REPLACEMENT | 9904 | The underground water line between the North Pump House and Residence #4 has reached the end of its expected life and should be scheduled for replacement. This project recommends the installation of 3/4" schedule 40 PVC pipe to replace the existing pipe. 1,500 lineal feet was used for this estimate. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0649EXT4 | EXTERIOR DOOR REPLACEMENT | 0649 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear and are in need of replacement to seal the building. This project would provide for the replacement of four wood doors with four new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0649EXT3 | WINDOW REPLACEMENT | 0649 | The windows are original, single pane construction in a metal frame. These older windows are damaged and in need of replacement to seal the building. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0649EXT2 | ROOF REPLACEMENT | 0649 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0955EXT3 | DO0R LANDING INSTALLATION | 0955 | The exterior door does not have a landing. This project would provide for the installation of a 3 foot by 3 foot concrete landing, 4 inches thick. | MVWMA PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 200 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 100
0650EXT4 | EXTERIOR DOOR REPLACEMENT | 0650 | The exterior wood doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two exterior wood door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0650EXT3 | WINDOW REPLACEMENT | 0650 | The windows are original, dual pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
0956SFT1 | ENTRY LANDING / STAIR / HANDRAIL INSTALLATION | 0956 | The front entry landing and stairs do not meet the 2006 IBC Chapter 10 building code. The landing is required to be a minimum of 36 inches and the stair risers are not equal. The stairs are missing a handrail. This project would provide for the installation of a new concrete landing, stairs and handrail. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 1500
0650EXT2 | ROOF REPLACEMENT | 0650 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. Replacement of the evaporative cooler should be completed prior to or at the same time. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14250
0650EXT1 | EXTERIOR FINISHES | 0650 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. The estimate is based on 950 square feet at $10.00 per foot for the main building plus 800 square feet at $2.00 per foot for the trellis in front of the building. The estimate also provides for removing earth to wood contact by regrading around the exterior of the building. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11100
0959EXT2 | EXTERIOR FINISHES | 0959 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting, sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 8000
0957SFT1 | ENTRY STAIR HANDRAIL INSTALLATION | 0957 | The front entry stairs do not meet the 2006 IBC Chapter 10 building code. The stairs are missing a handrail. This project would provide for the installation of a new handrail on the stairs. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 500
0958SFT1 | STAIR HANDRAIL INSTALLATION | 0958 | The front entry stairs do not meet the 2006 IBC Chapter 10 building code. The stairs are missing a handrail. This project would provide for the installation of a new handrail for the stairs. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 500
0959INT2 | CEILING REPAIR | 0959 | The gypsum board in the closet ceiling is damaged and / or missing at the HVAC duct penetration. This project would provide for the repairs to the ceiling including installing new gypsum board and painting. It is recommended that this project be completed in the next two years. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 500
0959PLM2 | WATER HEATER REPLACEMENT | 0959 | There is a 50 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1750
0650INT1 | INTERIOR FINISHES / CEILING REPAIRS | 0650 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. Repair to the damaged ceilings is also included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4750
0957INT3 | FLOORING REPLACEMENT | 0957 | The carpet and sheet vinyl flooring in the building are showing signs of extreme wear. It is recommended that the carpet and sheet vinyl be replaced with heavy duty commercial grade carpet and VCT (vinyl composite tile) flooring in the next one to two years. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11200
0961EXT1 | DEMOLISH STRUCTURE | 0961 | The Garage is dilapidated and deteriorating and has reached the end of its useful life. There is evidence of roof leaks. This project would provide funding for the demolition of the building. | MVWMA GARAGE | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1250 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6250
0962EXT1 | DEMOLISH STRUCTURE | 0962 | The Wood Shop contains numerous code and safety issues including but not limited to transite siding, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age of the building. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA WOOD SHOP | 9904 | Wildlife |  |  | Mason Valley | 1955 | 640 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 6400
0650SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0650 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project does not include a water storage tank for fire protection which may be required if existing water flows are not adequate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 13300
2984EXT1 | EXTERIOR FINISHES | 2984 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project also includes costs for installing a 3'x3' concrete landing at the door. | MVWMA FILTER HOUSE 2 | 9904 | Wildlife |  |  | Mason Valley | 0 | 63 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 500
2985EXT1 | EXTERIOR FINISHES | 2985 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE 4 GREENHOUSE | 9904 | Wildlife |  |  | Mason Valley | 0 | 64 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2985INT1 | INTERIOR FINISHES | 2985 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE 4 GREENHOUSE | 9904 | Wildlife |  |  | Mason Valley | 0 | 64 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
2986EXT1 | EXTERIOR FINISHES | 2986 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE 4 GAZEBO | 9904 | Wildlife |  |  | Mason Valley | 0 | 128 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1280
0650ADA1 | ADA ACCESSIBILITY IMPROVEMENTS | 0650 | The office is lacking ADA accessibility components for providing barrier free access to the public. This project would provide for an ADA compliant ramp and door hardware at the main entrance to the building as well as remodeling of the existing restroom into a unisex ADA compliant facility and appropriate signage. This may include but is not limited to replacing all restroom fixtures, door and hardware, painting and installing fiberglass reinforced panels (FRP). The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 38500
0959EXT3 | WINDOW REPLACEMENT | 0959 | The windows are older, dual pane construction in a vinyl frame which are not energy efficient and are reaching the end of their expected life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 17 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
0650ENR1 | LIGHTING UPGRADE | 0650 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2375
0954EXT1 | DEMOLISH STRUCTURE | 0954 | The Incubator House contains numerous code and safety issues including but not limited to bat infestation, broken or missing electrical fixtures, dry rot and possible structural damage. The exterior metal panels have blown off in the wind and there has been no attempt to repair the building. This has exposed the substrate and framing members to the elements. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA INCUBATOR HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1968 | 512 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 5120
0957INT2 | KITCHEN REMODEL | 0957 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0957PLM1 | WATER HEATER REPLACEMENT | 0957 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0957EXT6 | WINDOW REPLACEMENT | 0957 | The windows are older, dual pane construction in a vinyl frame which are not energy efficient and are reaching the end of their expected life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 9 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0957INT1 | INTERIOR FINISHES | 0957 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0957EXT2 | EXTERIOR FINISHES | 0957 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0956PLM1 | WATER HEATER REPLACEMENT | 0956 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new 50 gallon propane-fired water heater be installed. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0956INT1 | INTERIOR FINISHES | 0956 | The interior finishes are in good condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
0956EXT1 | EXTERIOR FINISHES | 0956 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #1 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
0955PLM1 | WATER STORAGE TANK REPLACEMENT | 0955 | There is a 500 gallon water storage tank in the building. The average life span of a water storage tank is forty to fifty years. The tank was installed in 1965. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. This project would provide for a new water storage tank to be installed including connections to existing utilities. | MVWMA PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 200 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0650SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0650 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 3325
2981SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2981 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. NAC 477.917 states that: Existing buildings and structures: Additions, alterations and repairs. (NRS 477.030) 1. If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. 2. The State Fire Marshal will determine the value of the building or structure and the value of any additions, alterations and repairs. If the owner of the building disagrees with the value as determined by the State Fire Marshal, the owner of the building may engage a qualified and disinterested appraiser to ascertain the fair market value of the building or structure and the value of any additions, alterations and repairs. 3. As used in this section, “addition” means any extension or increase in the floor space or height of a building or structure. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project does not include a water storage tank for fire protection which may be required if existing water flows are not adequate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 6720
0959INT1 | INTERIOR FINISHES | 0959 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0955EXT2 | EXTERIOR FINISHES | 0955 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting, sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 200 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 600
0958PLM1 | WATER HEATER REPLACEMENT | 0958 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0958INT1 | INTERIOR FINISHES | 0958 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
0958EXT1 | EXTERIOR FINISHES | 0958 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA RESIDENCE #3 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7000
2473EXT1 | EXTERIOR FINISHES | 2473 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA NORTH PUMP HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1955 | 64 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 160
2980EXT1 | EXTERIOR / INTERIOR FINISHES | 2980 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA CXT RESTROOM | 9904 | Wildlife |  |  | Mason Valley | 1990 | 81 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 810
2981EXT1 | EXTERIOR FINISHES | 2981 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the painting, sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 1440
2981ENR1 | LIGHTING UPGRADE | 2981 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0960EXT1 | EXTERIOR FINISHES | 0960 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for painting and sealing of the interior and exterior of the structure. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA EQUIPMENT SHED | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1536 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 3072
2981EXT3 | WINDOW REPLACEMENT | 2981 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0650HVA1 | REPLACE EVAPORATIVE COOLER | 0650 | The roof mounted evaporative cooler has been leaking and is problematic due to it's age. This project would provide for a new evaporative cooler to be installed including removal of the existing cooler and connections to the existing utilities. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2983EXT1 | EXTERIOR FINISHES | 2983 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project also includes costs for installing a 3'x3' concrete landing at the door. | MVWMA FILTER HOUSE 1 | 9904 | Wildlife |  |  | Mason Valley | 0 | 63 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 500
2476EXT1 | DEMOLISH STRUCTURE | 2476 | The Barn/ Box Stalls building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA BARN/BOX STALLS | 9904 | Wildlife |  |  | Mason Valley | 0 | 1200 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2475EXT1 | DEMOLISH STRUCTURE | 2475 | The Residence 4 Storage Shed is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA RESIDENCE 4 STORAGE SHED | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1500 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 7500
2474EXT1 | DEMOLISH STRUCTURE | 2474 | The Old Goose Pens building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA OLD GOOSE PENS | 9904 | Wildlife |  |  | Mason Valley | 0 | 3000 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 15000
2472EXT1 | DEMOLISH STRUCTURE | 2472 | The Storage Shed - West is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA STORAGE SHED - WEST | 9904 | Wildlife |  |  | Mason Valley | 1955 | 960 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 4800
2471EXT1 | DEMOLISH STRUCTURE | 2471 | The Tack Shed/ Calf Barn is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA TACK SHED/CALF BARN | 9904 | Wildlife |  |  | Mason Valley | 1955 | 1015 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10150
0650INT2 | FLOORING REPLACEMENT | 0650 | The existing flooring is a mix of concrete and old vinyl composition tile (VCT) which is in extremely poor shape. This project would provide for new VCT to be installed throughout the building. Removal of the existing flooring is included in this estimate. This project should be implemented in the next two years. | MVWMA OFFICE/HEADQUARTERS | 9904 | Wildlife |  |  | Mason Valley | 1955 | 950 | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 7600
0653EXT1 | DEMOLISH STRUCTURE | 0653 | The Oil Storage building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. | MVWMA OIL STORAGE | 9904 | Wildlife |  |  | Mason Valley | 1955 | 144 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 720
0959EXT4 | ROOF REPLACEMENT | 0959 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next four to five years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Four to Ten Years | Long-Term Needs | 3 | 24000
2981EXT2 | EXTERIOR DOOR REPLACEMENT | 2981 | The existing exterior wood door is approaching the end of its expected life. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Also, a 3'x3'x4" thick concrete landing is included in this project. Removal and disposal of the existing door and painting of the new door is included in this estimate. | MVWMA MECHANICS SHOP | 9904 | Wildlife |  |  | Mason Valley | 0 | 480 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0957EXT1 | REPLACE ROOF | 0957 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0649EXT1 | EXTERIOR FINISHES | 0649 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete masonry, painting and caulking of the wood siding, windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painting and caulked in the next 3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MVWMA BROODER HOUSE | 9904 | Wildlife |  |  | Mason Valley | 1965 | 2880 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0957EXT4 | RESCREEN PATIO | 0957 | The screens on the patio are torn and damaged. They have reached the end of their expected life and should be scheduled for replacement. This project would replace the screens and the wood door to keep insects and other pests out of the patio. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0957EXT5 | INSTALL PLANTER | 0957 | The Residence has relatively new vinyl siding. Along the rear and west side of the residence, the lawn grows right up to the house making it difficult to mow without damaging the siding. Watering the lawn also wets the siding causing premature deterioration. This project would remove the lawn within three feet of the residence and install a planter with drip irrigation. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #2 | 9904 | Wildlife |  |  | Mason Valley | 1961 | 1400 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9904SIT1 | RELOCATE FIRE HOSE SHED | 9904 | Residence No. 3 has a shed housing a fire hose and valve for fire fighting. The shed is in disrepair and is isolated behind the residence in shrubs and is obstructed by equipment. This project would relocate the hose and valve to a cabinet in front of the residence in an accessible location. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9904PLM1 | INSTALL 2-STAGE PROPANE REGULATORS | 9904 | NFPA 58 requires 2-stage pressure regulators on all fixed piping propane installations. Existing installations on the three residences and at the Mechanic's Shop have single stage regulation. This project would install a second stage regulator and relocate the tank at the Mechanic's Shop for proper clearance. Additionally, the heater in the Mechanic's Shop is installed with a flexible gas line penetrating the heater metal cabinet. This is a Plumbing Code Violation. This project will install a solid pipe nipple to project beyond the heater case for connection. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 4000
0959PLM1 | LANDSCAPE IRRIGATION | 0959 | Current landscape maintenance practices use excessive amounts of water to maintain the lawn and planter areas. This project would install a landscape irrigation system with an electronic controller to reduce water usage and maintain the excellent condition of the landscaping. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MVWMA RESIDENCE #4 | 9904 | Wildlife |  |  | Mason Valley | 1969 | 1600 | 2019-06-26 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9904ENV1 | INSTALL CON-VAULTS AND CONCRETE FUELING APRON | 9904 | The existing fuel tanks are single wall steel supported on beams. The tanks and fueling dispensers have no effective secondary containment. This project would install a split tank or two separate Con-Vault tanks and dispensers along with a concrete fueling apron to prevent spills and contamination of the soil. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MASON VALLEY WMA SITE | 9904 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-26 | Immediate to Two Years | Currently Critical | 1 | 40000
1657ENR1 | LIGHTING UPGRADE | 1657 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade T-12 lamps to T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Any electrical wiring upgrades are not included in this estimate. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37138
1656ENR1 | LIGHTING UPGRADE | 1656 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30020
9905ENV1 | RESIDENCE SEPTIC TANK SYSTEM MAINTENANCE | 9905 | There are 5 residences each with a 500 gallon septic tank and associated leach fields. They are in need of pumping to maintain the integrity of the leach lines and fields. This project would provide for the pumping of all 5 tanks. It is recommended that this project be scheduled on a cyclical basis based on usage. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9905ELE2 | REPLACE HATCHERY WATER MANAGEMENT COMPUTER SYSTEM | 9905 | The computer and software system for the hatchery operations monitors every aspect of fish hatching and rearing including but not limited to water flows, temperature, raceway flows, and well water flows to the main hatchery. This equipment is dated and is in need of an upgrade. There is not a backup to the system and if it fails, there could be losses to fish hatching and rearing operations. This project would provide for a new computer and upgrade the software system for fish hatchery operations. The main computer is located in Hatchery Office / Shop. It is recommended that this equipment be replaced in the next two years. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1664EXT1 | EXTERIOR FINISHES | 1664 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1280
1664INT1 | INTERIOR FINISHES | 1664 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1664EXT2 | ROOF REPLACEMENT | 1664 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3840
1664ENR1 | LIGHTING UPGRADE | 1664 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE C2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
1665EXT1 | EXTERIOR FINISHES | 1665 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1280
1665INT1 | INTERIOR FINISHES | 1665 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1665EXT2 | ROOF REPLACEMENT | 1665 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3840
1657EXT2 | ROOF REPLACEMENT | 1657 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next two years to be consistent with the roofing program. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 222825
1666EXT4 | GUTTER INSTALLATION | 1666 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1657ADA1 | ADA SIGNAGE | 1657 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 900
1657INT1 | INTERIOR FINISHES | 1657 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 74275
1656INT3 | BREAK ROOM REMODEL | 1656 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1667EXT4 | GUTTER INSTALLATION | 1667 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1656PLM2 | WATER HEATER REPLACEMENT | 1656 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-10 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1656SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1656 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 5000
1656SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1656 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 42028
1656SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1656 | The building is partially a B occupancy per the 2006 IBC and has a floor area greater than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 84056
1656ADA1 | ADA SIGNAGE | 1656 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 1800
1669INT4 | KITCHEN REMODEL | 1669 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1656EXT2 | EXTERIOR FINISHES | 1656 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36024
1665ENR1 | LIGHTING UPGRADE | 1665 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE A1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 256 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1662INT1 | INTERIOR FINISHES | 1662 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 778
1663EXT2 | ROOF REPLACEMENT | 1663 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4665
1663INT1 | INTERIOR FINISHES | 1663 | The interior finishes are in fair condition. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 778
1663EXT1 | EXTERIOR FINISHES | 1663 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1555
1662ENR1 | LIGHTING UPGRADE | 1662 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1662EXT2 | ROOF REPLACEMENT | 1662 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 2-3 years to be consistent with the roofing program. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4665
2979EXT1 | EXTERIOR FINISHES | 2979 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing and painting of the exterior of the building. Included in the cost is sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY BULK FEED BIN | 9905 | Wildlife |  |  | Mason Valley | 1990 | 196 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 1960
2978EXT1 | EXTERIOR FINISHES | 2978 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing and painting of the exterior of the building. Included in the cost is sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY RACEWAY SHELTER | 9905 | Wildlife |  |  | Mason Valley | 1990 | 75600 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18900
2977EXT1 | EXTERIOR FINISHES | 2977 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HATCHERY WATER TANK | 9905 | Wildlife |  |  | Mason Valley | 1990 | 531 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 7500
2461EXT1 | EXTERIOR FINISHES | 2461 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY MOWER SHED | 9905 | Wildlife |  |  | Mason Valley | 0 | 200 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
2460EXT2 | ROOF REPLACEMENT | 2460 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | HATCHERY RESIDENCE 4 SHOP | 9905 | Wildlife |  |  | Mason Valley | 1991 | 480 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 7200
2978EXT2 | GUTTER INSTALLATION | 2978 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the rip-rap slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RACEWAY SHELTER | 9905 | Wildlife |  |  | Mason Valley | 1990 | 75600 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
1670INT4 | KITCHEN REMODEL | 1670 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1656ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1656 | The building has a woodshop area which does not have an adequate dust collection system. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project recommends installing a new dust collection system. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 20000
1662EXT1 | EXTERIOR FINISHES | 1662 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY WATER WELL PUMP HOUSE C1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1555
1661ENR1 | LIGHTING UPGRADE | 1661 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2900
1661HVA1 | HVAC EQUIPMENT REPLACEMENT | 1661 | The three HVAC roof top units and the ceiling mounted heater were installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34800
1661EXT2 | ROOF REPLACEMENT | 1661 | The roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. The current rolled asphalt roof was installed in 1990. It is recommended that this building be re-roofed with a single-ply roofing system in the next 1-2 years to be consistent with the roofing program. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 17400
1661INT1 | INTERIOR FINISHES / CEILING REPAIR | 1661 | The interior finishes are in fair condition except for the damaged gypsum board ceiling . This project would provide for the removal and replacement of the damaged ceiling areas and painting. It is recommended that the interior walls be cleaned and sealed and that the ceiling be painted at least once in the next two years after the repairs are made. Prior to painting, all surfaces should be repaired and prepped. The roof replacement project must be done prior to the repairing of the ceiling. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 5800
1661EXT1 | EXTERIOR FINISHES | 1661 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1660EXT1 | EXTERIOR FINISHES | 1660 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY HAZMAT STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 247 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 741
1659EXT1 | EXTERIOR FINISHES | 1659 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY VEHICLE STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 5063 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 7554
1658ENR1 | LIGHTING UPGRADE | 1658 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY DRY STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1323 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3308
1658EXT1 | EXTERIOR FINISHES | 1658 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations and painting of the overhead doors. It is recommended that the building be caulked and sealed and the doors be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY DRY STORAGE | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1323 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3969
1657HVA1 | CHILLER CONTROL PROGRAMMING | 1657 | The electronic controller for the chillers is not functioning. The controller needs to be re-programmed by a qualified professional in order to achieve the energy efficiency of the equipment as well as to ensure that the building is consistently conditioned as needed. This project would provide for reprogramming the chiller controls. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 10000
2460INT1 | INTERIOR FINISHES | 2460 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HATCHERY RESIDENCE 4 SHOP | 9905 | Wildlife |  |  | Mason Valley | 1991 | 480 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1663ENR1 | LIGHTING UPGRADE | 1663 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | HATCHERY WATER WELL PUMP HOUSE A2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 311 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1669PLM1 | WATER HEATER REPLACEMENT | 1669 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1656EXT4 | OVERHEAD DOOR MOTOR INSTALLATION | 1656 | There are three 14'x16' overhead coiling doors which are manually operated. This project would provide for the installation of motors for the doors including remote operation, safety controls and connection to existing utilities. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1667HVA1 | HVAC EQUIPMENT REPLACEMENT | 1667 | The HVAC system consists of a roof top evaporative cooler and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1668INT4 | KITCHEN REMODEL | 1668 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1669HVA1 | HVAC EQUIPMENT REPLACEMENT | 1669 | The HVAC system consists of a roof top evaporative cooler and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1668PLM1 | WATER HEATER REPLACEMENT | 1668 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
9905SIT3 | COOLING TOWER CONCRETE APRON REPAIR | 9905 | The cooling tower along the west side of the Hatchery building has a large sloped concrete apron which is showing signs of damage. There are cracks from settling and evidence of erosion occurring underneath the concrete. This may compromise the structural stability of the concrete foundation below the cooling tower. This project would provide for the necessary repairs to be made to prevent water infiltration and erosion. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1668HVA1 | HVAC EQUIPMENT REPLACEMENT | 1668 | The HVAC system consists of a roof top evaporative condenser and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1657EXT1 | EXTERIOR FINISHES | 1657 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 74275
1670HVA1 | HVAC EQUIPMENT REPLACEMENT | 1670 | The HVAC system consists of a roof top evaporative condenser and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1667INT4 | KITCHEN REMODEL | 1667 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1666INT4 | KITCHEN REMODEL | 1666 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 35000
1656ADA2 | RACEWAY ADA ACCESS PROGRAM ACCESSIBILITY | 1656 | The Hatchery Raceway is open to the public for viewing fish rearing activities. There is not any designated ADA access to this area. This project would provide for an ADA accessible location inside of the public area of this building for an audio / visual (A/V) presentation of hatchery and raceway areas which may not be ADA accessible. This project includes funds for an audio / visual consultant to outline and document hatchery raceway operations and purchase and installation on all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 20000
1670PLM1 | WATER HEATER REPLACEMENT | 1670 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
9905ENV2 | INSTALL FUEL STORAGE TANKS | 9905 | The existing fuel tank adjacent to the vehicle storage building is a single-wall elevated fuel tank with a containment base. This project would install a 1,000 gallon gasoline and a 2,000 gallon diesel "ConVault" above ground tank and dispenser including all wiring, piping, vents, and spill containment. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1666EXT5 | WINDOW REPLACEMENT | 1666 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1666PLM1 | WATER HEATER REPLACEMENT | 1666 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1667PLM1 | WATER HEATER REPLACEMENT | 1667 | There is a 50 gallon propane-fired water heater in the garage. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1668EXT4 | GUTTER INSTALLATION | 1668 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1669EXT4 | GUTTER INSTALLATION | 1669 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1670EXT4 | GUTTER INSTALLATION | 1670 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing erosion to the grade and damage to the siding. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1666HVA1 | HVAC EQUIPMENT REPLACEMENT | 1666 | The HVAC system consists of a roof top evaporative cooler and gas fired furnace in the garage. These units are original to the building, installed in 1990. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installing new HVAC units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29580
1667EXT5 | WINDOW REPLACEMENT | 1667 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1668EXT5 | WINDOW REPLACEMENT | 1668 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1667INT2 | RESTROOM REMODEL | 1667 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1669EXT5 | WINDOW REPLACEMENT | 1669 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1670EXT5 | WINDOW REPLACEMENT | 1670 | The windows are original, dual pane construction in a metal frame. These older windows are not energy efficient and many have broken seals. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1666INT2 | RESTROOM REMODEL | 1666 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1668INT2 | RESTROOM REMODEL | 1668 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1669INT2 | RESTROOM REMODEL | 1669 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1670INT2 | RESTROOM REMODEL | 1670 | The two restrooms in the residence are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2460EXT1 | EXTERIOR FINISHES | 2460 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 SHOP | 9905 | Wildlife |  |  | Mason Valley | 1991 | 480 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1667INT1 | INTERIOR FINISHES | 1667 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1669EXT2 | REPLACE ROOF | 1669 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1667EXT1 | EXTERIOR FINISHES | 1667 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1670EXT1 | EXTERIOR FINISHES | 1670 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1670EXT2 | REPLACE ROOF | 1670 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
9905SIT2 | REMOVE & REPLACE,CRACK FILL AND SLURRY SEAL ASPHALT PAVEMENT | 9905 | There is approximately 327,150 Square feet of asphalt paving on the site. There are numerous areas that are damaged and the entire paved area is in need of a slurry seal. This project would provide for the removal and replacement of 260,550 square feet of pavement and crack fill and slurry sealing of 66,600 square feet of existing paving to remain. Striping is included in this estimate. Slurry sealing of the entire paved area is also recommended on a 5-7 year cycle to maintain the integrity of the paving on site. For budgeting purposes, a construction cost figure of 50 cents a square foot could be used for slurry sealing which is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/07/2009. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 817875
1668INT1 | INTERIOR FINISHES | 1668 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1669INT1 | INTERIOR FINISHES | 1669 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1670INT1 | INTERIOR FINISHES | 1670 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1667INT3 | REPLACE FLOOR COVERING | 1667 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1668INT3 | REPLACE FLOOR COVERING | 1668 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1669INT3 | REPLACE FLOOR COVERING | 1669 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1670INT3 | REPLACE FLOOR COVERING | 1670 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1667EXT2 | REPLACE ROOF | 1667 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1668EXT2 | REPLACE ROOF | 1668 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1669EXT1 | EXTERIOR FINISHES | 1669 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1656EXT1 | REPLACE GUTTER | 1656 | The existing gutter on the shop eve has numerous joints that have proven impossible to seal against leaks. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with seamless gutter. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 6800
1657ELE1 | INSTALL ELECTRIC WATER HEATER | 1657 | The existing propane-fired water heater is permanently installed in the same room as the chillers. 2006 IMC 1106.2 prohibits open flame-producing devices in refrigeration rooms. This project would replace the existing gas fired equipment with electric equipment. | HATCHERY BUILDING | 9905 | Wildlife |  |  | Mason Valley | 1990 | 14855 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 1500
9905ENR2 | ENERGY SAVINGS PERFORMANCE CONTRACT | 9905 | This project would invite an Energy Services Company (ESCO) to provide an analysis of energy and water savings opportunities at the Hatchery site. The ESCO could then enter into an Energy Savings Performance Contract with the Department of Wildlife to implement approved energy savings projects. Monetary savings from the projects would be used in whole or in part to pay the ESCO services. Among the opportunities that exist are lighting retrofits, the use of water or ground source heat pumps or heat exchangers, and the use of overhead low intensity radiant heating in shop areas. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
1668EXT1 | EXTERIOR FINISHES | 1668 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1670EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1670 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 5 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1656ELE1 | INCREASE PHONE CAPACITY AND ADD VOICE MAIL | 1656 | The existing phone switch is inadequate for the needs of the staff and currently does not offer voice mail. It is recommended that the switch be upgraded to add a voice mail module and ten new phone lines. To facilitate real time vendor access to the SCADA system and provide State employees with responsive access to email and data, the site should be provided with a high-speed internet connection as well. High-speed internet access costs are not included in the estimated costs for upgrading the phone switch. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Four to Ten Years | Long-Term Needs | 3 | 10000
1656INT1 | REPLACE CARPET AND TILE | 1656 | The carpet and VCT (vinyl composite tile) flooring in the Office is damaged and reaching the end of its useful life. It is recommended that the carpet and VCT flooring be replaced. This project would provide for removal and disposal of the carpet and VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
9905ELE1 | RELOCATE RESIDENCE AREA PHONE VAULT | 9905 | The phone system in the housing area is subject to frequent outages due to lighting strikes. In addition, the main junction box is in a below ground vault, which subjects the terminations to corrosion due to ground moisture reducing the quality of service. This project would relocate the junction box to an above ground location and install lightning protection. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | MASON VALLEY HATCHERY SITE | 9905 | Wildlife |  |  | Mason Valley | 0 |  | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1661ENV1 | REPLACE UNDERGROUND TANK | 1661 | The site emergency generators are served by a 1,000 gallon Fiberglas/steel underground fuel tank located between the well house and the above ground water tank. At the time of the previous site visit, the leak detection monitor was in alarm. This project would replace the existing tank with a 1,000 gallon above ground "ConVault" to serve the generators. The underground tank would be investigated for leakage and closed if none is found. This project does not include funds for site remediation. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY PUMP HOUSE B | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1160 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1666EXT1 | EXTERIOR FINISHES | 1666 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19720
1666EXT2 | REPLACE ROOF | 1666 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Immediate to Two Years | Currently Critical | 1 | 29580
1666INT1 | INTERIOR FINISHES | 1666 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9860
1666EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1666 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1666INT3 | REPLACE FLOOR COVERING | 1666 | The carpet and vinyl flooring in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new carpet and vinyl flooring. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 1 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15776
1667EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1667 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 2 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1668EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1668 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 3 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1669EXT3 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 1669 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. Backflow prevention devices would be enclosed in a heated enclosure to prevent freezing. Existing hose bibs upstream of the backflow preventers would be relocated downstream of the valve. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY RESIDENCE 4 | 9905 | Wildlife |  |  | Mason Valley | 1990 | 1972 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1656INT2 | INTERIOR FINISHES | 1656 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/09/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2009. | HATCHERY OFFICE/SHOP | 9905 | Wildlife |  |  | Mason Valley | 1990 | 12008 | 2019-06-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
9906SIT5 | CRACK FILL & SLURRY SEAL ASPHALT PAVING | 9906 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the CDL course. Striping is included in this estimate. This project should be scheduled on a 4-5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 120,880 square feet of asphalt area and 1,500 lineal feet of crack fill was used to generate this estimate. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75528
9906SIT4 | SITE DRAINAGE ASSESSMENT | 9906 | The site has a drainage problem on the east side between the Office Building Addition (East Wing) and the DMV Warehouse where grade does not properly slope away from the buildings. The rain accumulates in several areas adjacent to the building creating a water problem which may infiltrate the interior during inclement weather. This standing water also causes premature deterioration of the paving and other landscape improvements. This project would provide for a site survey and drainage report to be completed by a licensed professional to determine what measures should be taken to prevent future flooding. Future projects may arise from the results of this report. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 3000
2459INT2 | REPLACE VCT FLOORING | 2459 | The VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | LARGE VEHICLE SCALE BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 1981 | 160 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
2459INT1 | INTERIOR FINISHES | 2459 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. | LARGE VEHICLE SCALE BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 1981 | 160 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1990ADA1 | ADA RESTROOM MODIFICATIONS | 1990 | The ADA designated Men's and Women's restrooms on the lower level are not compliant. This project would provide for a new toilet and sink, horizontal and vertical grab bars and lever action door hardware. The partition located in front of the doors will need to be removed to provide for proper forward approach and is included in this estimate. The signage will need to be relocated. The 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG) was referenced for this project. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 12000
2459ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2459 | There is an electrical transformer located inside the building on the floor. The transformer was damaged in 2006 when the building flooded and does not function properly now. This project recommends replacing the transformer with a new 15 kVA power transformer. | LARGE VEHICLE SCALE BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 1981 | 160 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 3000
1990INT1 | INTERIOR FINISHES | 1990 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the offices and Mail Room be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. 2,500 square feet was used to generate this estimate. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2459EXT2 | EXTERIOR FINISHES | 2459 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing, tuck pointing the brick masonry and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | LARGE VEHICLE SCALE BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 1981 | 160 | 2009-01-14 | Four to Ten Years | Long-Term Needs | 3 | 2000
9906SIT6 | REPLACE VEHICLE SCALE | 9906 | The vehicle scale is damaged and does not always function properly. The scale platform is showing signs of wear including cracked concrete, broken welds and general instability. The steel framework for the scale is severely corroded due to flooding / moisture infiltration and clogged drains. The scale is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the existing vehicle scale and replacement with a new scale. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2037STR1 | RAISED FLOOR MODIFICATIONS | 2037 | The raised floor in the server room does not appear to have sufficient structural support for the equipment it is carrying. Global Risk Consultants, the State's insurance underwriter also has indicated that the floor does not have adequate seismic and structural support for the equipment. This project would provide for the attachment of the floor to the concrete slab -on-grade and evaluation by qualified individual for seismic loading. Replacement of the floor with a new code compliant raised flooring system may be an option, but is not included in this cost estimate. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 3000
2037SEC1 | EXTERIOR DOOR MODIFICATIONS | 2037 | The exterior metal exit door on the west side of the building does not function properly. The direct sun exposure in the afternoon causes the door to swell significantly. The locking mechanism then becomes jammed and does not hold the door closed properly. As this is a secured facility, it is imperative that all access into the building is controlled as well as meeting required building code exiting compliance. This project would provide for the construction of an interior vestibule with a new interior door for security. The proposed project should not require and structural modifications. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 15000
0210SIT1 | STAIR REPLACEMENT | 0210 | The exterior stairs on the south side of the breezeway are damaged and should be scheduled for replacement. The drainage problems in this area have caused corrosion of the concrete stairs and the metal handrails. This project would provide for replacement of the stairs and handrails in accordance with IBC 2006 Section 1009. Removal and disposal of the existing stairs is included in the estimate. The drainage problem will be addressed on the site report and the two projects should be implemented concurrently. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
1990ENR1 | LIGHTING UPGRADE | 1990 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade T-12 lamps to T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Any electrical wiring upgrades are not included in this estimate. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50250
1990EXT1 | LOADING DOCK UPGRADES | 1990 | There are two 8'x10' power-operated overhead coiling doors for the loading dock which are damaged and do not function properly. The loading dock lift is also not functioning properly and has reached the end of its useful life. The doors and the lift are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the doors and the lift and replacement with new power-operated overhead coiling doors and a new hydraulic lift. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2965EXT1 | EXTERIOR FINISHES | 2965 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for painting of the structural steel members and repairing broken welds as well as tuck pointing and sealing the brick masonry as needed. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9906 | MtrVeh | B&G |  | Carson City | 0 | 560 | 2009-01-14 | Four to Ten Years | Long-Term Needs | 3 | 1680
0210INT1 | INTERIOR FINISHES | 0210 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 3 to 4 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 255000
0210INT2 | REPLACE CARPET AND FLOORING | 0210 | The carpet and VCT (vinyl composite tile) flooring in the building are showing signs of wear. It is recommended that the flooring be replaced in the next four to five years. This project would provide for removal and disposal of the existing carpet and VCT and installation of new heavy duty commercial grade carpet and 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2009-01-14 | Four to Ten Years | Long-Term Needs | 3 | 408000
0210EXT3 | REPLACE ROOF | 0210 | The roof on this building was in poor condition at the time of the survey. This existing roof was installed around 1994. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed within the next one to two years to be consistent with the roofing program and the end of the warranty period. 25,500 square feet was used to generate this estimate. The penthouse roof is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 382500
0210SFT2 | PENTHOUSE STAIRS HANDRAIL INSTALLATION | 0210 | There is a set of stairs in the penthouse which provide access to the roof. It is missing handrails. This project would provide for the installation of handrails in accordance with the 2006 IBC Chapter 10, Section 1009. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 1000
1990SFT2 | FIRE SPRINKLER PIPE SUPPORT | 1990 | The fire sprinkler piping in the breezeway connecting the Warehouse to the upper level of the East Wing is supported off of a sprinkler pipe above. The building code does not allow for piping to be supported by other piping as it may damage the pipe and fitting above. This project would provide for proper structural support of the sprinkler pipe. This issue was noted in the State's insurance underwriter loss prevention report prepared by Global Risk Consultants dated 9 & 10 October 2008. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 500
9906SIT3 | TREE AND SHRUB PRUNING / REMOVAL | 9906 | Trees and shrubs on the site have grown to the extent that they are obstructing access to gas meters, electrical transformers, water valves, and in at least one case obscure a security camera's view. This project would trim, prune or remove the plants to allow access to building equipment and improve the site security. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9906ENV1 | DIESEL STORAGE TANK FILL CONCRETE PAD | 9906 | The existing fuel tank for the emergency generators has a fill pipe located in a river-rock landscaped area. This area is difficult to walk on and would not contain any spill during filling. This project would install a concrete slab around the tank fill and manway to prevent soil contamination and make it easier on maintenance and operations personnel to access the tank. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 1000
9906SIT2 | INSTALL SUMP PUMP IN COMMUNICATIONS VAULT | 9906 | The communications vault on the south side of the Computer Facility fills with water during heavy precipitation events. This project will install a sump and pump to remove the water and prevent damage to communications cables and duct banks. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV/PUBLIC SAFETY SITE | 9906 | MtrVeh | B&G |  | Carson City | 0 |  | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 2500
2037INT3 | REPLACE ROOF | 2037 | The single-ply roof on this building was in fair to condition at the time of the survey. This existing roof was installed in 1995. The statewide roofing program estimates the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. This building should be re-roofed in the next one to two years, consistent with the roofing program guidelines and the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 153825
0210EXT1 | EXTERIOR FINISHES | 0210 | It is important to maintain the finish, weather resistance and appearance of the building. This project includes items to protect the exterior building envelope other than the roof, including sealing and tuck pointing the masonry, painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure.. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2009-01-14 | Four to Ten Years | Long-Term Needs | 3 | 510000
2037INT2 | REPLACE CARPET | 2037 | The carpet is showing signs of wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. Removal and disposal of the existing carpet is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 59500
0210EXT2 | WINDOW REPLACEMENT | 0210 | The windows are original dual pane construction in an aluminum frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with new energy efficiency units which will match the new windows in the west wing. This estimate is for the replacement of 95 units. Removal and disposal of the existing windows is included in this estimate. | DMV OFFICE BUILDING ADDITION (EAST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1980 | 56688 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 95000
2037EXT2 | EXTERIOR FINISHES | 2037 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and tuck pointing the masonry, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51275
2037INT1 | INTERIOR FINISHES | 2037 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV COMPUTER FACILITY | 9906 | MtrVeh | B&G |  | Carson City | 1998 | 10255 | 2009-01-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51275
1990SFT1 | SEISMIC BRACING | 1990 | Current building codes and the State's Underwriter require non-structural equipment and fixtures to be braced against earthquakes. The building currently has several unit heaters, gas piping and storage racks that are not properly braced per seismic codes. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 5000
1990EXT3 | EXTERIOR FINISHES | 1990 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and tuck pointing the masonry, painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Four to Ten Years | Long-Term Needs | 3 | 83750
1990EXT2 | REPLACE ROOF | 1990 | The single-ply roof on this building was in fair condition at the time of the survey. This existing roof was installed in 1991. The statewide roofing program estimates the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. This building should be re-roofed in the next year, consistent with the roofing program guidelines and the warranty period. The connecting breezeway built-up roof is also included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 1/14/2009. | DMV WAREHOUSE | 9906 | MtrVeh | B&G |  | Carson City | 1991 | 16750 | 2009-01-14 | Immediate to Two Years | Currently Critical | 1 | 216750
0209EXT3 | REPAIR CONCRETE FASCIA | 0209 | There is a concrete fascia along the south and east sides of the building which are damaged. Reinforcing steel is exposed. This project would provide for the repair of the concrete fascia including painting and / or sealing as needed. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Immediate to Two Years | Currently Critical | 1 | 2000
0209ADA1 | ADA CANE DETECTION BARRIER INSTALLATION | 0209 | The stairwell in the atrium has an overhead hazard at the cane detection area under the stairs. This project recommends the installation of a permanent barrier under the stairs. IBC - 2006 Section 1012 and ADAAG 4.4.2 were referenced for this project. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Immediate to Two Years | Currently Critical | 1 | 1000
0209ENR2 | ATRIUM WINDOW / DOOR REPLACEMENT | 0209 | The window and storefront door systems in the courtyard are original, single pane construction in a hollow metal frame. These older windows and doors are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units and new aluminum storefront door systems. The new windows should match the windows that were recently installed around the perimeter of the building. This estimate is for the replacement of 44 window units and 4 storefront door systems. Removal and disposal of the existing windows is included in this estimate. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62400
0209SFT3 | ELECTRICAL SWITCHGEAR / TRANSFORMER MAINTENANCE | 0209 | The electrical switchgear and transformers appear to be more than 40 years old. This project would provide for an infrared thermography inspection to be done on all of the electrical equipment including switchgear, transformers and subpanels. This would determine the condition of the building's electrical system and it's condition. This project is for an inspection only and does not include equipment upgrades or replacement. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Immediate to Two Years | Currently Critical | 1 | 10000
0209EXT1 | EXTERIOR FINISHES | 0209 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting, staining, or other applied finishes, sealing and tuck pointing the masonry, minor concrete patching and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/12/2009. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 315000
0209PLM1 | ATRIUM FLOOR DRAIN CLEANING | 0209 | There are two floor drains in the atrium. One of them was completely covered with debris. This project would provide for the cleaning and testing of the drains to ensure proper drainage. The clogged drains could cause flooding of the building. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Immediate to Two Years | Currently Critical | 1 | 500
0209SFT2 | ONE-HOUR FIRE RATED WALL INSTALLATION | 0209 | The wall between the boiler room and the interior exit stairwell is required to be a one-hour fire rated assembly per 2006 IBC Table 508.2 and 1020. The drywall is missing on the interior of the boiler room and there are several penetrations lacking firestopping. This project would provide for the installation of a 1-hour fire rated assembly to be installed in accordance with IBC Section 706 and 1020. Firestopping of all penetrations is included in this estimate. It is recommended that this project be reviewed by the State Public Works Board Building Department. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Immediate to Two Years | Currently Critical | 1 | 7000
0209INT2 | REPLACE CARPET | 0209 | The carpet is showing signs of wear and tear. It is expected that the carpet will require replacement within the next five years. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next four to five years. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Four to Ten Years | Long-Term Needs | 3 | 220500
0209INT1 | INTERIOR FINISHES | 0209 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/12/2009. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 157500
0209EXT4 | ATRIUM STUCCO REPAIR | 0209 | The Atrium exterior stucco finish has numerous areas that appear to be cracking. There is evidence of water infiltration on the south side of the building in the interior. This project would provide for the repair of the stucco finish including elastomeric painting of the repair areas. This project should be coordinated with the window replacement project. | DMV OFFICE BUILDING (WEST WING) | 9906 | MtrVeh | B&G |  | Carson City | 1965 | 31500 | 2009-03-12 | Immediate to Two Years | Currently Critical | 1 | 1000
2027INT3 | INTERIOR FINISHES | 2027 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42500
2944EXT1 | INTERIOR / EXTERIOR FINISHES / GLAZING MAINTENANCE | 2944 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building excluding the roof. Included in the cost are painting of the exposed steel structure, caulking of the glazing panels and annual cleaning of the glazing panels inside and out. It is recommended that these items be assessed on an annual basis and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DEMA GUINN CONCOURSE | 9907 | CultAffr | M&H | Museums | Carson City | 2008 | 3949 | 2015-02-11 | Immediate to Two Years | Currently Critical | 1 | 39490
2027EXT1 | EXTERIOR FINISHES | 2027 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42500
2027HVA2 | REPLACE HVAC SYSTEM | 2027 | The existing roof mounted HVAC unit was installed in 1999 and will be reaching the end of it's expected life within the next 7-8 years. This project would provide for a new roof mounted package HVAC unit to be installed including all required connections to existing utilities and ducting. Removal and disposal or the existing unit is included in this estimate. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Four to Ten Years | Long-Term Needs | 3 | 75000
0205INT8 | REMODEL UPPER LEVEL & BASEMENT RESTROOMS | 0205 | The existing Men's and Women's restrooms are in need of remodeling due to age and use. This project would provide for the remodeling of two Men's and two Women's restrooms in the basement and upper level including but not limited to new plumbing fixtures partitions, accessories, flooring and painting. If space permits, ADA accessible elements should be incorporated into the design as much as feasible but the main level of the museum does have ADA accessible Men's and Women's restrooms for the public and employees. It is recommended that ADA directional signage be installed to provide location details to ADA accessible restrooms. | NEVADA STATE MUSEUM | 9907 | CultAffr | M&H | Museums | Carson City | 1871 | 45763 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0205HVA3 | HVAC SYSTEM REPLACEMENT | 0205 | The existing HVAC system components have or are close to reaching the end of their expected life. The gas fired boiler is about 25 years old as well as the 33 fan coil units. The roof mounted chiller is over ten years old and all of this equipment is not energy efficient. This project would provide for the installation of a new gas fired boiler, and 33 fan coil units as well as a new energy management system including controls and VFD's. Some modifications to the ducting system in the basement area are included in this estimate. | NEVADA STATE MUSEUM | 9907 | CultAffr | M&H | Museums | Carson City | 1871 | 45763 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 443370
0205INT6 | REPLACE CARPET TILES | 0205 | The existing carpet tiles on the upper level are worn and are in need of replacement. This project would provide for the installation of new commercial grade carpet tiles at the upper level of the museum. Removal and disposal of the existing carpet is included in this estimate. A total of 3,000 square feet was used for this estimate. | NEVADA STATE MUSEUM | 9907 | CultAffr | M&H | Museums | Carson City | 1871 | 45763 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0205INT5 | INTERIOR FINISHES | 0205 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE MUSEUM | 9907 | CultAffr | M&H | Museums | Carson City | 1871 | 45763 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 221865
0205EXT2 | EXTERIOR FINISHES | 0205 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and pointing the sandstone masonry as needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE MUSEUM | 9907 | CultAffr | M&H | Museums | Carson City | 1871 | 45763 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 310359
9907SIT3 | CRACK FILL / SEAL ASPHALT PAVING | 9907 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 4 year cyclical basis to maintain the integrity of the paving and prevent premature failure. | NEVADA STATE MUSEUM COMPLEX - CC | 9907 | CultAffr | M&H | Museums | Carson City | 1871 |  | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5136
0205INT7 | JANITOR CLOSET FRP INSTALLATION | 0205 | There are three janitor closets with floor sinks with a gypsum board surround that is damaged by moisture. This project would provide for the installation of a fiberglass reinforced panel (FRP) on the walls adjacent to the floor / mop sinks. | NEVADA STATE MUSEUM | 9907 | CultAffr | M&H | Museums | Carson City | 1871 | 45763 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
2027INT5 | REMODEL UPPER LEVEL RESTROOMS | 2027 | The existing upper level Men's and Women's restrooms are showing their age and are in need of an upgrade. This project would provide for new fixtures and finishes to be installed including toilets, sinks faucets, toilet partitions and countertops. The existing tile cold remain but it is recommended that the existing tile be removed and replaced with new floor and wall tile. Removal and disposal of the existing fixtures is included in this estimate. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Four to Ten Years | Long-Term Needs | 3 | 40000
2027EXT3 | ROOF REPLACEMENT | 2027 | The roof on this building was in fair at the time of the survey (Feb. 2015). The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of a 15 year time period for this installation. It is recommended that this building be scheduled for re-roofing in the next 4 years to be consistent with the newer roofing program and the end of the warranty period. This project or a portion there of was previously recommended in the FCA report dated 04/30/2004 and 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Four to Ten Years | Long-Term Needs | 3 | 42500
2027INT0 | REPLACE RESTROOM FLOORING | 2027 | The existing flooring in the lower level ADA accessible restrooms is vinyl composition tile (VCT). This creates a potential unsanitary condition and increases maintenance and also is showing signs of wear. This project would provide for removal of the existing VCT and installation of a slip resistant sheet vinyl. This project or a portion there of was previously recommended in the FCA report dated 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
2027INT2 | CARPET REPLACEMENT | 2027 | The interior carpet floor covering on the lower level and upper level is showing signs of wear. Several areas are worn, tears are evident, and it has reached the end of it's expected life. This project would replace the existing broad loom carpet with carpet tile. Carpet tile would allow for future replacement of only those sections of carpet that are worn or damaged without the need to remove the entire carpet. This project or a portion there of was previously recommended in the FCA report dated 04/30/2004 and 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2027ADA3 | ADA ACCESSIBLE COUNTERTOP REPLACEMENT | 2027 | The plastic laminate base cabinet, countertop and sink in the docent lounge does not meet the ADA requirements. It is currently 36" above the finish floor and is not accessible. This room is used by a variety of people and should have barrier free access to the room and it's amenities. This project addresses removal and replacement of the plastic laminate base cabinet, countertop and sink to bring them into compliance with the NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design which were used for reference on this project. The project includes the removal of the of the base cabinet, countertop and sink, and installation of a new plastic laminate cabinet system and sink. The cabinet should be sized accordingly to provide 18" of clearance between the cabinet and the exit door pull handle. Minor gypsum board repair and painting is included in this estimate. This project or a portion there of was previously recommended in the FCA report dated 6/6/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/11/2015. | NEVADA STATE MUSEUM - NORTH ANNEX | 9907 | CultAffr | M&H | Museums | Carson City | 1955 | 8500 | 2015-02-11 | Immediate to Two Years | Currently Critical | 1 | 5000
2428ELE1 | CLOTHES DRYER REPLACEMENT | 2428 | The two commercial tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the existing tumbler dryers and replacement with two new units. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2428ADA1 | ADA SIGNAGE | 2428 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 3750
9908SIT1 | DRY WELL INSTALLATION | 9908 | West of the Administration building, storm water runoff does not drain properly and pools up next to the curb and sidewalk. It is recommended to install a dry well to collect and dispose of the water. This project provides for installing a concrete dry well with a silt basin on the west side of the Administration building to mitigate the drainage problem. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2428EXT3 | EXTERIOR FINISHES | 2428 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 138910
2428INT2 | INTERIOR FINISHES | 2428 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 6-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 138910
2432ENR1 | HVAC REPLACEMENT | 2432 | The existing HVAC system consists of ceiling mounted natural gas fired heaters and wall mounted evaporative coolers. The system is inefficient, does not provide enough heating or cooling and should be scheduled for replacement. This project would provide for replacing the existing system. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
2428ENR1 | HVAC EQUIPMENT REPLACEMENT | 2428 | The HVAC system was installed in 2000 and is original to the building. It consists of 21 rooftop packaged units with natural gas-fired furnaces and air conditioners utilizing R-22 coolant. The system is not energy efficient and has reached the end of its expected and useful life. The R-22 coolant is no longer allowable for cooling. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 416830
9908ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9908 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. Currently, the path of travel from the entrance gate to the entrance door of the Administration building exceeds 5% in several places and does not have a compliant landing at the door. A compliant path of travel is necessary to comply with ADA accessibility requirements. This will require removing the existing concrete walkway, regrading, placement of P.C. concrete, signage, and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 700 square feet of concrete was used for this estimate. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 12500
2428ADA2 | ADA DINING UPGRADE | 2428 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are two small dining rooms in the building for the residents. The tables in the dining rooms do not provide an accessible place to sit. This project would provide for installing an accessible dining seat in each of the two dining rooms. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 2500
9908ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9908 | The existing site lighting is over 13 years old and the equipment is beginning to fail. A common problem that would need to be addressed is wires fraying and shorting out due to age and rubbing against the inside of the poles. This project would provide for the installation of 25 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles may be acceptable to re-use. If so, the estimate can be reduced accordingly. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 162500
2428EXT4 | ROOF REPLACEMENT | 2428 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 333384
2428INT3 | FLOORING REPLACEMENT | 2428 | The VCT (vinyl composite tile) and carpet in the building are in fair condition. It is recommended that the flooring is scheduled for replacement. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 7-8 years. | ADMINISTRATION & EDUCATION | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 27782 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 104000
2429EXT2 | EXTERIOR FINISHES | 2429 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 75500
2429INT2 | INTERIOR FINISHES | 2429 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 6-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 75500
2429ENR1 | HVAC REPLACEMENT | 2429 | The six HVAC roof top units were installed in 2000. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for purchasing and installing six new HVAC packaged units and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 226500
9908ADA1 | ADA PARKING SIGNS | 9908 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The parking signage does not comply with this criteria and there is no directional signage to the building entrance. This project would provide funding for purchase and installation of ADA signage including new parking signs and directional signage from parking to accessible building entrances. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Immediate to Two Years | Currently Critical | 1 | 2500
2432SIT1 | DOCK LIFT REPLACEMENT | 2432 | The 10,000 pound capacity scissor dock lift is damaged from age and general wear and tear and has reached the end of its expected life. Staff reported that the lift has not been operable in over 7 years and that additional fees are added to deliveries to compensate for the lack of a dock lift. This project would provide for the replacement of the lift with a new dock lift for deliveries. Removal and disposal of the existing lift is included in this estimate. It may be possible to repair the existing lift or replace parts on the existing lift to save costs. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2430SEC3 | DOORS, LOCKS AND MECHANISMS REPLACEMENT | 2430 | Housing Unit #2 was constructed in 2000. The sleeping room doors, controls, locks and mechanisms are original to the building and have been problematic due to wear and tear, abuse and age. This project would provide for installing new sleeping room doors, locks and mechanisms. A total of 48 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2430INT1 | INTERIOR FINISHES | 2430 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75500
2429EXT3 | ROOF REPLACEMENT | 2429 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 181200
2429PLM1 | WATER HEATER REPLACEMENT | 2429 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2429SEC3 | DOORS, LOCKS AND MECHANISMS REPLACEMENT | 2429 | Housing Unit #1 was constructed in 2000. The sleeping room doors, controls, locks and mechanisms are original to the building and have been problematic due to wear and tear, abuse and age. This project would provide for installing new sleeping room doors, locks and mechanisms. A total of 48 doors was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 - SIERRA | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2430EXT2 | EXTERIOR FINISHES | 2430 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 75500
2430ENR1 | HVAC REPLACEMENT | 2430 | The six HVAC roof top units were installed in 2000. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for purchasing and installing six new HVAC packaged units and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 226500
9908SEC1 | PERIMETER FENCE REPAIRS | 9908 | The chain link perimeter fence currently has an anti-climb mesh attached to it. The anti-climb mesh is not strong enough for this application and is due for replacement. Staff reported that the wind blows it off of the fence and that a heavier material would be more secure. This project would provide for removing the existing anti-climb mesh and replacing it with a heavier material with stronger attachments. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2430PLM1 | WATER HEATER REPLACEMENT | 2430 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9908SIT3 | SLURRY SEAL ASPHALT PAVING | 9908 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 65,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | SUMMIT VIEW YOUTH CORRECTIONAL CENTER | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 |  | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48750
2431EXT2 | EXTERIOR FINISHES | 2431 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the metal trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 7-8 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | GYMNASIUM | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 7773 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 39865
2431INT1 | INTERIOR FINISHES | 2431 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GYMNASIUM | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 7773 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 39865
2431ENR1 | HVAC REPLACEMENT | 2431 | The existing HVAC system consists of ceiling mounted natural gas fired heaters and wall mounted evaporative coolers. The system is inefficient, does not provide enough heating or cooling and should be scheduled for replacement. This project would provide for replacing the existing system. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | GYMNASIUM | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 7773 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 47838
2432EXT2 | EXTERIOR FINISHES | 2432 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
2432INT2 | INTERIOR FINISHES | 2432 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/08/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 01/28/2014. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
2432EXT3 | OVERHEAD DOOR REPAIRS | 2432 | The (2) 10'x10' overhead doors are showing signs of wear and tear and are due for maintenance. The cables are fraying and the pulleys and other hardware are worn. This project would provide for the inspection and maintenance of the doors including replacing the springs, cables and rollers, greasing the hardware and replacing any other parts as necessary. | WAREHOUSE/MAINTENANCE SHOP | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 3750 | 2014-01-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2430EXT3 | ROOF REPLACEMENT | 2430 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #2 - EVEREST | 9908 | HHS | DCFS | SVYCC | North Las Vegas | 2000 | 10454 | 2014-01-28 | Four to Ten Years | Long-Term Needs | 3 | 181200
2445PLM1 | WATER HEATER REPLACEMENT | 2445 | There is a 10 gallon natural gas fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new natural gas fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Four to Ten Years | Long-Term Needs | 3 | 1000
2444PLM1 | WATER HEATER REPLACEMENT | 2444 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Four to Ten Years | Long-Term Needs | 3 | 1000
2444INT1 | INTERIOR FINISHES | 2444 | The interior finishes are in fair condition. It is recommended that the interior painted gypsum board walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
9909ADA1 | ADA SIGNAGE UPGRADES - NDOW | 9909 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area in front of the NDOW Office are missing proper signage in accordance with ADA requirements. This project would provide for purchasing and installing a "NO PARKING" sign at the loading zone next to the accessible parking space and replacing the ADA parking sign with a current sign indicating a fine of $250-$1000. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | WINNEMUCCA SITE | 9909 | Wildlife |  |  | Winnemucca | 0 |  | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 1000
2444INT2 | FLOORING REPLACEMENT | 2444 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
2444ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2444 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 4000
2444ADA4 | ADA SIGNAGE | 2444 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 600
2444ENR1 | LIGHTING UPGRADE | 2444 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2160
2444SFT1 | GFCI DUPLEX OUTLET REPLACEMENT | 2444 | The outlet in the restroom is not GFCI. This outlet should be changed to a GFCI type outlet per the NEC. This project would provide for the purchase and installation of a GFCI duplex outlet for the restroom. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 300
2444SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2444 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 1000
2446EXT2 | ROOF REPLACEMENT | 2446 | The corrugated metal roof on this building was in poor condition at the time of the survey and staff reported that there are active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | NDOW GAS STORAGE | 9909 | Wildlife |  |  | Winnemucca | 0 | 512 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 5120
2444HVA1 | HVAC EQUIPMENT REPLACEMENT | 2444 | The packaged HVAC unit is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of a new HVAC packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2446EXT1 | EXTERIOR FINISHES | 2446 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW GAS STORAGE | 9909 | Wildlife |  |  | Winnemucca | 0 | 512 | 2011-05-11 | Four to Ten Years | Long-Term Needs | 3 | 2560
2444SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2444 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 4000
2445SIT1 | CONCRETE REPAIRS | 2445 | The concrete aprons and sidewalks around the building are deteriorated and failing in several areas. Cracks wider than two inches have been identified, and there is settling in many locations. This project addresses removal and replacement of existing sidewalks and repairing the concrete aprons as needed. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2445EXT1 | EXTERIOR FINISHES | 2445 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1260
2445EXT2 | EXTERIOR DOOR REPAIRS | 2445 | The two exterior metal man doors are damaged from age and general wear and tear and due for repairs. This project would provide for painting the doors and replacing the weather seals to maintain the doors in good working condition. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
2445ENR1 | LIGHTING UPGRADE | 2445 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3150
2445SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2445 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 4000
2445SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2445 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 3150
2445INT1 | RESTROOM REMODEL | 2445 | The restroom fixtures and finishes are in disrepair from general wear and tear and should be scheduled for replacement. This project would provide for a complete remodel of the restroom including fixtures, hardware, floor and wall finishes. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2444SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2444 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 10080
2436EXT1 | EXTERIOR DOOR REPLACEMENT | 2436 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear and the lock is not secure. This project would provide for the replacement of the wood door with a new metal door ,frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/11/2011. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
9909SIT5 | SLURRY SEAL ASPHALT PAVING | 9909 | It is important to maintain the asphalt concrete paving for the JOIN building and NDOW Office parking lots. This project would provide for minor crack filling and slurry sealing of the paving . Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 40,000 square feet of asphalt area was used to generate this estimate. | WINNEMUCCA SITE | 9909 | Wildlife |  |  | Winnemucca | 0 |  | 2011-05-11 | Four to Ten Years | Long-Term Needs | 3 | 30000
9909SIT6 | CHAIN LINK FENCE REPLACEMENT | 9909 | The majority of the chain link fencing around the site has failed and is due for replacement. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence in place of the existing fence with two 14' wide gates with hardware. The cost estimate also includes demolition and disposal of the existing fence. | WINNEMUCCA SITE | 9909 | Wildlife |  |  | Winnemucca | 0 |  | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
2436EXT3 | ROOF REPLACEMENT | 2436 | The corrugated metal and asphalt shingle roof on this building was in poor condition at the time of the survey and is showing signs of leaking. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27980
2436EXT2 | EXTERIOR FINISHES | 2436 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11192
2436INT1 | INTERIOR FINISHES | 2436 | There is a small room in the building that is finished with painted gypsum board. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2446ENV1 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 2446 | At the time of the survey, there were oil drums stored on bare dirt next to the building as well as cans of pesticide and gas cans stored in the same area. This does not meet OSHA standards for proper storage containment. The oil drums should be stored on OSHA approved drum spill pallets and placed on a concrete slab in order to protect the environment from spills or leaks. This project will provide for purchasing four OSHA approved drum spill pallets capable of storing four drums each and purchasing an OSHA approved storage cabinet for miscellaneous items such as the gas cans. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. | NDOW GAS STORAGE | 9909 | Wildlife |  |  | Winnemucca | 0 | 512 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 15000
2439EXT1 | EXTERIOR FINISHES | 2439 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the walls and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW DRY STORAGE QUONSET | 9909 | Wildlife |  |  | Winnemucca | 1961 | 1640 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3280
2445ENV1 | OIL WATER SEPARATOR INSTALLATION | 2445 | The existing wash facility adjacent to the maintenance shop currently has a plugged drain and does not have an oil water separator. It is recommended that an oil water separator be installed and the drain restored to bring the wash rack back to full operational capability. Additionally, a backflow preventer should be installed on the wash rack supply line. The estimate is based on work and materials to unplug the drain, install a 3/4" backflow preventer and install a 50 GPM steel oil interceptor. This project or a portion thereof was previously recommended in the FCA report dated 03/25/2004. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/11/2011. | NDOW SHOP | 9909 | Wildlife |  |  | Winnemucca | 1984 | 1260 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 15000
2444EXT2 | EXTERIOR FINISHES | 2444 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2436EXT4 | WINDOW REPLACEMENT | 2436 | The windows are original, single pane construction in a wooden frame. These older windows are damaged and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane windows. This estimate is for the replacement of 2 small units and 2 larger units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | NDOW LEAN-TO STORAGE | 9909 | Wildlife |  |  | Winnemucca | 1955 | 5596 | 2011-05-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2444SFT5 | FIRE ALARM SYSTEM INSTALLATION | 2444 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | NDOW OFFICE | 9909 | Wildlife |  |  | Winnemucca | 0 | 1440 | 2011-05-11 | Immediate to Two Years | Currently Critical | 1 | 5760
2433SIT4 | CONCRETE APRON REPLACEMENT | 2433 | The concrete entrance to the parking lot of the Winnemucca Office Building has extensive cracking and spalling and is due for replacement. This project would provide for the installation of a new concrete slab-on-grade driveway at the entrance to the parking lot. Removal and disposal of the existing concrete is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2433EXT6 | EXTERIOR FINISHES | 2433 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Four to Ten Years | Long-Term Needs | 3 | 39500
2433SFT10 | SITE BOLLARD INSTALLATION | 2433 | The natural gas meter at the rear of the building is not protected from vehicle impact. The meter is close to the parking lot on two sides and is at risk of damage from vehicles. This area is in need of bollards to protect the natural gas lines from damage. This project would provide funding for 4 eight inch diameter bollards to be located in between the gas meter and the parking areas. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2433SFT9 | EXTERIOR LANDING INSTALLATION | 2433 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the north side of the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2433ELE1 | ELECTRICAL UPGRADE | 2433 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential and there have been many alterations to the system over the years. Staff has reported that there are some outlets that do not work. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158000
2433ENR3 | HVAC REPLACEMENT | 2433 | The two HVAC roof top units in the single level portion of the building were installed in 1985. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52500
2433PLM1 | WATER HEATER REPLACEMENT | 2433 | There is a 30 gallon gas-fired water heater in the single level portion of the building that was installed in 2002. The average life span of a water heater is eight to ten years. It is missing seismic bracing straps, missing a drain pan and the electrical wiring is sub-standard. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2433EXT7 | WINDOW REPLACEMENT | 2433 | The windows on the second floor of the two level portion are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8250
2433INT5 | INTERIOR FINISHES | 2433 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Four to Ten Years | Long-Term Needs | 3 | 39500
2433SFT11 | GUARDRAIL REPLACEMENT | 2433 | The guard railing around the rear stairwell is older, non-code compliant in configuration and due for replacement. A compliant railing is recommended because the elevation change from the walking surface at grade level to the bottom landing of the stairwell exceeds 30 inches. This project recommends the replacement of guard railing to form a protective barrier along the open side in accordance with the 2012 IBC Chapter 10, Section 1013. 20 linear feet was used to generate this estimate. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2433SIT2 | SLURRY SEAL ASPHALT PAVING | 2433 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving in front of the building including the access roads and parking lot. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 3,600 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 03/25/2004 and 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2433INT6 | KITCHENETTE REPLACEMENT | 2433 | The kitchenette and associated cabinets in the first floor of the two level portion of the building are over 20 years old. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertop are delaminating and failing. This project recommends the replacement of the existing kitchen counter, cabinets, sink and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2433SFT8 | WATER HEATER REPAIRS | 2433 | There are two water heaters in the building, one serving the single level portion and one serving the two level portion. The water heater in the single level portion is missing a drain pan, missing seismic straps and the electrical wiring appears to be sub-standard. The new water heater installed in the two level portion of the building is not operational and is missing a drain pan. At the time of the survey, the electrical wiring was not connected to the breaker box. This water heater provides hot water to the entire two level portion of the building and should be repaired before employees are assigned to this area. This project would provide for a licensed electrician to properly connect power to the new water heater, repair the electrical wiring for the older water heater and perform testing to ensure that they are fully operational and safe. This project also provides for installing drain pans and seismic bracing. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 2500
2433SFT12 | FURNACE FLUE/ VENT REPLACEMENT | 2433 | The newer Lennox HVAC units in the two level portion of the building appear to have not been installed per the manufacturers instructions. Since this is a 90% efficiency unit, a proper PVC venting system should have been installed with the new units. It appears that the new units were connected to the existing sheet metal flue/ vent. This project would provide for a licensed HVAC installer to replace the flue/ vent per the manufacturers instructions. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 1500
2433SIT3 | DRAINAGE IMPROVEMENTS | 2433 | The building has had considerable damage to the paint and caulking in the past from improper drainage around the building. The exterior finishes have been repaired and the basement walls have been waterproofed, but the grading is still a problem. The grade does not slope away from the building in several areas, especially at the rear of the building. This is causing water to pool up next to the building, infiltrate the windows and damage the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. This project or a portion thereof was previously recommended in the FCA reports dated 03/25/2004 and 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2433SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2433 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2433INT1 | RESTROOM REMODELS | 2433 | The two restrooms in the first floor of the two level portion are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2433SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 2433 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building in two locations. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 8000
2433ADA4 | ADA SIGNAGE | 2433 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 2250
2433SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2433 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 110600
2433SIT1 | LANDSCAPE UPGRADES | 2433 | Landscaping around the Winnemucca Office Building has deteriorated over time and is due for an upgrade. This project would replace the existing landscaping with xeriscape including a new drip irrigation system and control box. This type of design will conserve water and require less maintenance. The estimate includes removal and disposal of the existing landscape materials. This project or a portion thereof was previously recommended in the FCA reports dated 03/25/2004 and 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2433SFT7 | CONFERENCE ROOM EXITING MODIFICATIONS | 2433 | All exit corridors in a building are required to have a clear width of at least 36". The corridor between the conference room and the main hallway is only 34" which is a building code violation. This project would provide for installing an exterior exit door in the conference room to comply with the building code. Alternatively, the corridor could be widened to provide the 36" clear width, but additional costs would be necessary for this alteration. Section 1005.1 and Table 1018.2 of the 2012 IBC were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2433SFT5 | INTERIOR STAIR HANDRAIL REPLACEMENT | 2433 | The interior stair handrails from the main floor to the upper and lower floors at the rear of the building are older and do not meet code for safety. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns, gripping surfaces and supports in accordance with the 2012 IBC Chapter 10, Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2433INT4 | CEILING TILE REPLACEMENT | 2433 | The ceiling in the single story portion of this building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and some are coming loose from the substrate. Many 2x2 tiles have been replaced with ill-fitting 2x4 tiles. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. Additional costs would be required if there is asbestos in the tiles or adhesive. Additional costs would be required if there is asbestos in the tiles or the insulation above the ceiling. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
2433INT3 | CARPET REPLACEMENT | 2433 | The carpet in the building is showing signs of wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet or Vinyl Composite Tiles (VCT) in the next 2-3 years. Additional costs would be required if there is asbestos in the carpet adhesive. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49000
2433SFT6 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 2433 | There are two sets of stair handrails at the rear of the building that are older and do not meet code for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair. This project recommends the installation of handrails in accordance with IBC Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 05/11/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/01/2015. | WINNEMUCCA OFFICE BUILDING | 9909 | Wildlife |  |  | Winnemucca | 1964 | 7900 | 2015-09-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0683ENR1 | LIGHTING UPGRADE | 0683 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BUTLER BUILDING #2 - NORTH | 9912 | Military | NNG |  | Henderson | 1992 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12800
0683EXT1 | EXTERIOR FINISHES | 0683 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BUTLER BUILDING #2 - NORTH | 9912 | Military | NNG |  | Henderson | 1992 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
0684EXT1 | EXTERIOR FINISHES | 0684 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HAZARDOUS WASTE STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 1990 | 252 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504
2412SFT1 | GUARDRAIL | 2412 | The tower is missing a solid wall or guardrail on one side of the platform. This project recommends the installation of a wall or guardrail to form a protective barrier along the open side. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | RANGE TOWER | 9912 | Military | NNG |  | Henderson |  | 12120 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 750
3094EXT1 | EXTERIOR FINISHES | 3094 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting the walls and roof and caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | OIL STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 2005 | 129 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1290
2412EXT1 | EXTERIOR FINISHES | 2412 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | RANGE TOWER | 9912 | Military | NNG |  | Henderson |  | 12120 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24240
9912PLM1 | SEPTIC SYSTEM REPLACEMENT | 9912 | The septic system serving the Henderson Armory site is original to the site and is in poor condition. The City of Henderson has developed around the Henderson Armory site and has made city sewer available to the site. This project recommends abandoning and filling in the old septic tank and leach field (per NDEP’s rules and regulations) and installing new sewer lines and a hot tap into the City of Henderson’s sewer system. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0683EXT2 | EXTERIOR SIDING REPLACEMENT | 0683 | The corrugated metal panels covering the building are original and some are dented and damaged and should be scheduled for replacement. This project would provide for the removal and the disposal of the existing damaged panels and the replacement with new pre-painted metal panels. The estimate is based on 96 square feet of 4' wide panels at $17.00 per square foot. | BUTLER BUILDING #2 - NORTH | 9912 | Military | NNG |  | Henderson | 1992 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1632
2412EXT2 | ROOF REPLACEMENT | 2412 | The standing seam metal roof, underlayment and sheathing on this building were in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed with new underlayment and sheathing in the next year with a new single-ply roofing system. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | RANGE TOWER | 9912 | Military | NNG |  | Henderson |  | 12120 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 181800
0680SFT4 | EXTERIOR LANDING INSTALLATION | 0680 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door and the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0680ADA10 | RAMP MODIFICATIONS | 0680 | This facility has an ADA accessible ramp located on the side of the building. This ramp is on the accessible path of travel from the accessible parking space to the Henderson Armory building. The ramp does not have proper landings or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 25000
0680ADA8 | ADA SHOWER UPGRADE | 0680 | This project would provide for one ADA compliant stainless steel shower cabinet to be installed to provide shower facilities for the disabled. Included in this estimate are the plumbing fixtures and seats. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180, and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 50000
0682SFT1 | ANCHOR SHELVES | 0682 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1), All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a licensed engineer or architect. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 10000
0680SFT5 | STORAGE REMOVAL | 0680 | The storage in the Drill Hall room is blocking the exit. The 2012 IBC Chapter 10 Means of Egress explains that exit routes cannot be blocked, reduced or altered. This project would provide for the removal of all items to ensure that the egress and exit routs are not impeded. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
0682ENR1 | LIGHTING UPGRADE | 0682 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12800
0680PLM1 | WATER HEATER REPLACEMENT | 0680 | There is a 118 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is missing proper seismic bracing and an expansion tank. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0684EXT2 | EXTERIOR SIDING REPLACEMENT | 0684 | The corrugated metal panels covering the building are original and some are dented and damaged and should be scheduled for replacement. This project would provide for the removal and the disposal of the existing damaged panels and the replacement with new pre-painted metal panels. The estimate is based on 96 square feet of 4' wide panels at $17.00 per square foot. | HAZARDOUS WASTE STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 1990 | 252 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1632
3094INT1 | INTERIOR FINISHES | 3094 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OIL STORAGE BUILDING | 9912 | Military | NNG |  | Henderson | 2005 | 129 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1290
9912SIT5 | EROSION CONTROL | 9912 | On the north side of the site, the dirt bank is eroding to the sidewalk. This is now causing damage to the site drainage and public sidewalk. There have been several minor improvements accomplished to control the situation, but it is apparent that a major improvement must happen in order to protect the site and public sidewalk from permanent damage. This project recommends installing a retaining wall between the site drainage and public sidewalk in order to provide proper drainage and erosion control. The estimate is based on a 500 foot long, 5'-0" high reinforced concrete masonry unit retaining wall. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9912SIT4 | CRACK FILL & SEAL ASPHALT PAVING | 9912 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 100,000 square feet of asphalt area was used to generate this estimate. It is recommended that this project coincide with the ADA Accessible Path of Travel project. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 125000
9912SIT3 | SITE DRAINAGE ASSESSMENT | 9912 | The site has drainage concerns on the west side of the buildings. There is a hill located behind the buildings that slope toward the buildings and asphalt parking lot. The rain accumulates in several areas behind and adjacent to the buildings, creating a possible infiltration into the interior during inclement weather. This standing water also causes premature deterioration of the paving and other landscape improvements. This project would provide for a site survey and a drainage report to be completed by a licensed professional to determine what measures should be taken to prevent future flooding. Future projects may arise from the results of this report. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0682EXT2 | EXTERIOR SIDING REPLACEMENT | 0682 | The corrugated metal panels covering the building are original and some are dented and damaged and should be scheduled for replacement. This project would provide for the removal and the disposal of the existing damaged panels and the replacement with new pre-painted metal panels. The estimate is based on 96 square feet of 4' wide panels at $17.00 per square foot. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1632
0680INT6 | INTERIOR FINISHES | 0680 | It is recommended to paint the interior walls and ceilings at least once in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 179600
0680INT4 | JANITORS CLOSET REPAIRS | 0680 | The mop sink in the Janitors Closet is mounted adjacent to CMU walls and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
9912ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 9912 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Henderson Armory are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 30000
0680INT5 | SOUND DAMPENING | 0680 | The staff has installed carpet on some of the walls to help reduce the echoing in the classroom in the Henderson Armory, however the sound echoes to the point that it makes the room unusable. This project would provide carpet or sound soak on the walls. This should dramatically reduce the echoing in the classroom. This project would provide for 600 square feet of carpet or sound soak to be installed on the walls. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 4800
0680SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0680 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
0680ENR1 | EXTERIOR INSULATION & FINISH SYSTEM | 0680 | The building is constructed of concrete masonry units (CMU) with no insulation. Buildings of this type are not energy efficient. This project recommends adding an exterior insulation & finish system (EIFS) over the CMU. The estimate is based on $10.00 per square foot for the EIFS. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176900
0680SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0680 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 247660
0680SFT3 | FIRE ALARM SYSTEM UPGRADE | 0680 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 70760
0680ADA6 | ADA SIGNAGE | 0680 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180, and the most current version of the ADA Standards For Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 1500
9912SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 9912 | There are two sets of concrete stairs on the west side of the property that are lacking handrails as required in the 2012 IBC Chapter 10, Section 1012. The stairs connect the lower east side of the property to the higher west side. This project would provide for tubular steel framed handrails to be installed in accordance with code. If the vertical rise exceeds 12 feet, the entire stairway will need to be removed and replaced with a stair landing at the midpoint. Field verification will need to be done to estimate the vertical rise from the upper landing to the lower landing. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 10000
0682EXT1 | EXTERIOR FINISHES | 0682 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BUTLER BUILDING #1 - SOUTH | 9912 | Military | NNG |  | Henderson | 1993 | 1600 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
0680EXT3 | OVERHEAD DOOR REPLACEMENT | 0680 | There is one 16'x14' and three 8'x10' overhead coiling doors on the building. They are not insulated and the weather stripping is damaged or missing causing heat loss in the winter and cooling loss in the summer. It is recommended to replace the doors with insulated doors and install new weather stripping. The door frames and mechanical equipment can be re-used with the new doors. This project would provide for the removal and disposal of the roll-up doors and installation of new doors. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
9912SFT2 | EMERGENCY GENERATOR INSTALLATION | 9912 | The site is lacking an emergency generator to power the buildings in the event of a loss of power. The Armory is designed as an essential services building which is a high priority for being equipped with emergency power. This project provides for the purchase and installation of a 150 kW diesel-engine-driven generator set. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
0680EXT1 | EXTERIOR FINISHES | 0680 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176900
0680ADA7 | ADA RESTROOM UPGRADES | 0680 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180, and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 40000
9912ENR1 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9912 | There are six or seven existing light poles around the site. With increased traffic and development in the area, insufficient site lighting is a security and safety concern. This project would provide for the installation of 12 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles may be acceptable to re-use. If so, the estimate can be reduced accordingly. This project or a portion thereof was previously recommended in the FCA report dated 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY SITE | 9912 | Military | NNG |  | Henderson | 0 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 264000
0680ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0680 | This building contains water fountains on each floor that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. This project or a portion thereof was previously recommended in the FCA report dated 10/16/2003 and 02/01/2011. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | HENDERSON ARMORY | 9912 | Military | NNG |  | Henderson | 1971 | 17690 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
1681PLM1 | WATER HEATER REPLACEMENT | 1681 | There is a 5 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9913SIT2 | ASPHALT PAVING INSTALLATION | 9913 | The access road from the parking lot to the Maintenance Shop and the parking area in front of the Maintenance Shop are not paved. This project would provide asphalt cement paving for a 10' wide access road and paving the parking area at the maintenance shop. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. A drainage swale should be incorporated into the access road at the slope going down to the parking lot. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1905SFT1 | FIRE ALARM SYSTEM INSTALLATION | 1905 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4000
9913SIT3 | WATER FEATURE REPAIRS | 9913 | The man made creek and pond on the site are deteriorating and due for repairs. They are made of free-formed concrete to direct and collect the water. The concrete is settling and shifting and has significant cracking. The cracks allow water to seep into the ground requiring the park to increase their water consumption from the city. The creek and pond have not been equipped with a sufficient pump and filter which have allowed debris and trash to build up and generally to cloud the water. This project would provide for repairing the concrete and cleaning up the creek and pond. The pump and filter equipment will be addressed in the Pump House projects. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1681ADA2 | ADA RAMP HANDRAIL INSTALLATION | 1681 | This building has an ADA accessible ramp located on the east side of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have handrails or edge protection which are required for ADA compliance. This project would provide for installing handrails on the ramp including proper returns, gripping surfaces and edge protection to make it fully ADA compliant. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 5000
1681INT1 | INTERIOR FINISHES | 1681 | The interior finishes are in fair condition. It is recommended that the painted interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1681ENR2 | PHOTOVOLTAIC POWER SYSTEM INSTALLATION | 1681 | There is no natural gas service to the site. All of the equipment including HVAC and water heating is powered solely by electricity. This makes the building an ideal candidate for photovoltaic power which could be installed on the roof. A photovoltaic power system would eliminate electricity costs and could be fitted with a reverse power meter to sell power back to the electric company. This project would provide for the purchase and installation of a 15 kW photovoltaic system including solar panels, deep cycle solar batteries, a reverse power meter and all associated electrical boxes and hardware to connect it to the main electrical service. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 150000
1681ADA1 | ADA SIGNAGE | 1681 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 750
1681INT2 | FLOORING MAINTENANCE | 1681 | The concrete floor sealant is damaged and reaching the end of its useful life. It is recommended that the concrete be stripped and re-sealed in order to extend the concretes' useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next 2-3 years. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1905ELE1 | ELECTRICAL UPGRADE | 1905 | The building is equipped with a knob and tube electrical system. This type of system is no longer used and replacement parts are impossible to find. The main disadvantage of this electrical system is that there is no safety grounding conductor. Also, as the cotton and rubber wire insulation ages, it becomes dry and brittle and becomes easily damaged. It is recommended the entire system be upgraded to a modern electrical system. The existing knob and tube system could remain in place to display the historical nature of the Museum. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1905EXT1 | EXTERIOR/ INTERIOR FINISHES | 1905 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the structure. Included in the cost is basic adobe maintenance by the staff as well as funds for adobe specialists to come out once a year. These costs should be sufficient to allow the specialists to spend two days per year at the Museum over the next four years. This project should be scheduled on a cyclical basis to maintain the integrity of the Museum. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1681EXT2 | PUBLIC ENTRANCE STAIRWAY INSTALLATION | 1681 | The entrance to the building is often overlooked by visitors and is generally uninviting. Without a stairway from the parking lot to the front door, visitors have a hard time discerning where the entrance to the Visitors Center is. This project would provide for installing a concrete stairway in front of the entrance to the building. The stairway shall be designed to comply with all adopted building codes and the ADA accessibility guidelines. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 20000
1681SEC1 | SECURITY UPGRADES | 1681 | The site and buildings have experienced break-ins in the recent past. The Visitors Center was compromised by breaking a window in the Conference Room. Currently, the windows are not alarmed and the alarm sensors in the building did not detect the intruder quickly. Part of the reason for the delay in detection may have been that some of the motion sensors are not located properly. They are located too high on the walls and some are blocked by displays. This project would provide for upgrading the security system by relocating the existing sensors and alarming the doors and windows. Alternatively, the windows could be provided with an exterior security shutter to prevent vandalism and break-ins. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 25000
1681ENR1 | OCCUPANCY SENSOR INSTALLATION | 1681 | There are no occupancy sensors installed in the building to control lighting. It is recommended to install sensors in order to reduce energy costs. Occupancy sensors will be installed in restrooms, conference rooms, utility rooms and other low occupancy. This project provides for purchase and installation of 6 sensors. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1681PLM2 | BACKFLOW PREVENTER INVESTIGATION | 1681 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. There may be a pressure problem with the incoming water main. The psi valve is maxed out indicating the pressure is above 100 psi. This may be the cause of the broken prevention valve and should be analyzed by a licensed plumber. This project would provide for employing a licensed plumber to replace the backflow preventer and to analyze the system. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 1000
1681EXT1 | EXTERIOR FINISHES | 1681 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9913SEC1 | FENCE UPGRADE | 9913 | The landscape fence on the south side of the site is not tall enough to keep people from climbing over it. Vandals and thieves have accessed the property by climbing over the fence and it is recommended to add height to the fence to prevent this. This project would provide for adding concrete masonry units to the existing fence to raise the height of the fence by 3 feet. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 8000
9913SIT5 | GRADING AT BONEYARD AREA | 9913 | The site has a drainage problem in the bone yard area on the northwest side of the site. The existing grade does not properly slope towards the storm drain. Water accumulates in several areas adjacent to the drain creating a water and mud problem during inclement weather. This project would provide for grading in this area to slope the grade towards the drain. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
9913SIT4 | TREE REMOVAL | 9913 | There are two Mulberry trees that have reached the end of their expected lives and should be removed. The trees are adjacent to the Historic Fort Museum which would incur extensive damage if one of these trees fell on it. Previously, a similar tree fell into the road and caused an emergency road closure and removal of the fallen tree. This project would provide for removal of the two trees next to the Museum by a licensed tree removal company and a survey of the site to determine whether any other trees should be removed. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 3000
9913ADA3 | ADA SIGNAGE | 9913 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 2500
9913ADA2 | GROUP USE AREA IMPROVEMENTS | 9913 | The group use area is not ADA compliant and is not functional as is. This area should be scheduled for improvements. Currently, the picnic tables are under wooden grape vine trellises. The tables are also worn and deteriorated and there are no ADA tables or access. This project would provide for the purchase and installation of 10 new picnic tables including one accessible table, a new shade ramada to cover all of the tables and flatwork to provide ADA access between the new tables and the restroom. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 25000
1681HVA1 | HVAC DUCTING REPLACEMENT | 1681 | The existing HVAC system employs a collapsible ducting system. This system makes a lot of noise in such a way that it startles visitors in the building. It is not a system that is appropriate for a museum type setting and it is recommended to install rigid ducting in its place. This project would provide for the removal of the existing ducting and installation of new rigid ducting including attachment to ceiling, supply and return diffusers and balancing by a licensed HVAC contractor. | MORMON FORT VISITORS CENTER | 9913 | CNR | Parks |  | Las Vegas | 2005 | 5000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2397EXT2 | GUTTER INSTALLATION | 2397 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the built-up dirt slope around the foundation. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2397INT1 | INTERIOR FINISHES | 2397 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
2397SEC1 | SECURITY SYSTEM INSTALLATION | 2397 | The building does not have a security system. This project recommends motion detection and window and door sensors be installed and interfaced with the site wide security system. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
1905SEC1 | SECURITY SYSTEM INSTALLATION | 1905 | The building does not have a security system. This project recommends motion detection and window and door sensors be installed and interfaced with the sitewide security system. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1905EXT3 | WINDOW REPLACEMENT | 1905 | The windows are older single pane construction in a wooden frame. These older windows are drafty and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane units. This estimate is for the replacement of 10 units including wooden frames. Additional costs are included due to the historic nature of the building and that the window frames will need to be replicated based on the existing windows. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1905EXT2 | ROOF REPLACEMENT | 1905 | The hot-mopped tar roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed and fitted with rain gutters in the next 2-3 years to be consistent with the roofing program. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC FORT MUSEUM | 9913 | CNR | Parks |  | Las Vegas | 1855 | 1000 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2397SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2397 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 4704
2397EXT1 | EXTERIOR FINISHES | 2397 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
2397SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2397 | The building is partly a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 8232
2397ENR1 | LIGHTING UPGRADE | 2397 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom and office areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2900EXT1 | EXTERIOR FINISHES | 2900 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting or sealing the exposed wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2900INT3 | COUNTERTOP MAINTENANCE | 2900 | The concrete countertop sealant is damaged and reaching the end of its useful life. It is recommended that the concrete be stripped and re-sealed in order to extend the concretes' useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next 2-3 years. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
2900ENR1 | OCCUPANCY SENSOR INSTALLATION | 2900 | There are no occupancy sensors installed in the building to control lighting. It is recommended to install sensors in order to reduce energy costs. Occupancy sensors will be installed in each restroom. This project provides for purchase and installation of 2 sensors. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2864PLM1 | BACKFLOW PREVENTER INVESTIGATION | 2864 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be replaced immediately. There may be a pressure problem with the incoming water main. This may be the cause of the broken prevention valve and should be analyzed by a licensed plumber. This project would provide for employing a licensed plumber to replace the backflow preventer and to analyze the system. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 1000
2900ADA1 | ADA SIGNAGE | 2900 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 900
2397ENV1 | SAFETY CABINETS | 2397 | The shop contains many different oils, paints, stains and other hazardous products on open shelves and work benches. This does not meet OSHA standards for hazardous materials containment. This project would provide for the purchase of two hazardous materials storage containers and installing placards on the building exterior in accordance with OSHA 1910.106 (d). | MORMON FORT VEHICLE SHOP | 9913 | CNR | Parks |  | Las Vegas | 1999 | 1176 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 5000
2900INT2 | FLOORING MAINTENANCE | 2900 | The concrete floor sealant is damaged and reaching the end of its useful life. It is recommended that the concrete be stripped and re-sealed in order to extend the concretes' useful life. This project would provide for stripping the concrete and applying a new coat of sealant in the next 2-3 years. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2900INT1 | INTERIOR FINISHES | 2900 | The interior finishes are in fair condition. It is recommended that the interior concrete masonry unit walls are cleaned and sealed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMOM FORT SOUTH RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 2005 | 600 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2864PLM2 | PUMP AND FILTER REPLACEMENT | 2864 | There is a man made stream with a pond at the bottom that is due for a new water pump and filter. The existing pumps and filters were designed for a swimming pool application, not a large stream and pond with continuously running pumps. It is recommended to replace the pumps with a new 5 H.P. fountain water pump system including a large solids filter and a microfilter. This project includes removal and disposal of the existing pumps and filters and all required connections to utilities. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2864INT1 | INTERIOR FINISHES | 2864 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 700
2398EXT1 | EXTERIOR FINISHES | 2398 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2398INT1 | INTERIOR FINISHES | 2398 | The interior finishes are in fair condition. It is recommended that the painted interior walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
2398ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2398 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 3000
2398ENR1 | LIGHTING UPGRADE | 2398 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restrooms for additional savings. Any electrical wiring upgrades are not included in this estimate. | MORMON FORT RESTROOM | 9913 | CNR | Parks |  | Las Vegas | 1999 | 240 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 360
2399EXT1 | EXTERIOR/ INTERIOR FINISHES | 2399 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building excluding the roof. Included in the cost is cleaning and repairing the brick masonry as needed and caulking of any penetrations. It is recommended that the building be repaired and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMON FORT TOWER | 9913 | CNR | Parks |  | Las Vegas | 1999 | 200 | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2864EXT1 | EXTERIOR FINISHES | 2864 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the exposed wood features, repairing and sealing the stone and masonry work and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MORMOM FORT PUMP HOUSE | 9913 | CNR | Parks |  | Las Vegas | 1999 | 140 | 2017-12-12 | Four to Ten Years | Long-Term Needs | 3 | 700
9913SIT1 | FOG / CRACK SEAL ASPHALT PAVING | 9913 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and fog sealing of the paved parking lot. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 25,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 10/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/01/2011. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18750
9913ADA1 | ADA SITE IMPROVEMENTS | 9913 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. Access to the various features throughout the site is necessary to comply with ADA accessibility requirements. This project would provide for an accessible path of travel to the adobe fort, tower, group use area and to a platform to view the battle re-enactments and other performances on the upper portion of the site. This will require regrading, placement of P.C. concrete, signage, ramps, handrails, a concrete viewing platform and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 10/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/01/2011. | OLD LAS VEGAS MORMON FORT STATE PARK | 9913 | CNR | Parks |  | Las Vegas | 0 |  | 2017-12-12 | Immediate to Two Years | Currently Critical | 1 | 100000
9914SEC2 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9914 | There is no site lighting for the site which is a security and safety concern. This project would provide for the installation of 5 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2395INT3 | COLUMN REPAIRS | 2395 | The existing gypsum board wrapped columns are severely damaged from water infiltration and impacts from forklifts and / or vehicles. This project would provide for column repairs which could include a spray on foam fire proofing system or a gypsum board column wrap. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 18000
2395SFT4 | FIRE ALARM SYSTEM INSTALLATION | 2395 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 45500
9914ADA1 | ADA ACCESSIBLE PARKING AND PATH OF TRAVEL | 9914 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office door are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the ASPHALT PAVING REPLACEMENT project. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 10000
2395EXT2 | EXTERIOR FINISHES | 2395 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting or sealing the concrete masonry unit walls and caulking of the windows, flashing, fixtures, and all other penetrations. It is recommended that the building be painted, sealed, and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
2395ADA2 | ADA RESTROOM REMODEL | 2395 | The Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. The items may include a new sink, toilet, hardware, mirror, fixture, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 15000
9914SEC1 | FENCE REPLACEMENT | 9914 | The majority of the fencing on the west and north sides has reached the end of its expected life and should be scheduled for replacement. This project recommends the installation of a 6 foot high 6 gauge wire perimeter chain link fence with barbed or razor wire on the south, west and north sides of the property. The fence on the east side was recently replaced and is in good condition. The cost estimate also includes demolition and disposal of the existing fence. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 30000
2396EXT1 | DEMOLISH STRUCTURE | 2396 | The wood framed structure is structurally failing and is in danger of falling down. At least one post has sheared off and is resting on the asphalt, numerous wood members are splitting and numerous connections between structural members have detached. The roof sheathing is also failing and is dangerous due to wood pieces becoming detached by the wind. The structure is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the structure. | PURCHASING WAREHOUSE CARPORT | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 2000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 20000
2395INT2 | INTERIOR FINISHES | 2395 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the office portion of the building be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Four to Ten Years | Long-Term Needs | 3 | 7500
2395EXT3 | EXTERIOR DOOR REPLACEMENT | 2395 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the single man door assembly with a new metal door, frame, and hardware. Removal and disposal of the existing door is included in this estimate. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2395EXT5 | ROOF REPLACEMENT | 2395 | The roof on this building was in poor condition at the time of the survey. The current roofing system which was installed in 2007 is an elastomeric silicone coating and rigid insulation over the original standing seam metal roof panels. The elastomeric coating is splitting and cracking in many areas due to expansion and contraction of the metal roof framing. It is recommended that this building be re-roofed in the next 1-2 years to maintain the integrity of the structure. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 156000
9914SIT1 | ASPHALT PAVING REPLACEMENT | 9914 | The asphalt paving around the building is failing, with significant alligatoring, settling and cracks observed. This project covers the removal and replacement of the existing asphalt site wide for parking, site access and deliveries. Striping for safety, parking and loading zones is included in this estimate. 25,000 square feet was used to generate this estimate. This project should be implemented concurrently with the ADA ACCESSIBLE PARKING AND PATH OF TRAVEL project. This project or a portion thereof was previously recommended in the FCA report dated 10/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | LAS VEGAS PURCHASING WAREHOUSE SITE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 |  | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 250000
2395STR1 | STRUCTURAL / SEISMIC RETROFIT | 2395 | The concrete masonry and steel framed structure was built in 1960 and is due for structural repairs. There are major cracks in the concrete masonry unit walls which have gotten worse year by year. Water which infiltrates the cracks freezes in the winter and causes the cracks to widen. Cracking at the southwest corner of the building is significant and may indicate a settling issue below the foundation. The water infiltration also damages the interior of the building and is a health department violation due to the storage of dry goods in the building. It is recommended to repair the structure immediately by patching and sealing any existing cracks. Further evaluation of the structure should be done to determine whether more permanent repairs are needed such as pumping under the foundation or rebuilding the walls. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 390000
2395EXT4 | LOADING DOCK UPGRADE | 2395 | The loading dock is damaged and due for major repairs. The concrete is cracked and failing to the point of exposing the reinforcing steel and jeopardizing the integrity of the structure. The ramp from the parking lot also has significant deterioration and requires complete replacement. This project would provide for repairs to the loading dock including removing and replacing damaged concrete and bumpers, replacement of the ramp, and installing a mechanical dock leveler. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
2395ENR1 | LIGHTING UPGRADE | 2395 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, the conference room, and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
2395ENR2 | HVAC EQUIPMENT REPLACEMENT | 2395 | One of the two HVAC roof top units above the office area has reached the end of its expected and useful life. This project would provide for installation of one new HVAC packaged unit and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2395SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2395 | The building is more than 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Immediate to Two Years | Currently Critical | 1 | 123500
2395EXT6 | WINDOW REPLACEMENT | 2395 | There are four old single pane windows which are in need of replacement. This project would provide for four new insulated window units to be installed. Removal and disposal of the old units is included in this estimate. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2395SFT1 | INTERIOR STAIR HANDRAIL REPLACEMENT | 2395 | The interior stair handrail is older and does not meet code for safety or accessibility. The gripping surfaces are incorrect, the handrail is missing from one side of the stair and it does not have proper returns. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railing is included. NRS 338.180, 2006 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 10/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/10/2012. | LAS VEGAS PURCHASING WAREHOUSE | 9914 | Admin | PubWorks | B&G | Las Vegas | 1960 | 13000 | 2018-05-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2304EXT1 | EXTERIOR FINISHES | 2304 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #3 | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 600 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
2304EXT2 | SIDING AND ROOF REPAIRS | 2304 | There is damage to the metal siding and the metal roof which is compromising the weather resistance of the building. The siding has been punctured and is exposing the framing of the building. It is recommended to repair the damage immediately in order to protect the framing and the interior of the building. | STORAGE #3 | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 600 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 3500
2303EXT4 | REPLACE EXTERIOR STAIRS, DECK AND DOOR | 2303 | The existing deck and stairs on the north side of the building are in poor condition and do not meet current building code requirements. This project would provide for the removal of the existing stairs and deck and replacement with a new wood framed deck and stair system including hand and guardrails, landing and route of travel to the paved parking area. Also included is the replacement of the exterior door, frame and hardware. | MODULAR STORAGE #2- EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19500
2304EXT3 | INSTALL EXTERIOR DOOR LANDING | 2304 | The exterior door on the north side of the building does not have a landing as required by the 2006 IBC Chapter 10. The step from finish floor to grade is about 12". This project would provide for the installation of a concrete landing at the exterior door. | STORAGE #3 | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 600 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 250
0395ADA3 | INSTALL ADA SIGNAGE | 0395 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC Chapter 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 900
0395INT1 | INTERIOR FINISHES | 0395 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40685
2303EXT1 | EXTERIOR FINISHES | 2303 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. This project also includes an allowance for the replacement of damaged fascia and trim. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | MODULAR STORAGE #2- EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8064
0395ADA1 | ADA ACCESSIBLE COUNTER | 0395 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This building contains a counter which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. The 2006 IBC Chapter 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 3000
0395EXT1 | EXTERIOR FINISHES | 0395 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the brick masonry, painting, staining or other applied finishes, and caulking around windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project also includes the repair and / or replacement of missing and damaged brick masonry units. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56959
0395EXT3 | REPLACE WINDOWS | 0395 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 109 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 109000
0395SFT1 | INSTALL DUST COLLECTION SYSTEM | 0395 | The building has an automated OCR mail sorter, which generates an observable amount of fine paper dust. The equipment does not have a dust collection system. This project recommends the installation of a dust collection system for the mail sorter including vacuum tubing and all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 18000
2303EXT2 | REPLACE ROOF | 2303 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | MODULAR STORAGE #2- EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
9916SIT2 | CONCRETE SIDEWALK REPLACEMENT | 9916 | Several sections of the concrete sidewalks serving this site have deteriorated and are spalling or heaving which presents a tripping hazard. The sidewalk east of the Mail Services building has sections missing and the sidewalks along the north side of the site are in need of replacement and new curb cuts should be provided. This project would provide for the removal and replacement of all damaged concrete walkways on this site including tying into the new sidewalks along the north side of the site. 4,000 square feet of concrete was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION/STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 40000
9916SIT1 | PATCH, CRACK FILL AND SLURRY SEAL ASPHALT PAVEMENT | 9916 | The existing asphalt pavement is in poor to fair condition. There are areas that are in need of removal and replacement, crack filling and sealing. This project would provide for the removal and replacement of damaged asphalt pavement, crack filling and a slurry seal of the entire paved parking area. Striping and wheel stops are included in this estimate. Also included are concrete filled bollards to be installed around the gas meter servicing the Education Office. Sealing of the asphalt paving also should be scheduled on a cyclical basis of every 3 to 5 years to maintain the integrity of the paving. A figure of 60 cents a square foot for sealing could be used for cyclical pavement sealing which is not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION/STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62901
9916ADA1 | ADA PARKING | 9916 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are two existing ADA parking spaces on the south side of the Education Building that do not meet the requirements of the code. Also, this project would upgrade the ADA parking and loading spaces for the Mail Services building on the north and south parking areas. This project provides funding to bring the existing ADA, route of travel and parking spaces up to code including removal of the asphalt and replacement with P.C. concrete where applicable, updated signage, re-striping, re-grading, route of travel and any other necessary upgrades. The 2006 IBC Chapter 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project should coincide with the recommended pavement project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION/STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 25000
0395HVA1 | HVAC EQUIPMENT REPLACEMENT | 0395 | The six HVAC roof top units should be scheduled for replacement in the next ten years. They are not energy efficient and will reach the end of their expected and useful life in ten years. This project would provide for installation of six new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Four to Ten Years | Long-Term Needs | 3 | 72000
0395PLM1 | WATER HEATER REPLACEMENT | 0395 | There is a 53 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0395SFT2 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0395 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 4000
0395SFT3 | SAFETY CABINETS | 0395 | There are paints and cleaning products stored in a closet which also contains a water heater. This does not meet OSHA standards for hazardous materials containment. This project would provide a hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 5000
0395ENR1 | LIGHTING UPGRADE | 0395 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20342
2303INT1 | INTERIOR FINISHES | 2303 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MODULAR STORAGE #2- EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3456
2303ADA1 | REPLACE ACCESSIBLE ENTRANCE RAMP / ENTRY DECK | 2303 | This facility has a wood ramp and entry deck located on the south side of the building which is the only entrance and exit to the building. The ramp and deck are deteriorating and do not have proper landings, guardrails or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant including new decking, handrail, guardrails, signage and landings. The 2006 IBC Chapter 10 and 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | MODULAR STORAGE #2- EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 18000
2303EXT3 | WINDOW REPLACEMENT | 2303 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | MODULAR STORAGE #2- EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0395ADA2 | ADA ACCESSIBLE ENTRANCE RAMP | 0395 | This facility has an ADA accessible ramp located on the north side of the building. This ramp is on the accessible path of travel from the accessible parking space to the rear entrance of the building. The ramp does not have proper landings nor does it have handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2006 IBC Chapter 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 15000
2303SFT1 | FIRE ALARM SYSTEM UPGRADE | 2303 | This building is equipped with an automatic fire detection and alarm system that is no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MODULAR STORAGE #2- EAST | 9916 | Admin | PubWorks | B&G | Carson City | 1960 | 1152 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 3456
0395ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0395 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. The 2006 IBC Chapter 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 4000
0395INT2 | RESURFACE CONCRETE FLOOR | 0395 | The painted concrete floor in the building is worn and cracked and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45500
9916ENV1 | IRRIGATION RELOCATION AND TURF REMOVAL | 9916 | There is a large area of irrigated turf along the south and east side of the Mail Services building. There are sprinkler heads adjacent to the brick masonry exterior which are wetting the brick and is causing damage. Water may also infiltrate the walls which could lead to mold growth and other environmental issues with the structure. This project would provide for the removal of the turf to about 5 feet away from the structure and relocate all sprinkler heads to prevent water from spraying the side of the building. | EDUCATION/STATE MAIL SERVICES SITE | 9916 | Admin | PubWorks | B&G | Carson City | 0 |  | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 3000
0395SFT4 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0395 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the tables, boxes and other items currently blocking the working space. | STATE MAIL SERVICES BUILDING | 9916 | Admin | PubWorks | B&G | Carson City | 1953 | 8137 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 250
2308EXT3 | WINDOW REPLACEMENT | 2308 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2308SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2308 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 16128
2308SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2308 | This building is equipped with an automatic fire detection and alarm system that appears to be no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 3402
2308HVA1 | HVAC EQUIPMENT REPLACEMENT | 2308 | The building is heated and cooled by several separate pieces of equipment including electric baseboard heaters, wall-mounted evaporative coolers and a portable air conditioning unit. These units are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new HVAC packaged unit and ductwork to provide conditioning for the entire building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 34560
2308ENR1 | LIGHTING UPGRADE | 2308 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
0202INT1 | INTERIOR FINISHES | 0202 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2 to 3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 82500
2308EXT1 | EXTERIOR FINISHES | 2308 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming, painting, caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 8064
2308INT1 | INTERIOR FINISHES | 2308 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
2302EXT1 | EXTERIOR FINISHES | 2302 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2302EXT2 | REPLACE ROOF | 2302 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21600
2308EXT2 | REPLACE ROOF | 2308 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. Repairs to the fascia board are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
2308ADA1 | REPLACE ACCESSIBLE ENTRANCE RAMP / ENTRY DECK / STAIR | 2308 | This facility has a wood ramp, stairs and entry deck located on the south side of the building which is the only entrance and exit to the building. The ramp, stairs and deck are deteriorating and do not have proper landings, guardrails or handrails. This project would provide for an upgrade to the ramp, deck and stairs to make it fully ADA compliant including new decking, handrail, guardrails, signage and landings. The 2006 IBC Chapter 10 and 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 25000
0202INT2 | REPLACE CARPETING | 0202 | The carpeted flooring was installed during the remodel of 1995. It is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal of the existing carpet and installation of new commercial grade carpet tiles and new rubber base. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105000
2308INT2 | REPLACE CARPETING | 2308 | The carpet in the building is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet tiles in the next two to three years. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | EDUCATION MODULAR OFFICE-WEST | 9916 | Educ | B&G |  | Carson City | 1960 | 1152 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8064
0202EXT1 | EXTERIOR FINISHES | 0202 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including cleaning and sealing the brick masonry, painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Also included is repairs to the damaged brick masonry columns and damaged infill CMU / concrete slab areas where doors once were located. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192500
0202ADA1 | ADA SIGNAGE INSTALLATION | 0202 | The Education Office is missing some ADA accessible signage. This project would provide for the installation of ADA compliant signage including identifying accessible entrances into the building and direction signage to the restrooms. The 2006 IBC Chapter 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 1200
2302ADA1 | REPLACE ACCESSIBLE ENTRANCE RAMP / ENTRY DECK | 2302 | This facility has a wood ramp and entry deck located on the south side of the building which is the only entrance and exit to the building. The ramp and deck are deteriorating and do not have proper landings, guardrails or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant including new decking, handrail, guardrails, signage and landings. The 2006 IBC Chapter 10 and 11, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 18000
0202EXT3 | REPLACE ROOF | 0202 | The existing singly-ply roofing system was installed in 1995 and the composition shingle system around 2007. The statewide roofing program has set the useful life of an average single-ply roof at 20 years. To be consistent with the Statewide Roofing Program, it is recommended that this roof be scheduled for replacement 4-5 years with a new single-ply roofing system. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Four to Ten Years | Long-Term Needs | 3 | 270000
0202PLM1 | WATER HEATER REPLACEMENT | 0202 | The existing 80 gallon natural gas fired water heater is about 10 years old. The average lifespan of these units is around 10-15 years. This project would provide for the scheduled replacement of the unit with a new 80 gallon gas fired water heater including all connections to the existing utilities. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2302INT1 | INTERIOR FINISHES | 2302 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
2302EXT3 | EXTERIOR DOOR REPLACEMENT | 2302 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0202ELE1 | ELECTRICAL SYSTEM / SWITCHGEAR UPGRADE | 0202 | The existing electrical system and switchgear in this building has reached capacity and is of original construction except for minor upgrades over the years. Staff has reported breakers tripping and other issues with overloaded circuits. Technology has evolved over the years and current electrical demands appear to have exceeded the capacity. This project would provide for a complete upgrade to the existing electrical system include all switchgear, subpanels, wiring as needed and all outlets and switches. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412500
2302SFT1 | FIRE ALARM SYSTEM UPGRADE | 2302 | This building is equipped with an automatic fire detection and alarm system that appears to be no longer operating. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MODULAR STORAGE #1-NORTH | 9916 | Educ | B&G |  | Carson City | 1960 | 1440 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 4320
0202SFT1 | INSTALL SEISMIC GAS SHUTOFF VALVE | 0202 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Immediate to Two Years | Currently Critical | 1 | 4000
0202ENR1 | LIGHTING UPGRADE | 0202 | The building lighting fixtures are older units and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Sensors would be installed in low occupancy areas for additional savings. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/31/2009. | DEPARTMENT OF EDUCATION OFFICE | 9916 | Educ | B&G |  | Carson City | 1965 | 27500 | 2009-03-31 | Two to Four Years | Necessary - Not Yet Critical | 2 | 68750
0306PLM1 | FOUNTAIN PUMP REPLACEMENT | 0306 | There is a decorative fountain in front of the building that is no longer operating. The water pump has reached the end of its expected life and is due for replacement. It is recommended to replace the pump with a new 1/2 H.P. fountain water pump. This project includes removal and disposal of the existing pump and all required connections to utilities. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0261INT1 | INTERIOR FINISHES | 0261 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73400
0261EXT2 | EXTERIOR ARCHITRAVE REPAIR | 0261 | It is important to maintain the finish, weather resistance and appearance of the building. There is visible damage to the finish on the architrave section of the entablature. This project recommends work to repair the substrate and finish at this area in order to maintain the building in good, weather tight condition. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 1500
0244EXT3 | EXTERIOR FINISHES | 0244 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, masonry sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Four to Ten Years | Long-Term Needs | 3 | 139920
0244INT2 | INTERIOR FINISHES | 0244 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69960
0244INT3 | JANITORS CLOSET REPAIRS | 0244 | The mop sinks in the Janitor Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitor Closets. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0244SFT5 | INSTALL MAGNETIC DOOR HOLDERS | 0244 | There are doors in the building which have been propped open. In the event of a fire or other emergency, these doors would remain open, creating a possible hazard. This project recommends the installation of magnetic door holders, with closers, tied into the fire alarm, which would hold the doors open. In the event of a fire, the alarm would release the doors, allowing them to close. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 20000
0244SFT6 | PANIC HARDWARE INSTALLATION | 0244 | There are two doors along the fire exit path that do not have panic hardware. It is recommended that the doors be retrofitted with panic hardware to ensure the safety of the occupants in the event of a fire. This project would provide for installing panic hardware on two exit doors. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 2000
0244INT4 | REPAIR MARBLE FLOORING | 0244 | The marble flooring at the entry area is damaged as well as the door threshold adjacent to the marble. Some of the marble tile is completely missing and some is cracked and will continue deteriorating. The damaged area is near a wood door threshold that is deteriorating which has probably contributed to the marble becoming damaged. This project would provide for removing damaged materials and replacing them with new matching marble and a new door threshold. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0261EXT1 | EXTERIOR FINISHES | 0261 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, masonry sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2008-12-10 | Four to Ten Years | Long-Term Needs | 3 | 146800
2950EXT1 | EXTERIOR FINISHES | 2950 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2008-12-10 | Four to Ten Years | Long-Term Needs | 3 | 48000
0306INT2 | INTERIOR FINISHES | 0306 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115500
2950ADA2 | ADA RESTROOM UPGRADE | 2950 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include modifying the lavatory counter to ensure that there is enough legroom under the counter to comply with ADAAG 4.19. Currently, the counter does not provide a clearance of 29 in. above the finish floor nor does it provide a clearance of 8 in. in depth under the counter. This estimate is for two Men's and two Women's restrooms. The removal and disposal of the old restroom fixtures is included in this estimate. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 2000
9917SIT6 | CRACK FILL AND SEAL ASPHALT PAVING | 9917 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the northwest parking lot within the next 2-3 years. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 9,736 square feet of asphalt area was used to generate this estimate. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7302
2950INT1 | INTERIOR FINISHES | 2950 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2950ADA1 | ADA SIGNAGE | 2950 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. | SERVICE CUBE BUILDING | 9917 | AttGen | B&G |  | Carson City | 1994 | 4800 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 900
2311EXT1 | EXTERIOR FINISHES | 2311 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Four to Ten Years | Long-Term Needs | 3 | 68190
2311INT2 | INTERIOR FINISHES | 2311 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34095
2311SFT2 | SEISMIC RETROFIT | 2311 | This building is an unreinforced masonry structure which requires seismic strengthening to meet current life safety codes. An initial study was done under CIP 07-M46 which provided detailed recommendations for a seismic retrofit. The planning and design will be requested under CIP 09-P04 and the construction cost will be requested for the 2011 CIP. The estimate is for the construction costs only. This project should coincide with a complete remodel of the interior of the building. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 238665
2311EXT2 | WINDOW REPLACEMENT | 2311 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2311SFT5 | PANIC HARDWARE INSTALLATION | 2311 | There is a door at the bottom of the north stairwell that does not have proper exiting hardware on the door. It is recommended that the door be retrofitted with new exiting hardware to ensure the safety of the occupants in the event of a fire. This project would provide for installing panic hardware on the door. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 2000
0306EXT1 | EXTERIOR FINISHES | 0306 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Four to Ten Years | Long-Term Needs | 3 | 231000
9917SIT5 | SIDEWALK REPLACEMENT | 9917 | The existing sidewalks around the site range from new to poor condition. Some of the sidewalks have deteriorated and are failing. This project addresses removal and replacement of existing sidewalks as needed including those on the North side of the Attorney General's Office, some areas in the rear courtyard and along 2nd street. The sidewalks should include flared curb cuts for site ADA accessibility. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2311SFT3 | EXIT SIGN UPGRADE | 2311 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Additional signs are also needed to ensure a safe escape in case of a fire. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 6000
0306SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 0306 | There is inadequate emergency egress lighting in the building and the existing lights do not meet current standards. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 3000
9917SIT3 | FENCE INSTALLATION | 9917 | The west side of the complex between the Attorney General's Office and the Heroes Memorial contains electrical equipment and the backup generator. Portions of the area are not blocked from view from the street and equipment switches and shutoffs are in plain view. This project recommends the installation of a wrought iron fence along the west side of the site, similar in design to the one at the Capitol building to keep unauthorized personnel out, and provide a secure outdoor break area for employees. It would be most beneficial if this project is incorporated with the SITE DRAINAGE project that is also included in this report. This fence could be mounted on a curb or stem wall that would help divert water that comes from the west during occasional flooding. This area has to be lined with sand bags during these floods and a wall type item would help mitigate this issue. The estimate is for 300 linear feet of fencing mounted on a concrete stem wall. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 60000
0244EXT1 | WINDOW REPLACEMENT | 0244 | The exterior windows appear to be original to the building. They are single pane, not energy efficient and the wood is in very poor condition. Many windows are no longer operational and have been screwed shut. This project recommends replacing the windows with Pella Monumental Clad Commercial Architect "Classic" model, to match the windows installed in the Frankie Sue Del Papa Building at the opposite end of the block. Costs were developed from information provided by the manufacturer's representative. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0244ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0244 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Signage on the second floor should direct occupants to the new ADA Unisex restroom on the first floor. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 1800
2311ADA3 | SIGNAGE FOR ADA COMPLIANCE | 2311 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Signage on the second floor should direct occupants to the new ADA Unisex restroom on the first floor. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 1800
0306SFT2 | EXIT SIGN UPGRADE | 0306 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Additional signs are also needed to ensure a safe escape in case of a fire. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 3000
0244SFT1 | EXIT SIGN UPGRADE | 0244 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. Additional signs are also needed to ensure a safe escape in case of a fire. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 5400
0306ADA2 | SIGNAGE FOR ADA COMPLIANCE | 0306 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Signage on the second floor should direct occupants to the new ADA Unisex restroom on the first floor. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 3000
2311SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 2311 | There is inadequate emergency egress lighting in the building and the existing lights do not meet current standards. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 5000
2311ENR1 | LIGHTING UPGRADE | 2311 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20457
9917SFT3 | REPLACE STAIR HANDRAILS/ GUARDRAILS | 9917 | The handrails and guardrails at some of the exterior stairs, including the fire escapes, do not meet code for safety or accessibility. The gripping surfaces are incorrect, the handrails do not have proper returns and/or there are improper or missing guardrails. This project recommends the installation of new handrails on both sides of the stairs, with proper guardrails, returns and supports. The rails should be replaced at the Heroes Memorial monument stairs, Heroes Memorial fire escape and the Heroes Memorial Annex fire escape. The 2006 IBC Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
0244STR1 | SEISMIC RETROFIT | 0244 | This building is an unreinforced masonry structure which requires seismic strengthening to meet current life safety codes. An initial study was done under CIP 07-M46 which provided detailed recommendations for a seismic retrofit. The planning and design will be requested under CIP 09-P04and the construction cost will be requested for the 2011 CIP. The estimate is for the construction costs only. This project should coincide with a complete remodel of the interior of the building. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 489720
0306ENR1 | LIGHTING UPGRADE | 0306 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69300
9917SIT1 | SITE DRAINAGE PROJECT | 9917 | There are several site drainage problems around the complex including flooding from the street to the West, improper roof drains and window wells without drains. The site is fairly flat and the grading slopes toward the building in several locations, most noticeably at the Heroes Memorial and Heroes Memorial Annex. Several reports of water seeping into the building's basement have been reported over the past few years. Some of the roof drains do not drain to the storm drain system resulting in pooling against the buildings and leaking into the building. There have been reports of water accumulation in several of the window wells on the Attorney General's Office due to drainage problems. This project recommends grading the site, and installing a system of drains, catch basins and storm drain connections to minimize recurring flooding, water movement and accumulations. It would be most beneficial if this project be incorporated with the fence project that is also included in this report. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL OFFICES COMPLEX | 9917 | AttGen | B&G |  | Carson City | 0 |  | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 250000
0244SFT2 | INSTALL EMERGENCY EGRESS LIGHTING | 0244 | There is inadequate emergency egress lighting in the building and the existing lights do not meet current standards. This project would provide for the purchase and installation of emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 5400
0261PLM1 | MODIFY ROOF DRAIN PLUMBING | 0261 | The majority of the roof drain plumbing system is located inside the building and it exits the building near ground level. The building has decorative spouts mounted to the building exterior that do not do a very good job of draining the water away from the building. These drains also allow the wind to push the drain water back against the building. Poor site drainage causes many problems with buildings such as water infiltration. This project recommends that the drains be modified to deliver the drain water away from the building and that collection drain systems be installed to catch the roof drain water and carry it to the storm drain system. This project would be best served if coupled with the site drainage project located in the site report for this building. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | FRANKIE SUE DEL PAPA BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 14680 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 30000
0306SFT4 | INSTALL MAGNETIC DOOR HOLDERS | 0306 | There are doors in the AG's office which have been propped open. In the event of a fire or other emergency, these doors would remain open, creating a possible hazard. This project recommends the installation of magnetic door holders, with closers, tied into the fire alarm, which would hold the doors open. In the event of a fire, the alarm would release the doors, allowing them to close. This applies to the one hour doors into the corridors. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 20000
0306ADA3 | REPLACE STAIR HANDRAILS | 0306 | The handrails in several stairwells do not meet code for safety or accessibility. The gripping surfaces are incorrect, the handrails do not have proper returns and they are not continuous from the top to bottom of the stairs. The east stairwell near the main entrance has an overhead hazard at the cane detection area under the stairs. This project recommends the installation of handrails on both sides of stairwells, with proper returns and supports as well as installing a barrier under the stairs. IBC - 2006 Section 1012 and ADAAG 4.4.2 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | ATTORNEY GENERAL'S OFFICE | 9917 | AttGen | B&G |  | Carson City | 1937 | 23100 | 2008-12-10 | Immediate to Two Years | Currently Critical | 1 | 35000
2311SFT4 | REPLACE STAIR HANDRAILS | 2311 | The handrails in several stairwells do not meet code for safety. The gripping surfaces are incorrect, the handrails do not have proper returns and they are not continuous from the top to bottom of the stairs. This project recommends the installation of handrails on both sides of stairwells, with proper returns and supports. IBC - 2006 Chapter 10 - Section 1012 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL ANNEX | 9917 | AttGen | B&G |  | Carson City | 1951 | 6819 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0244SFT3 | REPLACE INTERIOR STAIR HANDRAILS | 0244 | The handrails in several stairwells do not meet code for safety. The gripping surfaces are incorrect, the handrails do not have proper returns and they are not continuous from the top to bottom of the stairs. This project recommends the installation of handrails on both sides of stairwells, with proper returns and supports. IBC - 2006 Section 1012 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0244ENR1 | LIGHTING UPGRADE | 0244 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/09/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/10/2008. | HEROES MEMORIAL BUILDING | 9917 | AttGen | B&G |  | Carson City | 1920 | 13992 | 2008-12-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41976
0235INT2 | INTERIOR FINISHES | 0235 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 273890
9918SIT3 | SLURRY SEAL ASPHALT PAVING | 9918 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving including the access road and parking area on the south side of the Capitol. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 10,000 square feet of asphalt area was used to generate this estimate. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2011-03-23 | Four to Ten Years | Long-Term Needs | 3 | 7500
9918ADA1 | SIDEWALK / CONCRETE REPAIRS | 9918 | Some of the sidewalks around the building are deteriorated and failing and some do not meet ADA requirements. In some areas there is extensive cracking, heaving and settling. The concrete landings at the bottom of the three steel exterior exit stairs are too small and one is missing. This project addresses removal and replacement of existing sidewalks as needed particularly for the ADA path of travel on the east side of the site and installing new landings for the exit stairs. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 15000
0203EXT2 | EXTERIOR FINISHES | 0203 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and sealing the sandstone masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49320
0235EXT1 | EXTERIOR FINISHES | 0235 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, cleaning and pointing the sandstone masonry as needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 273890
9918SIT4 | DRAINAGE IMPROVEMENTS | 9918 | There is a drainage problem on the west side of the Capitol building resulting in water leaking into the basement. Two roof drain downspouts and landscaping are just outside of the subject area and it is suspected that the water is pooling up in this area instead of running off away from the building. It is recommended to extend the downspouts underground to a dry well or similar drainage feature to carry the water away from the building and regrade the landscaped area to provide a positive slope away from the building. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 5000
0235INT3 | JANITORS CLOSET REPAIRS | 0235 | The mop sink in the basement Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0235ADA3 | ADA RESTROOM UPGRADES | 0235 | The building has several ADA accessible restrooms, some of which are not fully compliant. For instance, the unisex ADA restroom on the 2nd floor is missing pipe protection under the sink and the water closet is lower than the required 17" height for the seat. Also, the countertop in the Men's restroom on the 1st floor does not meet height requirements and the water closet flush handle in the Men's restroom in the basement is on the wrong side of the water closet. This project would provide funding for these specific repairs and any other necessary upgrades to bring the restrooms into full compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 15000
9918SFT1 | CONCRETE STAIR REPAIRS | 9918 | The south side concrete stairs and landing at the breezeway between the Annex and Capitol are severely deteriorated. Spalling and cracking have occurred to the extent that the stairs need to be replaced and the landing resurfaced. It is currently a tripping hazard especially during inclement weather. This project addresses removal and replacement of the entire stair structure and resurfacing the concrete landing. The existing handrails do not meet current building codes and may need to be replaced in kind or altered to bring them into compliance. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. Section 1012 of the 2006 IBC was referenced for this project. | NEVADA STATE CAPITOL SITE | 9918 | Admin | PubWorks | B&G | Carson City | 0 |  | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 15000
0203INT2 | INTERIOR FINISHES | 0203 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49320
0235ADA2 | ADA SIGNAGE | 0235 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/03/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/23/2011. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 3000
0203ADA4 | ADA SIGNAGE | 0203 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/03/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/23/2011. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 1500
0235ADA1 | ADA ACCESSIBLE COUNTER | 0235 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The security desk near the entrance to the building has a counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/03/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/23/2011. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 1500
0235EXT2 | REMOVE VINE GROWTH FROM BUILDING | 0235 | There is extensive vine growth on the exterior sandstone masonry of the building. This will damage the sandstone masonry and grout joints. This project will provide for the removal of all vines from the exterior of the building including the actual plant itself along the perimeter of the structure. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 2000
0235ELE2 | ELEVATOR UPGRADES | 0235 | The elevator was built in 1979 and requires periodic repairs. It is currently due for a refurbishment of all mechanical parts to maintain the elevator in a safe working order. The maintenance staff has acquired a bid for the work in the amount of $190,000 which also includes a regenerative elevator drive that generates its own electricity. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 190000
0235SFT5 | GUARD REPAIRS | 0235 | The guardrail on the 2nd floor of the building around the stairwell is older and does not meet code for safety. Being a historic building, the guard is only required to meet a level of protection for a means of egress. It does not meet this level of protection because it is not at least 42 inches in height. This project provides for attaching a new top rail to the existing guard in order to raise the overall height to more than 42 inches. The new rail will be designed and built to match the style of the existing historic guard. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. Section 1003.1 of the 2006 International Existing Building Code and section 1013.2 of the 2006 International Building Code were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 5000
0203ADA1 | ADA KITCHENETTE UPGRADES | 0203 | The kitchenette in the employee break room does not entirely meet the Americans with Disabilities Act (ADA) requirements. Minor modifications are necessary. This project would provide funding for upgrades to the kitchenette to remove architectural barriers. These items may include a new sink, modifications to the casework to provide clearances, hardware, relocating the microwave and moving furniture to provide clearances. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 2500
0235ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0235 | This building contains a water fountain on each floor. The basement floor and 1st floor drinking fountains are not accessible. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of two new accessible fixed high/ low ADA drinking fountains for the basement and 1st floor. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 8000
0203PLM1 | WATER HEATER REPLACEMENT | 0203 | There is a 30 gallon electric water heater in the building that was installed in 2005. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | STATE CAPITOL ANNEX | 9918 | Admin | PubWorks | B&G | Carson City | 1905 | 9864 | 2011-03-23 | Four to Ten Years | Long-Term Needs | 3 | 2500
0235PLM1 | WATER HEATER REPLACEMENT | 0235 | There is a 100 gallon natural gas-fired water heater in the basement mechanical room. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0235INT4 | BASEMENT CARPET REPLACEMENT | 0235 | The carpet in the staff offices in the Basement is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0235SFT1 | GFCI DUPLEX OUTLET REPLACEMENTS | 0235 | There are two outlets in the Governor's Office kitchen which are not GFCI. One is above the countertop near the sink and the other is in the cabinet directly under the sink. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of two GFCI duplex outlets. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 600
0235SFT4 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0235 | There are two exit stairwells on the west side of the building. The handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect, they do not have proper returns, they are on only one side of the stairway and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper gripping surfaces, returns and supports. Removal and disposal of the existing railing is included. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. NRS 338.180, 2006 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NEVADA STATE CAPITOL | 9918 | Admin | PubWorks | B&G | Carson City | 1870 | 54778 | 2011-03-23 | Immediate to Two Years | Currently Critical | 1 | 15000
9919SIT2 | SLURRY SEAL ASPHALT PAVING | 9919 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site-wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 102,500 square feet of asphalt area was used to generate this estimate. | PLUMB LANE READINESS CENTER SITE | 9919 | Military | NNG |  | Reno | 1965 |  | 2010-07-08 | Four to Ten Years | Long-Term Needs | 3 | 76875
2042SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2042 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 45828
2043SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2043 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 10444
2043SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2043 | There is no emergency egress lighting in the building and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 1000
2043ENR1 | WINDOW REPLACEMENT | 2043 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2043EXT1 | EXTERIOR FINISHES | 2043 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, painting the stucco eaves, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING 2 | 9919 | Military | NNG |  | Reno | 1965 | 2611 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13055
2044EXT2 | EXTERIOR DOOR REPLACEMENT | 2044 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the three double door assemblies with new metal doors, frames, and hardware. Removal and disposal of the existing doors is included in this estimate. | STORAGE BUILDING 1 | 9919 | Military | NNG |  | Reno | 1980 | 405 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2044EXT1 | EXTERIOR FINISHES | 2044 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and painting the concrete masonry and caulking of the flashing, fixtures, and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING 1 | 9919 | Military | NNG |  | Reno | 1980 | 405 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2025
2042ADA7 | ADA DOOR UPGRADE | 2042 | The exterior entrance door on the east side of the building is on an accessible path of travel. It has a power door opener installed on it which has been disabled for security reasons. Without the power door opener, the entrance is not accessible. This project would provide for replacement of the doors to provide an accessible entrance including new ADA compliant door hardware, threshold, signage and space requirements. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. The other option would be to activate the power door opener which must open both door leaves along with signage identifying ADA access which may cost less than door replacement. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 5000
2042ADA6 | ADA UNISEX RESTROOM UPGRADE | 2042 | The designated unisex ADA accessible restroom is not fully compliant. There is no pipe protection, the toilet paper dispenser is not in the correct location, and it is missing a grab bar. A partial retrofit is necessary. This project would provide funding to bring the restroom into full ADA compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 2000
9919SIT3 | SIDEWALK REPLACEMENT | 9919 | The sidewalks serving the building are deteriorated and failing. In some areas, settling has caused changes in elevation in excess of 1/2" and there are cracks in many locations. This project addresses removal and replacement of existing sidewalks and the concrete patio in the rear of the building. 2,500 SF of 4" thick concrete sidewalk was used for this estimate. | PLUMB LANE READINESS CENTER SITE | 9919 | Military | NNG |  | Reno | 1965 |  | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2042PLM1 | REMODEL RESTROOMS | 2042 | The existing Men's and Women's restrooms are original to building and are in need of upgrades. This project would provide for the remodeling of both restrooms including but not limited to new toilets, shower modifications, sinks, fixtures, hardware, and floor and wall finishes. It is also recommended that these restrooms become ADA accessible but there already is a unisex ADA restroom present in the building which would provide minimum ADA restroom facilities after the proposed project for upgrading that restroom is complete. This cost estimate does not include an ADA upgrade which may increase the construction cost. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2042SFT4 | EXTERIOR LANDING MODIFICATION | 2042 | The entrance on the south side of the building does not have a proper exterior landing, stairway, and is missing handrails as required by the 2006 IBC, Chapter 10, Section 1008, 1009 and 1012. Also the exit door from the drill hall area swings out over a step. This project would provide for the reworking of the exterior landing and steps to provide a proper landing and stairs including handrails at the south entrance, and adding a new concrete landing at the drill hall exit door. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 3500
2042EXT2 | EXTERIOR FINISHES | 2042 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the masonry, priming and painting the stucco, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Also included is the repairing of the concrete roof deck overhang at the damaged areas. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57285
2042SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2042 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 80199
2042ENR1 | REPLACE OVERHEAD COILING DOOR | 2042 | The existing overhead coiling door in the drill hall is damaged and is not insulated resulting in increased energy usage. This project would provide for installation of a new power operated insulated overhead coiling door. Removal of the existing door is included in this estimate. A 14'x12' door was used for this estimate. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9919ADA2 | ADA RAMP UPGRADE | 9919 | This facility has an ADA accessible ramp on the east side of the Readiness Center. This ramp is on the accessible path of travel from the accessible parking spaces to the Readiness Center. The ramp does not have proper landings, the handrails are not compliant, and it is missing edge protection. This project would provide for an upgrade to the ramp to make it fully ADA compliant. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER SITE | 9919 | Military | NNG |  | Reno | 1965 |  | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 25000
2042ADA4 | ADA SIGNAGE | 2042 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Immediate to Two Years | Currently Critical | 1 | 3000
2042INT2 | INTERIOR FINISHES | 2042 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57285
2042INT1 | REPLACE CARPETING | 2042 | The carpet in the facility is worn from age and normal use and is in need of replacement. This project would provide for the installation of about 2,000 square feet of commercial grade carpet. Removal and disposal of the old carpet is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/08/2010. | PLUMB LANE READINESS CENTER | 9919 | Military | NNG |  | Reno | 1965 | 11457 | 2010-07-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2045HVA1 | BOILER REPLACEMENT | 2045 | The building has four hot water boilers servicing the building. Two boilers service the North Hangar and the other two service the South Hangar. Of the two in each Hangar, one is original to the building. The life expectancy of these units is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boilers, controls and mixing valve and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 1,460 MBH output hot water boiler. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
2408ADA2 | ADA RESTROOM REMODEL | 2408 | The vanities in the Men's and Women's restroom are not accessible and should be replaced with an ADA accessible countertop, sink, faucet and plumbing jacket. There are also showers present which are not compliant. This project also includes remodeling both showers into ADA compliant showers including fixtures. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 16000
2408ADA1 | ADA SIGNAGE | 2408 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 3500
2408INT1 | INTERIOR FINISHES | 2408 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55655
2408EXT1 | EXTERIOR FINISHES | 2408 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It appears that the building was not properly sealed at the time of construction. There is evidence of water penetration on the inside of the CMU walls. It is recommended that this project be implemented as soon as possible and is recommended on a cyclical basis based on environmental conditions. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 111310
2909EXT1 | EXTERIOR FINISHES | 2909 | This wood framed shade ramada covers picnic tables and a barbecue. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting the structure and should be done on a cyclical basis based on environmental conditions. | SHADE RAMADA | 9920 | Military | NNG |  | Stead | 0 | 450 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 900
2910INT1 | INTERIOR FINISHES | 2910 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | GUARD SHACK | 9920 | Military | NNG |  | Stead | 0 | 64 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
9920SIT3 | SLURRY SEAL ASPHALT PAVING | 9920 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, aprons and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 1,150,000 square feet of asphalt area was used to generate this estimate. | SEN. HARRY REID READINESS & TRAINING CTR | 9920 | Military | NNG |  | Stead | 0 |  | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 862500
2408INT2 | JANITORS CLOSET REPAIRS | 2408 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2041EXT2 | EXTERIOR FINISHES | 2041 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 316790
2041PLM1 | WATER HEATER REPLACEMENT | 2041 | The average life span of a water heater is eight to ten years. The existing 80 gallon natural gas fired water heater in the building is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heater and installation of a new natural gas fired water heater. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2040EXT1 | EXTERIOR FINISHES | 2040 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 29000
2040SIT1 | ASPHALT REPLACEMENT | 2040 | The asphalt around the building is failing, with significant alligatoring, settling and cracks observed. It was not included in the 2007 asphalt replacement for the rest of the site. This project covers the removal and replacement of the existing asphalt for parking and site access. Striping for safety, parking and loading zones is included in this estimate. 16,500 square feet was used to generate this estimate. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 165000
2040ADA1 | ADA SIGNAGE | 2040 | The building is lacking ADA signage. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 2000
2040PLM1 | WATER HEATER REPLACEMENT | 2040 | The average life span of a water heater is eight to ten years. The existing 50 gallon natural gas fired water heater in the building is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heater and installation of a new natural gas fired water heater. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2910EXT1 | EXTERIOR FINISHES | 2910 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | GUARD SHACK | 9920 | Military | NNG |  | Stead | 0 | 64 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 320
2055EXT1 | EXTERIOR FINISHES | 2055 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE #5 | 9920 | Military | NNG |  | Stead | 1984 | 500 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 800
2047EXT1 | EXTERIOR FINISHES | 2047 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | AVIATION STORAGE #1 | 9920 | Military | NNG |  | Stead | 1987 | 960 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 1920
2048EXT1 | EXTERIOR FINISHES | 2048 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | AVIATION STORAGE #2 | 9920 | Military | NNG |  | Stead | 1987 | 960 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 1920
2049EXT1 | EXTERIOR FINISHES | 2049 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE BUILDING #10 | 9920 | Military | NNG |  | Stead | 2006 | 3300 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 6600
2050EXT1 | EXTERIOR FINISHES | 2050 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | AVIATION STORAGE #8 | 9920 | Military | NNG |  | Stead | 1987 | 3300 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 6600
2051EXT1 | EXTERIOR FINISHES | 2051 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | POL BUILDING | 9920 | Military | NNG |  | Stead | 1992 | 630 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 2200
2052EXT1 | EXTERIOR FINISHES | 2052 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE #1 | 9920 | Military | NNG |  | Stead | 1994 | 1260 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 2520
2408SFT1 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 2408 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 3500
2054EXT1 | EXTERIOR FINISHES | 2054 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HAZARDOUS WASTE STORAGE #4 | 9920 | Military | NNG |  | Stead | 1991 | 252 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 504
2408PLM1 | WATER HEATER REPLACEMENT | 2408 | The average life span of a water heater is eight to ten years. The existing 100 gallon natural gas fired water heater in the building is reaching the end of its expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heater and installation of a new 100 gallon natural gas fired water heater. | OSA FLIGHT DETACHMENT 45 | 9920 | Military | NNG |  | Stead | 2000 | 11131 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2046EXT1 | EXTERIOR FINISHES | 2046 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | PHYSICAL TRAINING | 9920 | Military | NNG |  | Stead | 1992 | 1632 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 3264
2046INT1 | INTERIOR FINISHES | 2046 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PHYSICAL TRAINING | 9920 | Military | NNG |  | Stead | 1992 | 1632 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8160
2046INT2 | RESTROOM REMODEL | 2046 | The restroom in the building was out of service at the time of the survey. It is original to the building and is due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | PHYSICAL TRAINING | 9920 | Military | NNG |  | Stead | 1992 | 1632 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2045EXT1 | EXTERIOR FINISHES | 2045 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 361460
2045ADA1 | ACCESSIBLE WATER FOUNTAIN | 2045 | This building has three water fountains. IBC-2006 Section 1109.5 states that where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of two ADA compliant high/ low water fountains. The installation of the water fountains must comply with ICC/ANSI A117.1-2003 and the most current edition of the Americans with Disabilities Act Accessibility Guidelines (ADAAG). | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 6000
2045PLM1 | WATER HEATER REPLACEMENT | 2045 | The average life span of a water heater is eight to ten years. The two existing 75 gallon natural gas fired water heaters and the 65 gallon natural gas fired water heater in the building have reached the end of their expected life and should be scheduled for replacement. This project would provide for the removal and disposal of the old water heaters and installation of three new natural gas fired water heaters. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2045SFT1 | EGRESS LIGHTING UPGRADE | 2045 | The existing egress lights in this building are older types or are missing altogether. Egress lighting should be installed and/or replaced to provide illumination along the egress route per 2006 IBC Chapter 10, Section 1006. This project would provide for the installation of egress lighting including connections to existing utilities in the office support area of the facility. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 7500
2053EXT1 | EXTERIOR FINISHES | 2053 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, sealing metal siding penetrations or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | PUMPHOUSE | 9920 | Military | NNG |  | Stead | 1984 | 480 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 960
2045INT1 | INTERIOR FINISHES | 2045 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 361460
9920SFT1 | INSTALL MOTORIZED GATES | 9920 | The site has a perimeter fence that has vehicle access gates off Army Aviation Drive. They are mechanically operated, have been problematic, and are difficult to open and close. This project recommends the gates be upgraded to a motorized track system that can handle heavy equipment traffic. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | SEN. HARRY REID READINESS & TRAINING CTR | 9920 | Military | NNG |  | Stead | 0 |  | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2041EXT1 | REPLACE ROOF | 2041 | The roof was installed in 1997 and is in fair shape. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed in 2012 to be consistent with the roofing program and the end of the warranty period and prevent future damage to the interior finishes. This project applies to the single-ply membrane system only. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Four to Ten Years | Long-Term Needs | 3 | 675000
2045ENV1 | INSTALL CARBON MONOXIDE DETECTORS | 2045 | Portions of the facility are served by direct fired gas furnaces. These devices can put out elevated levels of carbon monoxide. This project would install carbon monoxide detectors in all areas served by the direct fired furnaces with both alarms and furnace interlocks. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | ARMY AVIATION SUPPORT FACILITY | 9920 | Military | NNG |  | Stead | 1984 | 72292 | 2008-07-17 | Immediate to Two Years | Currently Critical | 1 | 5000
2041INT1 | INTERIOR FINISHES | 2041 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 316790
2040INT1 | INTERIOR FINISHES | 2040 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and / or sealed at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FIELD MAINTENANCE SHOP 2 | 9920 | Military | NNG |  | Stead | 1994 | 5800 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29000
2041INT2 | REPLACE CARPET FLOORING | 2041 | The carpet is showing signs of extreme wear and has reached the end of its useful life. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. Approximately half of the flooring in the building is carpet. This project or a portion thereof was previously recommended in the FCA report dated 08/27/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/17/2008. | WASHOE COUNTY TRAINING CENTER | 9920 | Military | NNG |  | Stead | 1997 | 63358 | 2008-07-17 | Two to Four Years | Necessary - Not Yet Critical | 2 | 158395
1318INT1 | INTERIOR FINISHES | 1318 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3795
1165EXT1 | EXTERIOR FINISHES | 1165 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 12000
2386EXT1 | EXTERIOR FINISHES | 2386 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLACKSMITH SHOP | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 195 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1950
2386EXT2 | ROOF REPLACEMENT | 2386 | The rolled asphalt roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | BLACKSMITH SHOP | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 195 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2925
2385EXT1 | EXTERIOR FINISHES | 2385 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUCKLAND STATION KIOSK | 9921 | CNR | Parks |  | Fort Churchill | 2001 | 16 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175
1318EXT1 | EXTERIOR FINISHES | 1318 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7590
2402EXT1 | EXTERIOR/ INTERIOR FINISHES | 2402 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT RESTROOM #1 - BUCKLAND | 9921 | CNR | Parks |  | Fort Churchill | 2007 | 196 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 830
1318EXT2 | ROOF REPLACEMENT | 1318 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11385
1318EXT3 | EXTERIOR DOOR REPLACEMENT | 1318 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear and is not wide enough to accommodate the needs of the staff. This project would provide for widening the doorway to 36" and replacing the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1318ADA1 | ADA RESTROOM UPGRADE | 1318 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 25000
2403EXT1 | EXTERIOR/ INTERIOR FINISHES | 2403 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT RESTROOM #2 - GROUP CAMP | 9921 | CNR | Parks |  | Fort Churchill | 2000 | 196 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 830
1318ENR1 | LIGHTING UPGRADE | 1318 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1898
2988EXT1 | EXTERIOR/ INTERIOR FINISHES | 2988 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT FIRE PROTECTION PUMP HOUSE-BUCKLAND | 9921 | CNR | Parks |  | Fort Churchill | 2006 | 220 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 2200
1165INT1 | INTERIOR FINISHES | 1165 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next four to five years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 6000
1318ADA2 | ADA SIGNAGE | 1318 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. | SHOP/PUBLIC RESTROOM BUILDING | 9921 | CNR | Parks |  | Fort Churchill |  | 759 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 600
0964CUL1 | OVEN REPLACEMENT | 0964 | There is a propane fired oven in the kitchen that is not operating. It has reached the end of it's useful and expected life and should be scheduled for replacement. This project would provide for a new oven/ cook top to be installed including all required connections to utilities. The estimate includes removal and disposal of the old oven. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0965HVA1 | EVAPORATIVE COOLER REPLACEMENT | 0965 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0964EXT2 | ROOF REPLACEMENT | 0964 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32490
0964EXT4 | SLIDING GLASS DOOR REPLACEMENT | 0964 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0964EXT5 | SCREEN DOOR REPLACEMENT | 0964 | The screen door at the entry is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the screen door. Removal and disposal of the existing door is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0964INT2 | RESTROOM REMODEL | 0964 | The restroom in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2405EXT1 | EXTERIOR FINISHES | 2405 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0964HVA1 | EVAPORATIVE COOLER REPLACEMENT | 0964 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2405SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 2405 | The existing wood exterior stairs at the entry and the concrete stairs going to the basement are lacking handrails as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for a tubular steel framed handrail to be installed at both stairs. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 7500
0964SFT2 | EXTERIOR LANDING INSTALLATION | 0964 | Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. There are two doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for each door. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 5000
1165HVA1 | AIR CONDITIONER REPLACEMENT | 1165 | Two air conditioners are installed in this building that have reached the end of their useful and expected life. This project would provide for two new air conditioners to be installed including all required connections to utilities. The estimate includes removal and disposal of the old equipment. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2406EXT1 | EXTERIOR FINISHES | 2406 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry, staining the wood members and caulking of the penetrations. It is recommended that the building be sealed, stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #2 - RESIDENCE #1 | 9921 | CNR | Parks |  | Fort Churchill | 1980 | 64 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1165SIT1 | VEHICLE GATE REPAIRS | 1165 | The vehicle gate on the side of the building is damaged and should be scheduled for repairs. The hinges have broken away from the concrete wall and the gate is currently inoperable. This project would provide for repairing the concrete wall and reattaching the vehicle gate. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2405INT1 | INTERIOR FINISHES | 2405 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2405EXT2 | EXTERIOR DOOR REPLACEMENT | 2405 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | PUMP HOUSE #1 - RANGER RESIDENCE | 9921 | CNR | Parks |  | Fort Churchill | 1997 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0964EXT6 | CHIMNEY REPLACEMENT | 0964 | The metal chimney flue is original to the building and should be scheduled for replacement. The flue does not properly vent the wood burning fireplace. This project would provide for the replacement of the flue and related chimney accessories. Removal and disposal of the existing materials is included in this estimate. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 2500
9921ADA2 | RUINS ADA ACCESS PROGRAM ACCESSIBILITY | 9921 | The Fort Churchill ruins are open to the public for viewing and historic education. There is no designated ADA access to this area. This project would provide for an ADA accessible location inside of the public area of the Museum/ Visitor Center for an audio/ visual (A/V) presentation of the ruins which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document a typical walking tour of the ruins and purchase and installation of all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. The 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | FORT CHURCHILL STATE PARK | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 20000
1165INT2 | FLOORING REPLACEMENT | 1165 | The carpet and VCT (vinyl composite tile) flooring in the office areas are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the carpet and VCT and installation of new carpet and 12x12 VCT with a 6" base. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0488SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0488 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 9100
0488SEC1 | SECURITY SYSTEM ASSESSMENT | 0488 | The security system has been disabled due to too many false alarms. It is recommended that a security system specialist evaluate the system to determine any deficiencies in order to bring the system back on line. Future projects would be based on this report. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0488HVA1 | HVAC EQUIPMENT INSTALLATION | 0488 | The building does not have any HVAC equipment other than wood burning stoves. It is recommended to condition this building to provide comfort for visitors and preserve the displays and artifacts in the building. This project would provide for the installation of a central HVAC system for the building. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39000
0488ADA2 | EXTERIOR HANDRAIL REPLACEMENT | 0488 | The handrails on the stairs and ramps around the exterior of the building are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and/ or they are installed on only one side of the stair or ramp. This project recommends replacement of the handrails in accordance with NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003. The removal and disposal of the existing handrails is included in the estimate. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 6000
0488ENR1 | LIGHTING UPGRADE | 0488 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3250
0487EXT2 | ROOF REPLACEMENT | 0487 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | ADOBE BRICK STORAGE SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1981 | 516 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6192
0488ADA1 | ADA SIGNAGE | 0488 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 750
0502EXT1 | COMFORT STATION REPLACEMENT | 0502 | This comfort station was built in 1979. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. The new restroom shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | ADA ACCESSIBLE COMFORT STATION #2 | 9921 | CNR | Parks |  | Fort Churchill | 1979 | 140 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0501EXT1 | COMFORT STATION REPLACEMENT | 0501 | This comfort station was built in 1979. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. An ADA accessible parking space and route of travel to the comfort station is included in this estimate. The new restroom, parking space and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | ADA ACCESSIBLE COMFORT STATION #1 | 9921 | CNR | Parks |  | Fort Churchill | 1979 | 140 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0500EXT1 | COMFORT STATION REPLACEMENT | 0500 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station to be located near the ADA accessible parking space. An ADA accessible route of travel from the parking space to the comfort station is included in this estimate. The new restroom and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #4 - PICNIC | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0492EXT1 | COMFORT STATION REPLACEMENT | 0492 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station to be located near the ADA accessible parking space. An ADA accessible route of travel from the parking space to the comfort station is included in this estimate. The new restroom and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #3 - CAMPGROUND | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0491EXT1 | COMFORT STATION REPLACEMENT | 0491 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station to be located near the ADA accessible parking space. An ADA accessible route of travel from the parking space to the comfort station is included in this estimate. The new restroom and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #2 - CAMPGROUND | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
0486EXT1 | COMFORT STATION REPLACEMENT | 0486 | This comfort station was built in 1963. It is dilapidated and deteriorating and no longer meets accessibility guidelines. It is recommended that the building be demolished and replaced with a new restroom facility. This project would provide for the installation of a precast CXT or similar unisex comfort station in the same location as the existing building. An ADA accessible parking space and route of travel to the comfort station is included in this estimate. The new restroom, parking space and route of travel shall be compliant with the 2006 IBC, ICC/ANSI A117.1 - 2003, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG). | COMFORT STATION #1 - GROUP CAMP | 9921 | CNR | Parks |  | Fort Churchill | 1963 | 147 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0487EXT1 | EXTERIOR FINISHES | 0487 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADOBE BRICK STORAGE SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1981 | 516 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0541EXT1 | EXTERIOR FINISHES | 0541 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUCKLAND STATION HISTORIC BUILDING | 9921 | CNR | Parks |  | Fort Churchill | 1870 | 4056 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 40560
1165EXT3 | OVERHEAD DOOR REPLACEMENT | 1165 | There are three 8'x8' overhead coiling doors on the building, one of which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. Removal and disposal of the existing door is included in this estimate. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0965EXT2 | EXTERIOR FINISHES | 0965 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1165ENR1 | LIGHTING UPGRADE | 1165 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0965EXT3 | ROOF REPLACEMENT | 0965 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
1165INT3 | NONABSORBANT FINISHES | 1165 | 2006 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 3000
0488SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0488 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 18200
0963EXT2 | ROOF REPLACEMENT | 0963 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | CANNON SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 400 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1165EXT2 | ROOF REPLACEMENT | 1165 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | PARK SHOP/OFFICE | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 1200 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0541INT1 | INTERIOR FINISHES | 0541 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUCKLAND STATION HISTORIC BUILDING | 9921 | CNR | Parks |  | Fort Churchill | 1870 | 4056 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20280
0490EXT1 | EXTERIOR FINISHES | 0490 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting the wood supports and painting the masonry. It is recommended that the building be painted, sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP RAMADA | 9921 | CNR | Parks |  | Fort Churchill | 1976 | 1430 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 3575
0490EXT2 | ROOF REPLACEMENT | 0490 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | GROUP RAMADA | 9921 | CNR | Parks |  | Fort Churchill | 1976 | 1430 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17160
0488EXT1 | EXTERIOR FINISHES | 0488 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 13000
0488INT1 | INTERIOR FINISHES | 0488 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
0488EXT2 | ROOF REPLACEMENT | 0488 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | MUSEUM/VISITOR CENTER | 9921 | CNR | Parks |  | Fort Churchill | 1935 | 1300 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15600
0963EXT1 | EXTERIOR/ INTERIOR FINISHES | 0963 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building. Included in the cost is power washing, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CANNON SHELTER | 9921 | CNR | Parks |  | Fort Churchill | 1992 | 400 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 4000
0965SFT2 | EXTERIOR LANDING INSTALLATION | 0965 | Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. There are two doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for each door. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 5000
1474EXT1 | DISCONTINUE BUILDING USE | 1474 | The residence contains numerous code and safety issues including, but not limited to an upper level exterior door without a deck or stairway, rodent infestation, broken or missing doors and windows, possible asbestos contamination and broken or missing electrical fixtures. This project recommends that the residence be secured by boarding up exterior openings and weather proof the exterior to prevent further damage. The electrical service should be disconnected and the public/personnel should not be allowed to enter or use this building. This project or a portion thereof was previously recommended in the FCA report dated 03/07/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #4 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1945 | 1380 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 10000
1413INT1 | INTERIOR FINISHES | 1413 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10640
0964INT1 | INTERIOR FINISHES | 0964 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10830
0965INT1 | INTERIOR FINISHES | 0965 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0964EXT1 | EXTERIOR FINISHES | 0964 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21660
1413EXT2 | EXTERIOR FINISHES | 1413 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 21280
0539EXT1 | EXTERIOR FINISHES | 0539 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. The wood siding is failing and will no longer hold additional coats of paint. The stone chimney is also failing and will collapse if not replaced soon. Included in the cost is replacing and painting the wood siding, replacing the stone chimney and sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be repaired, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0539HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0539 | An evaporative cooler is installed on the roof of this building. It is reaching the end of it's useful and expected life and should be scheduled for replacement. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 3000
0490INT1 | CONCRETE REPLACEMENT | 0490 | The concrete slab floor in the structure is in need of replacement. Settling and heaving has caused cracking and spalling of the concrete. This project would provide for the removal and replacement of the concrete floor. 1430 SF of 4" thick concrete was used for this estimate. | GROUP RAMADA | 9921 | CNR | Parks |  | Fort Churchill | 1976 | 1430 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 14300
9921ENV3 | PEST CONTROL CONTRACT | 9921 | Many of the buildings throughout the site are in need of pest control. Mice, rats, pigeons and other pests are damaging the buildings and leaving droppings. Due to the potential risk of disease, this project provides for treatment, clean up and prevention of these pests by a licensed pest control company. It is recommended that this project be scheduled on a cyclical basis to maintain control of the pests. | FORT CHURCHILL STATE PARK | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9921SFT1 | FIRE HOSE REPLACEMENT | 9921 | There are several fire hose sheds around the site. Three of the hoses are cracked and leaking and are due for replacement. This project would provide for the replacement of three 200 foot by 1.5 inch diameter fire hoses. | FORT CHURCHILL STATE PARK | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1500
1413SFT1 | INSTALL SMOKE DETECTORS | 1413 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
9921SIT2 | BRIDGE REPAIRS | 9921 | There are two wooden vehicle bridges on the site that are in need of repairs. One bridge is near the entrance to the campground and one is near the entrance to the group area. Both bridges are structurally sound, but the top layer of lumber is deteriorating and should be scheduled for replacement. This project would provide for the removal and replacement of the deteriorating boards and associated hardware. | FORT CHURCHILL STATE PARK | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 10000
9921SIT1 | RESEAL ASPHALT PARKING AND ROADS | 9921 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 400,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | FORT CHURCHILL STATE PARK | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0539INT3 | REPLACE KITCHEN COUNTERTOPS | 0539 | The countertops in the kitchen are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0539HVA1 | EXHAUST VENT REPAIR | 0539 | The exhaust fan for the restroom currently vents into the attic space. The vent should continue through the roof and exhaust to the outside. This project would provide for the purchase and installation of a new exhaust vent roof jack and additional piping to connect the existing vent to the roof jack. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 500
0539SFT1 | INSTALL SMOKE DETECTORS | 0539 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0539EXT2 | WINDOW REPLACEMENT | 0539 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 14 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0539INT2 | INTERIOR FINISHES | 0539 | The interior finishes are in good condition. It is recommended that the interior walls be painted at least once in the next five to six years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #5 - GHIGLIA RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1950 | 1026 | 2018-10-09 | Four to Ten Years | Long-Term Needs | 3 | 5130
1413SFT2 | EXTERIOR LANDING INSTALLATION | 1413 | Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The rear exterior door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 2500
1413EXT4 | WINDOW REPLACEMENT | 1413 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1413EXT3 | ROOF REPLACEMENT | 1413 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE #3 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2128 | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25536
0965SFT1 | INSTALL SMOKE DETECTORS | 0965 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #1 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 1600 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
0964SFT1 | INSTALL SMOKE DETECTORS | 0964 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 08/08/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/09/2009. | RESIDENCE #2 - DEPAOLI RANCH | 9921 | CNR | Parks |  | Fort Churchill | 1983 | 2166 | 2018-10-09 | Immediate to Two Years | Currently Critical | 1 | 1000
9921ENV2 | RESIDENCE SEPTIC TANK SYSTEM MAINTENANCE | 9921 | There are 4 residences each with a septic tank and associated leach fields. They are in need of pumping to maintain the integrity of the leach lines and fields. This project would provide for the pumping of Residence 1, 2, 3, and 5. Residence 4 is vacant and is not connected to any utilities. It is recommended that this project be scheduled on a cyclical basis based on usage. | FORT CHURCHILL STATE PARK | 9921 | CNR | Parks |  | Fort Churchill | 1860 |  | 2018-10-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0472EXT1 | HISTORIC BUILDING MAINTENANCE | 0472 | The wood and adobe brick structure is over 100 years old and there are numerous areas where the adobe is failing and the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for cleaning, repair and re-pointing of the adobe brick work, sealing the wood, caulking the flashing, fixtures and windows, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADOBE HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1863 | 544 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8160
0470ADA1 | BUILDING REPLACEMENT | 0470 | The restroom is approaching the end of its expected life and should be scheduled for replacement. Although it has an ADA sign on it, it is not compliant with current ADA requirements. This project would provide for the demolition and disposal of the existing structure and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to an ADA accessible parking space. An ADA accessible route of travel from the parking to the comfort station is included in this estimate. | RESTROOM - PICNIC AREA | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0469INT2 | INTERIOR FINISHES | 0469 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 3750
0473EXT1 | EXTERIOR FINISHES | 0473 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FOSSIL HOUSE STORAGE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0469EXT1 | EXTERIOR FINISHES | 0469 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0471EXT1 | HISTORIC BUILDING MAINTENANCE | 0471 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FOSTERS BLACKSMITH SHOP | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 480 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0473EXT2 | ROOF REPLACEMENT | 0473 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. Metal roofing to match fossil house is also an option. This estimate includes removal and disposal of the old roofing. | FOSSIL HOUSE STORAGE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
9922PLM1 | HOSE BIB REPLACEMENTS | 9922 | There are 9 frost-proof hose bibs throughout the campground that have reached the end of their expected life. Many are damaged by freezing temperatures and have active leaks and should be replaced in the next one to two years. This project would provide for the removal and disposal of the existing hose bibs and purchase and installation of new frost proof hose bibs at all 9 locations. | BERLIN ICHTHYOSAUR STATE PARK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 13500
9922EXT2 | WALL REPAIRS - FOSSIL HOUSE AREA | 9922 | The large concrete wall that displays a life size image of an Ichthyosaur next to the Fossil House is due for repairs. It has developed large vertical cracks in several areas and the top is spalling and crumbling. This project provides for filling the cracks and patching the spalled and crumbled areas to protect the display from further damage. | BERLIN ICHTHYOSAUR STATE PARK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9922ADA2 | CAMPGROUND ADA UPGRADES | 9922 | According to proposed US Access Board regulations, a campground with 2-25 camping spaces shall have 2 accessible spaces spaced throughout the campground to provide as many campsite options as possible. Of the 14 available spaces, the campground currently does not have any accessible spaces. Other regulations include 20'-0" wide drive aisles for RV/ tent trailer sites and accessible amenities on an accessible route including grills, picnic tables, fire rings and water & electric utilities. These guidelines are not official at this time, but are expected to be incorporated into the ADAAG soon. This project provides for upgrading two existing campsites to accessible campsites. | BERLIN ICHTHYOSAUR STATE PARK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 20000
9922ADA1 | ADA PARKING SPACES | 9922 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary in seven locations throughout the park to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space at the Visitor's Center/ Park Office, Restroom A - Visitor's Center, Restroom B - Campground, Comfort Station A - Campground, Comfort Station B - Campground, Comfort Station C - Fossil House and the Fossil House. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2011. | BERLIN ICHTHYOSAUR STATE PARK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 21000
9922SFT1 | FIRE DEFENSE UPGRADE | 9922 | In the summer of 2002 the Nevada Division of Forestry performed a Wild Land Fire Risk Assessment on this facility. Several factors are taken into consideration when performing these assessments such as type of building and roofing materials, what kind of water supply is available, fuel density, defensible space, topography, who responds in case of fire, how far away the responding party, is, etc. The Berlin Ichthyosaur Park was given a Risk Assessment Rating of 85 points. This rating is well into the Extreme Danger Category of 75 and above. The Park was also assessed by the State Fire Marshal's office in the summer of 2003. Recommendations from these assessments include thinning and treatment of fuels, removal of ladder fuels, creating defensible space, reseeding, and addition of a water storage tank dedicated to the existing fire suppression hydrant system. Also obtain additional fire fighting apparatus and provide training to park personnel. Address the need for a reliable source of electrical power. Provide secondary emergency egress from park and develop areas of refuge (Safety Zones) for visitors to take shelter in the event of a fire. Develop evacuation/emergency procedures and establish a more dependable means of communication from the Park to local resources. This project or a portion thereof was previously recommended in the FCA report dated 07/28/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2011. | BERLIN ICHTHYOSAUR STATE PARK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 1500000
3101INT1 | INTERIOR FINISHES | 3101 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 7-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2011 | 1112 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 5560
3101EXT1 | EXTERIOR FINISHES | 3101 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2011 | 1112 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 5560
3102EXT1 | EXTERIOR FINISHES | 3102 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #2 GARAGE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2011 | 774 | 2019-06-13 | Four to Ten Years | Long-Term Needs | 3 | 3870
2576EXT1 | EXTERIOR FINISHES | 2576 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEASONAL CABIN #1 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
3104ADA1 | BUILDING REPLACEMENT | 3104 | The restroom is approaching the end of its expected life and should be scheduled for replacement. Although it has an ADA sign on it, it is not compliant with current ADA requirements. This project would provide for the demolition and disposal of the existing structure and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to an ADA accessible parking space. An ADA accessible route of travel from the parking to the comfort station is included in this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | RESTROOM A - VISITORS CENTER | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 36 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2576INT1 | INTERIOR FINISHES | 2576 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SEASONAL CABIN #1 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
2577INT1 | INTERIOR FINISHES | 2577 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SEASONAL CABIN #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
2577EXT1 | EXTERIOR FINISHES | 2577 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEASONAL CABIN #2 | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2006 | 248 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1240
1008EXT1 | HISTORIC BUILDING MAINTENANCE | 1008 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STEVENS HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 462 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6930
1011EXT1 | HISTORIC BUILDING MAINTENANCE | 1011 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MACHINE SHOP | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 2150 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32250
1012EXT1 | HISTORIC BUILDING MAINTENANCE | 1012 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for replacing wood siding and roofing as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BALL MILL | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 1200 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1010EXT1 | HISTORIC BUILDING MAINTENANCE | 1010 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ITALIAN HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 462 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6930
1009EXT1 | HISTORIC BUILDING MAINTENANCE | 1009 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for replacing wood siding and roofing as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOIST SHACK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 336 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 672
1007EXT1 | EXTERIOR/ INTERIOR FINISHES | 1007 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION C - FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1985 | 60 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1006EXT1 | EXTERIOR/ INTERIOR FINISHES | 1006 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION B - CAMPGROUND | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1985 | 60 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1005EXT1 | EXTERIOR/ INTERIOR FINISHES | 1005 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION A - CAMPGROUND | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1985 | 60 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1004EXT1 | HISTORIC BUILDING MAINTENANCE | 1004 | The wood structure is over 50 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing rolled asphalt roofing as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMP SHED | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1954 | 560 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
1003EXT1 | HISTORIC BUILDING MAINTENANCE | 1003 | The wood structure is over 50 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing rolled asphalt roofing as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOBTOWN BOXCAR | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1954 | 300 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1002EXT1 | HISTORIC BUILDING MAINTENANCE | 1002 | The wood structure is over 50 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing rolled asphalt roofing as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMP CABIN | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1954 | 458 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6870
1000EXT1 | HISTORIC BUILDING MAINTENANCE | 1000 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ASSAY OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 576 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8640
1013EXT1 | HISTORIC BUILDING MAINTENANCE | 1013 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PHILLIPS HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 483 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7245
1001EXT1 | HISTORIC BUILDING MAINTENANCE | 1001 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BERLIN MILL | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 9945 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149175
0467INT1 | INTERIOR FINISHES | 0467 | The interior finishes are in fair condition. It is recommended that the interior concrete be sealed, the wood plywood, beams and posts be cleaned and stained and the metal hardware and bolts be tightened or replaced as needed at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and prepped. | FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1966 | 4300 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21500
9922EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9922 | There are 14 wood shade ramadas in the campground which are 120 s.f. each for a total of 3,360 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for staining the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. | BERLIN ICHTHYOSAUR STATE PARK | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 0 |  | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
0467ADA1 | ADA UPGRADES | 0467 | The Fossil House is lacking an accessible path of travel inside the building and to the museum exhibits. The building is open to the public, requiring it to have an accessible path of travel per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible path of travel throughout the museum including an accessible ramp, handrail/guardrails and modifications to the paver walkway to bring the slopes into compliance. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. Alternatively, an ADA accessible location could be provided inside the building for an audio/visual (A/V) presentation of the exhibit areas which are not ADA accessible. | FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1966 | 4300 | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 100000
0467EXT1 | EXTERIOR FINISHES | 0467 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the fiberglass panels, windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FOSSIL HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1966 | 4300 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21500
0468ADA1 | ADA UPGRADES | 0468 | The Visitor's Center/ Park Office is lacking an accessible entrance into the building and path of travel inside the building. The building is open to the public, requiring it to have an accessible entrance and interior path of travel per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible ramp to access the building, accessible door and hardware and accessible path of travel inside the building to all programs, exhibits and areas open to the public. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. The State Historic Preservation Office should be consulted prior to project implementation. | VISITOR'S CENTER/PARK OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 880 | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 15000
0468INT1 | INTERIOR FINISHES | 0468 | The interior finishes are in fair condition. It is recommended that the historic wallpapered walls and ceilings be maintained in a state of arrested decay and the painted walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. | VISITOR'S CENTER/PARK OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 880 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
0468EXT1 | EXTERIOR FINISHES | 0468 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITOR'S CENTER/PARK OFFICE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 880 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
0469PLM1 | WATER HEATER REPLACEMENT | 0469 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0469INT5 | RESTROOM REMODEL | 0469 | The restroom in the residence is in overall poor condition and should be scheduled for a remodel. The finishes, fixtures, cabinets, toilet, shower and exhaust fan are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0469INT4 | KITCHEN REMODEL | 0469 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1032EXT1 | HISTORIC BUILDING MAINTENANCE | 1032 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WATSON HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 483 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7245
0469INT3 | FLOORING REPLACEMENT | 0469 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new sheet vinyl with a 6" base and heavy duty commercial grade carpet in the next 3-4 years. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
0469HVA1 | HVAC UPGRADE | 0469 | The existing HVAC system consists of a wood burning stove, several small propane fired unit heaters and no cooling equipment. There is a need for cooling equipment to provide a comfortable living environment in the summer. This project would provide for replacing the existing heaters with an exterior ground mounted packaged unit that provides heating as well as air conditioning. An electric unit would be most economical if it is solely powered by the solar array electrical system as opposed to a propane fired unit. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2379EXT1 | EXTERIOR FINISHES | 2379 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLACKSMITH SHOP - DIANA MINE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 2003 | 400 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1035EXT1 | HISTORIC BUILDING MAINTENANCE | 1035 | The wood and stone structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, cleaning, repair and re-pointing of the stone work, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORE WAREHOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 464 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6960
1034EXT1 | HISTORIC BUILDING MAINTENANCE | 1034 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing wood shake roof shingles as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TIFFELS CABIN/STAGECOACH STOP | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 693 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10395
0469SFT1 | SMOKE DETECTOR UPGRADE | 0469 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. The existing smoke detectors are not hard wired to the buildings electrical system. This project would provide funding for replacing the existing battery powered smoke detectors and the purchase and installation of new smoke detectors. | RANGER RESIDENCE - MINE FORMAN'S HOUSE | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1896 | 750 | 2019-06-13 | Immediate to Two Years | Currently Critical | 1 | 750
1028ADA1 | BUILDING REPLACEMENT | 1028 | The restroom is approaching the end of its expected life and should be scheduled for replacement. Although it has an ADA sign on it, it is not compliant with current ADA requirements. This project would provide for the demolition and disposal of the existing structure and installation of an ADA compliant precast CXT or similar unisex comfort station to be located adjacent to an ADA accessible parking space. An ADA accessible route of travel from the parking to the comfort station is included in this estimate. | RESTROOM B - CAMPGROUND | 9922 | CNR | Parks |  | Berlin-Ichthyosaur | 1970 | 100 | 2019-06-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0056HVA1 | AIR CONDITIONER INSTALLATION | 0056 | The server room is not sufficiently cooled by the existing HVAC system. The communications system has already failed due to overheating and when the room is too warm, the computer and communications equipment age prematurely. It is recommended to install an independent air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Immediate to Two Years | Currently Critical | 1 | 2500
1682HVA1 | VEHICLE EXHAUST EXTRACTION SYSTEM | 1682 | The vehicle maintenance garages have no exhaust extraction system to remove toxic exhaust fumes. In enclosed areas where motor vehicles operate, mechanical ventilation shall be provided per the 2006 IBC 406.6.3 and UMC 502.14. This project would provide for the purchase and installation of a vehicle exhaust extraction system in two garage bays including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided and / or required by the manufacturer. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
1682EXT2 | EXTERIOR FINISHES | 1682 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24500
1682PLM1 | WATER HEATER REPLACEMENT | 1682 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1682INT1 | INTERIOR FINISHES | 1682 | The interior finishes are in fair condition. The walls and ceilings are mostly unfinished concrete and brick masonry, but some rooms are finished with painted gypsum board. It is recommended that the finished interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
1682ADA1 | ADA SIGNAGE | 1682 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2011-05-19 | Immediate to Two Years | Currently Critical | 1 | 750
0056ADA5 | ADA SHOWER UPGRADE | 0056 | The Men's and Women's restrooms each contain at least one shower. The existing showers are not ADA accessible. This project would provide for an ADA compliant shower for each restroom including access, compliant plumbing fixtures and shower seats. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0056PLM1 | WATER HEATER REPLACEMENT | 0056 | There is a 100 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Four to Ten Years | Long-Term Needs | 3 | 3000
0056ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0056 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Immediate to Two Years | Currently Critical | 1 | 4000
0056ADA3 | ADA SIGNAGE | 0056 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0056INT5 | OFFICE REMODEL | 0056 | The Command Secretary desk and office space are in need of a remodel. The configuration of the space is not functional. The built-in desk does not have enough space for computer equipment, is missing a keyboard tray, and does not allow enough space for moving around in an office chair. This project would provide for removing the existing desk and replacing it with a new desk which fits the needs of the employee. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9923SIT4 | FENCE REPAIRS | 9923 | The painted wrought iron perimeter fence is in need of repairs. The entire fence is due for painting and there are some areas where the iron tubing has split open. Allowing moisture inside the tubing will cause premature deterioration from rusting and corrosion. This project would provide for painting of the fence and repair or replacement of damaged sections of fencing. 300 lineal feet of fencing was used for this estimate. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0056EXT2 | EXTERIOR FINISHES | 0056 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete and brick masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73815
9923SIT3 | GATE OPERATOR REPLACEMENT | 9923 | The site has a perimeter fence with two automatic vehicle access gates off of Hammill Lane and Kietzke Lane. The gate operators are malfunctioning, have been problematic, and have difficulty opening and closing the gates. This project recommends replacing the two gate operators with high quality operators that can handle heavy traffic as well as servicing the gates and related hardware to ensure prolonged operation. The gate operators will be required to meet UL Standard 325, per NRS 405.270. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9923ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9923 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A path of travel from the public street to the accessible public entrance of the building is necessary to comply with ADA accessibility requirements. This project would provide for a concrete walkway from the existing sidewalk to the building. This will require regrading, placement of P.C. concrete, installing a ramp with compliant handrails, signage, striping and any other necessary upgrades. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2011-05-19 | Immediate to Two Years | Currently Critical | 1 | 50000
0056INT1 | FLOORING REPLACEMENT | 0056 | The carpet throughout the building is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84000
0056INT4 | COUNTERTOP REPLACEMENT | 0056 | The countertops in the restrooms and breakroom are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9923SIT2 | SLURRY SEAL ASPHALT PAVING | 9923 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. The rear parking lot is extremely tight which has caused numerous minor vehicle accidents. It may be beneficial to redesign the flow of the parking lot and striping pattern. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 60,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/19/2011. | RENO NHP HQ SITE | 9923 | PubSafe | NHP | B&G | Reno | 1994 |  | 2011-05-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0056INT3 | INTERIOR FINISHES | 0056 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NHP REGIONAL HEADQUARTERS | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 14763 | 2011-05-19 | Four to Ten Years | Long-Term Needs | 3 | 73815
1682ADA2 | ADA RESTROOM REMODEL | 1682 | The existing accessible restroom does not fully meet the Americans with Disabilities Act (ADA) requirements. This project would provide for minor modifications to the existing restroom including flush handle relocation, sink and fixture modifications and accessory mounted location modifications. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HQ GARAGE/SHOP | 9923 | PubSafe | NHP | B&G | Reno | 1994 | 4900 | 2011-05-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0277SFT7 | REMOVE AND REPLACE EAST RAMP AND STAIRS | 0277 | There is a ramp along the northeast side of the building which exceeds 12% slope. The stairs and handrails also are not up to current building code requirements. This project would provide for the removal of the existing ramp and stairs and installation of a new ramp, stairs and handrails per Chapter 10, 2006 IBC. This estimate is for concrete construction. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0277PLM2 | WATER HEATER REPLACEMENT | 0277 | There is a 30 gallon electric water heater in the mechanical room that was installed in 2005. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 3000
0277SFT2 | REPAIR / REPLACE FUSIBLE LINKS | 0277 | The building has two 1-hour Firefly coiling doors with fusible links that are connected to the fire alarm system. Both of the fusible links are not currently operating. This project would provide for repair and/or replacement of the damaged fusible links to ensure proper functioning of the fire rated doors. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 3000
0277SFT3 | EXIT SIGN UPGRADE | 0277 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2006 Chapter 10 was referenced for this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 6750
0277SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0277 | The building is a B occupancy per the 2006 IBC and exceeds 12,000 square feet. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 206080
0277SFT4 | SMOKE DETECTOR UPGRADE | 0277 | The smoke detectors in the building are reaching the end of their expected life and do not meet current standards. It is recommended that the smoke detectors be scheduled for replacement. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0277HVA1 | HVAC EQUIPMENT REPLACEMENT | 0277 | There are fourteen separate HVAC units servicing the building. They were installed at various times, but are all at least ten years old. Each unit serves a particular portion of the building which causes the conditioned spaces to be unbalanced and forces some of the units to be overworked. These older units are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new central HVAC system to provide conditioning for the entire building. The new system will most likely include altering the existing duct work and adding new duct work. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This also includes an energy management system to be installed as part of this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 441600
0277HVA2 | HVAC ALTERATIONS | 0277 | The building has two areas which do not have appropriate heating and cooling service. The Staff Biologist Office does not have supply or return ducting resulting in an unconditioned space that is uncomfortably warm or cold year round. The server room does not have sufficient cooling to accommodate the high heat output from the computer equipment which will cause the equipment to prematurely fail. It is recommended to install supply and return ducting to the office and to provide additional cooling to the server room. This project includes all required connections to existing utilities. This project should be coordinated with the HVAC replacement project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 3500
0277PLM1 | WATER HEATER REPLACEMENT | 0277 | There is a 12 gallon electric water heater in the Hunter's Education portion of the building which was installed in 2000. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. The closet has gas service stubbed into it. This estimate includes: 10 feet of gas pipe, fittings, couplers, and labor for installation. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0277ELE1 | ELECTRICAL UPGRADE | 0277 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit and staff has indicated some of the old wiring and fixtures has been damaged and does not meet today's code requirements. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power, switchgear, wiring, panels and fixtures as required. This project is recommended to be done as soon as possible. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 294400
0277EXT3 | ROOF REPLACEMENT | 0277 | The roof on the Hunter Education Addition area of this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1990. It is recommended that this building be re-roofed in the next two years to be consistent with the roofing program and the end of the warranty period. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 73230
0277PLM3 | RESTROOM UPGRADE | 0277 | The Men's and Women's restrooms on the east side of the building are of original construction and they are due for an upgrade. This project would provide for a remodel of both Men's and Women's restrooms. The remodel may include, but is not limited to, new sinks, toilets, piping, hardware, mirrors, fixtures, partitions, cabinetry, flooring and paint. A lump sum of $16,000 has been included in this estimate for hazardous materials abatement if it is determined that there is asbestos in the flooring adhesive. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 33000
0277INT5 | JANITORS CLOSET REPAIRS | 0277 | The mop sink in the Janitor Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0277EXT2 | EXTERIOR FINISHES | 0277 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 73600
0277INT4 | BREAK ROOM REMODEL | 0277 | The kitchenette and associated casework in the employee break room are original to the building, dating to 1972. The quality of construction and installation were inadequate for the high usage at this facility, and the casework and counter tops are delaminating and failing. This project recommends the replacement of the existing counters, casework, and associated hardware and fixtures with heavy duty, quality components. The casework should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9924SIT3 | PATCH, CRACK FILL AND SLURRY SEAL ASPHALT PAVEMENT | 9924 | The existing asphalt pavement is in poor to fair condition. There are areas that are in need of removal and replacement, crack filling and sealing. This project would provide for the removal and replacement of damaged asphalt pavement on the east side of the site and crack filling and a slurry seal of the west and south paved parking area. Striping including ADA accessible signage, parking, loading and boat inspection spaces and wheel stops are included in this estimate. Also included are concrete filled bollards to be installed around the HVAC unit by the Dispatch Office. Sealing of the asphalt paving also should be scheduled on a cyclical basis of every 3 to 5 years to maintain the integrity of the paving. A figure of 60 cents a square foot for sealing could be used for cyclical pavement sealing which is not included in this estimate. | DEPARTMENT OF WILDLIFE REGIONAL SITE | 9924 | Wildlife |  |  | Reno | 1960 |  | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 120000
0277ADA1 | ADA ACCESSIBLE WATER FOUNTAIN | 0277 | This building contains a water fountain. The 2006 IBC Chapter 11, Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/07/2009. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 4000
9924SIT5 | SHRUB AND TREE REMOVAL | 9924 | There are several shrubs and trees that are in need of removal to prevent damage to the structures on site. This project would provide for the trimming and / or removal of the trees along the main office building, the storage building along the east side of the site and removal of the trees and shrubs along the fence line. | DEPARTMENT OF WILDLIFE REGIONAL SITE | 9924 | Wildlife |  |  | Reno | 1960 |  | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0277INT1 | INTERIOR FINISHES | 0277 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73600
0277ADA3 | ADA ACCESSIBLE RAMP MODIFICATIONS | 0277 | This facility has an ADA accessible ramp located on the south side of the building. The ramp does not have a proper landing, slope or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. This project should coincide with the recommended pavement project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 15000
0277ENR1 | LIGHTING UPGRADE | 0277 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project should be coordinated with the electrical upgrade project. This project or a portion thereof was previously recommended in the FCA report dated 07/15/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/07/2009. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36800
0277EXT4 | WINDOW REPLACEMENT | 0277 | The windows in the older portion of the building are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 75 units. Removal and disposal of the existing windows is included in this estimate. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0277INT2 | FLOORING REPLACEMENT | 0277 | The carpet and VCT (vinyl composite tile) flooring in the building is damaged and reaching the end of its useful life. It is recommended that the carpet and VCT flooring be replaced. This project would provide for removal and disposal of the carpet and VCT and installation of new carpet and 12x12 VCT with a 6" base. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132480
0277INT3 | CEILING TILE REPLACEMENT | 0277 | The original 1963 construction portion of the building has adhered acoustical tiles on the ceiling. A large portion of the ceiling tiles are damaged and stained. This project would provide for the replacement of the acoustical tiles. Removal and disposal of the existing ceiling tiles is included in this estimate. The tiles and / or the adhesive may contain asbestos containing material (ACM) and remediation of ACM is not included in this estimate. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30251
0277ADA4 | ADA ACCESSIBLE SIGNAGE | 0277 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. Some of the signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed or replaced where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 1200
9924SIT4 | PERIMETER FENCE & VEHICLE GATE REPAIRS | 9924 | The chain link perimeter fence has several areas that are in need of repair. The vehicle gate is not operating properly. This project would provide for a new electric vehicle gate to be installed along with repair or replacement of damaged sections of fencing. A three wire barbed fence is also recommended to be installed along the top of the chain link fence to prevent vandalism from occurring inside of the facility. | DEPARTMENT OF WILDLIFE REGIONAL SITE | 9924 | Wildlife |  |  | Reno | 1960 |  | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0278INT1 | INTERIOR FINISHES | 0278 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. The square footage cost is reduced for this building because some of the walls are unfinished and other walls are covered with wallpaper. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3456
0277SFT5 | INSTALL SEISMIC GAS SHUT-OFF VALVE | 0277 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0277SFT6 | HANDRAIL MODIFICATION / INSTALLATION | 0277 | The stair handrails at the front entrance stairs do not meet code for safety or accessibility. There should be two intermediate handrails for the stairs due to the width of the stairs and the existing stairs do not have the proper extensions. This project recommends the installation of two additional handrails on the stairs, with proper returns and supports and modifications to the existing handrails to meet code. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | NDOW REGIONAL OFFICE/ANNEX | 9924 | Wildlife |  |  | Reno | 1963 | 14720 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 3000
0278EXT1 | EXTERIOR FINISHES | 0278 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 3456
0278ADA1 | ADA ACCESSIBLE ENTRANCE RAMP | 0278 | The building has an ADA accessible ramp and handrails that does not meet current code requirements. It is recommended that the ramp, stairs and handrails be replaced. This project would provide for removal and replacement of the existing ADA accessible ramp and handrails. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 35000
0703EXT1 | EXTERIOR FINISHES | 0703 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #2 | 9924 | Wildlife |  |  | Reno |  | 600 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 1200
0659ENR1 | LIGHTING UPGRADE | 0659 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | STORAGE #3 | 9924 | Wildlife |  |  | Reno | 1993 | 2400 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0278ADA2 | ADA ACCESSIBLE SIGNAGE | 0278 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) was used as a reference for this project. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 600
0278ENR1 | LIGHTING UPGRADE | 0278 | The existing lighting fixtures in the Radio Shop are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438
0278SFT1 | EXTERIOR LANDING INSTALLATION | 0278 | There is an exterior door from the Radio Shop which swings out over a step and does not have a proper landing. This does not comply with 2006 IBC Section 1008.1 which describes the requirements for landings including that the landing must be less than 1/2" below the threshold. This project addresses installing a landing designed to current code. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0634EXT1 | EXTERIOR FINISHES | 0634 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #1 - COMMUNICATIONS | 9924 | Wildlife |  |  | Reno |  | 600 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 1200
0659EXT1 | EXTERIOR FINISHES | 0659 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE #3 | 9924 | Wildlife |  |  | Reno | 1993 | 2400 | 2009-04-07 | Four to Ten Years | Long-Term Needs | 3 | 4800
0278EXT2 | ROOF REPLACEMENT | 0278 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next one to two years with a new standing seam metal roofing system. This estimate includes removal and disposal of the old roofing material. | RADIO SHOP/DISPATCH OFFICE | 9924 | Wildlife |  |  | Reno | 1969 | 1152 | 2009-04-07 | Immediate to Two Years | Currently Critical | 1 | 17280
2682ADA2 | ADA RESTROOM ADDITION | 2682 | The existing building was originally a residence and is now being used as a park office. Staff indicated that the public does use the park office on occasions. The existing restroom does not meet ADA accessibility requirements. This project would provide for the existing restroom to be remodeled into a unisex ADA compliant restroom including toilet, sink, door and hardware, signage and toilet accessories. Minor demolition and finishes including flooring and paint is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 15000
9925SIT6 | DRINKING FOUNTAIN REPLACEMENT | 9925 | There are 4 drinking fountains scattered around the park which are damaged from freeze thaw cycles. This project would provide for the replacement of these fountains with 4 new fountains. It is recommended that they be in a style compatible with the park's history and also be ADA compliant. | MORMON STATION STATE HISTORIC PARK | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
2681EXT1 | EXTERIOR FINISHES | 2681 | The cyclical treatment of the kiosk exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the structure. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the kiosk including painting or staining, sealing, repair, and caulking where applicable. This project should be scheduled on a cyclical basis. | PARK KIOSK | 9925 | CNR | Parks |  | Genoa | 1998 | 36 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
9925SIT7 | CRACK FILL / SEAL ASPHALT PAVING | 9925 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving at the ADA accessible parking spaces. Striping is included in this estimate. This project should be scheduled on a 4 year cyclical basis to maintain the integrity of the paving and prevent premature failure. If the new parking area project is completed, this project recommends the same level of maintenance. | MORMON STATION STATE HISTORIC PARK | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 462
9925SIT5 | STOCKADE GATE REPAIR | 9925 | The stockade gate on the south side of the stockade fence is in need of modifications to allow the gate to open properly. This project would provide for the modification of the gate including but not limited to adding sturdy wheels and hardware for ease of operation and stability. | MORMON STATION STATE HISTORIC PARK | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2682EXT3 | EXTERIOR FINISHES | 2682 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are sanding, priming and painting, and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2682INT1 | INTERIOR FINISHES | 2682 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2682ELE1 | ELECTRICAL UPGRADE | 2682 | The building was originally a residence and now is being used as the park office. The electrical system is original and does not have the capacity for it's current use as a park office. This project would provide for a complete electrical upgrade including a new 200 amp service, rewire, and outlet installation. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
2680INT1 | INSTALL FIBERGLASS REINFORCED PANEL (FRP) | 2680 | There is a small mop sink in the janitor's storage room. The gypsum wall board behind the mop sink is damaged from exposure to water and should be repaired and protected. This project would provide for repairs to the wall board and installation of a fiberglass reinforced panel (FRP) on the walls adjacent to the sink. | COMFORT STATION | 9925 | CNR | Parks |  | Genoa | 2006 | 783 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
1334SEC1 | SECURITY SYSTEM INSTALLATION | 1334 | The Park Museum is lacking any type of a security system. It contains numerous artifacts and displays which are valuable. This project would provide for the installation of a security system complete with an alarm and motion detection devices and remote monitoring. | MORMON STATION PARK MUSEUM | 9925 | CNR | Parks |  | Genoa | 1947 | 450 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 15000
2682SFT1 | LIFE SAFETY UPGRADES | 2682 | The building's original occupancy and use was a residence. State park is currently using the facility as a park office which requires the addition of exit signs, a fire alarm and smoke detection system. This project would provide for the installation of new exit signs, a fire alarm and smoke detection system. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 9800
2680PLM1 | WATER HEATER REPLACEMENT | 2680 | There is a 20 gallon electric water heater that is approaching 10 years old and should be scheduled for replacement. The average lifespan is 8-12 years for a water heater based on average use. This project would provide for a new 20 gallon electric water heater to be installed. Removal and disposal of the existing unit is included in this estimate. | COMFORT STATION | 9925 | CNR | Parks |  | Genoa | 2006 | 783 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 850
9925PLM1 | GRINDER PUMP REPLACEMENT | 9925 | There are two grinder pumps which are problematic, failing and should be scheduled for replacement. This project would provide for the replacement of two grinder pumps including all required connections to existing utilities. Removal of the existing pumps is included in this estimate. | MORMON STATION STATE HISTORIC PARK | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 6000
1333EXT3 | ROOF REPLACEMENT | 1333 | The existing wood shingle roof is in poor condition. There are missing shingles and it is showing signs of failure. This project would provide for the installation of a new wood shingle roofing system including new underlayment and waterproofing. The shingles shall match the other wood shingle roofs at the park. Removal and disposal of the old roofing and underlayment is included in this estimate. | GROUP RAMADA | 9925 | CNR | Parks |  | Genoa | 1977 | 1268 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19020
2680EXT1 | INTERIOR / EXTERIOR FINISHES | 2680 | The cyclical treatment of the building interior and exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repairing the chinking and caulking where applicable. This project should be scheduled on a cyclical basis. Exterior chinking maintenance and interior painting is also included in this estimate. | COMFORT STATION | 9925 | CNR | Parks |  | Genoa | 2006 | 783 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3915
1335EXT2 | EXTERIOR FINISHES | 1335 | The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repairing the chinking and caulking where applicable. This project should be scheduled on a cyclical basis. Interior and exterior chinking maintenance is also part of this project. | IRRIGATION PUMP HOUSE | 9925 | CNR | Parks |  | Genoa | 1977 | 160 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
1334ENV1 | REPLACE ROOF | 1334 | The existing wood shingle roof is showing it's age. The wood shingles are deteriorating, there are signs of water damage and some shingles are missing. This project would provide for new wood shingles to be installed including rubberized asphalt sheet waterproofing and felt paper underlayment. Removal and disposal of the existing shingles and underlayment are included in this estimate. | MORMON STATION PARK MUSEUM | 9925 | CNR | Parks |  | Genoa | 1947 | 450 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1334EXT1 | EXTERIOR / INTERIOR FINISHES | 1334 | The cyclical treatment of the building interior and exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repairing the chinking and caulking where applicable. This project should be scheduled on a cyclical basis. Interior and exterior chinking maintenance is also part of this project. | MORMON STATION PARK MUSEUM | 9925 | CNR | Parks |  | Genoa | 1947 | 450 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1333EXT2 | EXTERIOR FINISHES | 1333 | The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with weather proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable. This project should be scheduled on a cyclical basis. | GROUP RAMADA | 9925 | CNR | Parks |  | Genoa | 1977 | 1268 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6340
2378EXT1 | EXTERIOR FINISHES | 2378 | The cyclical treatment of the building exterior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. | WAGON SHED | 9925 | CNR | Parks |  | Genoa | 1995 | 800 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9925SIT4 | PARKING LOT ADDITION | 9925 | The site currently has only a portion of the parking area paved. The area paved is where the ADA accessible parking is located. The rest of the parking area is loose compacted soil and gravel. This project would provide for 3" of asphalt concrete paving over 6" of compacted base. The length of the parking area used for this estimate is 300 feet and the width 25 feet. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | MORMON STATION STATE HISTORIC PARK | 9925 | CNR | Parks |  | Genoa | 0 |  | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
2682ADA1 | ACCESSIBLE BUILDING ENTRANCE | 2682 | The existing exterior entry door and frame are original to the building. The entrance door system does not meet the requirements for ADA Accessibility. This project would provide for a new door, frame, lever action hardware, threshold and exterior landing to be installed. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 5500
1335EXT1 | EXTERIOR DOOR REPLACEMENT | 1335 | The exterior door to the pump house is in poor shape and is delaminating due to excess moisture and age. This project would provide for a new exterior door/frame assembly including door hardware. A paintable metal door system was used for this estimate and will help reduce maintenance costs related to wood. This door should be replaced in the next two years. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | IRRIGATION PUMP HOUSE | 9925 | CNR | Parks |  | Genoa | 1977 | 160 | 2015-02-18 | Immediate to Two Years | Currently Critical | 1 | 2000
2682PLM1 | REPLACE WATER HEATER | 2682 | The average life span of a typical gas/oil or electric water heater is eight to ten years. With the passage of time and constant use, this unit will be reaching the end of its useful life in approximately two to three years. It is recommended that a new natural gas water heater be installed for more efficient use of energy. This estimate includes 100 feet of gas pipe, fittings, couplers, and labor for installation. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | CAMPBELL HOUSE-PARK OFFICE | 9925 | CNR | Parks |  | Genoa | 1945 | 1400 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2683EXT3 | EXTERIOR FINISHES | 2683 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finish on the building is starting to peel and blister. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This building should be painted in the next two years. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | PUMP HOUSE STORAGE | 9925 | CNR | Parks |  | Genoa | 1945 | 100 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2684EXT2 | EXTERIOR FINISHES | 2684 | It is important to maintain the finish, weather resistance and appearance of the building. The exterior finish on the building is starting to peel and blister and some of the wood siding is damaged. This project would provide funding to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. Additional monies are included to replace damaged siding as needed and repair / stabilize the stairs. This building should be painted in the next two years. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | BLACKSMITH SHOP | 9925 | CNR | Parks |  | Genoa | 1945 | 900 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2686EXT1 | CHICKEN COOP - NORTHEAST DEMOLITION | 2686 | The Chicken Coop - Northeast is an abandoned outbuilding on the newly acquired Campbell property. This structure is in poor condition and is not proposed to be used by the park staff. This project would provide for the demolition of this building. This project or a portion there of was previously recommended in the FCA report dated 8/1/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 2/18/2015. | CHICKEN COOP | 9925 | CNR | Parks |  | Genoa | 1945 | 350 | 2015-02-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
9926SIT5 | RESEAL ASPHALT PARKING AND ROAD | 9926 | The existing AC paving is in fair condition. This project would provide for a slurry seal and striping of the paved areas at Cave Rock including the entrance road. This project should be scheduled on a cyclical basis based on environmental conditions and should be implemented in the next two years. This project or a portion thereof was previously recommended in the FCA report dated 07/01/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2012. | LAKE TAHOE NEVADA-CAVE ROCK STATE PARK | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 |  | 2012-06-07 | Immediate to Two Years | Currently Critical | 1 | 22750
9926SIT3 | SIDEWALK / WALKWAY REPAIR | 9926 | The existing AC and PC concrete pathways are failing, some due to exposure to the extreme weather and also erosion from the lake wave action and is a safety concern for the public. This project would provide for the removal repair or replacement as needed of the damaged portions of the walkway. Funds are also included to mitigate future erosion. 2000 square feet of area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/01/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2012. | LAKE TAHOE NEVADA-CAVE ROCK STATE PARK | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 |  | 2012-06-07 | Immediate to Two Years | Currently Critical | 1 | 14000
9926ADA1 | ADA PARKING / ROUTE OF TRAVEL | 9926 | The existing ADA parking spaces are not fully compliant and a route of travel to the restroom does not exist. This project would provide for installing new ADA compliant parking including one van accessible parking and loading space and a striped route of travel to the restroom. Signage is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 07/01/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/07/2012. | LAKE TAHOE NEVADA-CAVE ROCK STATE PARK | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 |  | 2012-06-07 | Immediate to Two Years | Currently Critical | 1 | 4000
0588EXT1 | EXTERIOR FINISHES | 0588 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the doors, wood siding and trim and caulking of the door frames, wood siding and trim as needed, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAVE ROCK FEE STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 2016 | 128 | 2012-06-07 | Four to Ten Years | Long-Term Needs | 3 | 510
9926SIT1 | EROSION / SLOPE MITIGATION | 9926 | The site has some areas with steep slopes that have stacked rail road ties for slope stabilization which are damaged and some are failing. This project would provide for new slope stabilization and mitigation in the areas that are damaged. | LAKE TAHOE NEVADA-CAVE ROCK STATE PARK | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 |  | 2012-06-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0597EXT1 | REROOF BUILDING | 0597 | The existing composition roofing system is showing signs of leaking. There is also a roof mounted platform which has a weather station on it and two skylights on the building. This project would provide for the removal of all of the roof mounted equipment and the two skylights, existing composition shingles and underlayment and installation of a new 50 year asphalt composition roofing system including underlayments. This project may require the approval of the Tahoe Regional Planning Agency due to the structure's location along the waterfront scenic corridor. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2012-06-07 | Immediate to Two Years | Currently Critical | 1 | 7500
0597ADA1 | ADA MODIFICATIONS | 0597 | The existing Men's and Women's restrooms are not fully ADA complaint. This project would provide for modifications to the entrance into the restrooms including reworking the concrete ramp and privacy walls, installing the wall mounted dispensers at the proper location and other improvements as required. ADA signage is also included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2012-06-07 | Immediate to Two Years | Currently Critical | 1 | 15000
0597INT1 | INTERIOR FINISHES | 0597 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2012-06-07 | Four to Ten Years | Long-Term Needs | 3 | 2240
0588INT1 | INTERIOR FINISHES | 0588 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | CAVE ROCK FEE STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 2016 | 128 | 2012-06-07 | Four to Ten Years | Long-Term Needs | 3 | 510
0597EXT2 | EXTERIOR FINISHES | 0597 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the doors, wood siding and trim and caulking of the door frames, wood siding and trim as needed, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAVE ROCK COMFORT STATION | 9926 | CNR | Parks |  | Lake Tahoe/Cave Rock | 1977 | 448 | 2012-06-07 | Four to Ten Years | Long-Term Needs | 3 | 2240
1599EXT1 | EXTERIOR FINISHES | 1599 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
1603SIT1 | RELOCATE AND REMODEL | 1603 | The design of the building has proven to be inadequate in both size and location. The staff regularly sits outside of the building to collect fees stating that the building is too small and uncomfortable to stay inside. The building is also too close to the access road and has been hit by vehicles, trailers and boats on many occasions. This project would provide for moving the entire structure back from the road and adding 50 square feet of floor area. A new roof should be included for the entire structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | BOAT RAMP FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 48 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1575SFT2 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 1575 | The stair handrails and guardrails leading up to the second story of the Storage/ Maintenance Office do not meet code for safety. This project recommends the installation of handrails and guardrails in accordance with the 2012 IBC Section 1012 and Section 1013. Removal and disposal of the existing rails is included in the estimate. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 13200
2552SIT1 | PAVER REPAIR | 2552 | The concrete pavers on the front patio of the building are settling and sinking due to rodent holes. This project would provide for installing a rodent barrier around the perimeter of the pavers to prevent them from burrowing under the pavers. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1593SFT1 | EXTERIOR LANDING INSTALLATION | 1593 | There is an out-swinging exterior door from the building which swings out over a steep ramp and does not have a landing. This does not comply with 2012 IBC Section 1008: 1008.1.6 Landings at doors, which states, "Landings shall have a width not less than the width of the stairway or the door, whichever is greater. Doors in the fully open position shall not reduce a required dimension by more than 7 inches (178mm). When a landing serves an occupant load of 50 or more, doors in any position shall not reduce the landing to less than one-half its required width. Landings shall have a length measured in the direction of travel of not less than 44 inches (1118mm)." This project would provide for the installation of a compliant landing for the door. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 5000
2552INT1 | INTERIOR FINISHES | 2552 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 55800
2552EXT1 | EXTERIOR FINISHES | 2552 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting, staining and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 55800
1599INT1 | INTERIOR FINISHES | 1599 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 900
2552PLM1 | WATER HEATER REPLACEMENT | 2552 | There is a 100 gallon electric water heater in the building. The average lifespan of a water heater is eight to ten years and the water heater was installed in 2007. It is recommended that a new electric water heater, straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. | VISITOR'S CENTER/ CONCESSION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2005 | 5580 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 2200
2376ENR1 | LIGHTING UPGRADE | 2376 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | GROUP USE RAMADA | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1124 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3372
1567PLM1 | WATER HEATER REPLACEMENT | 1567 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 1500
1381ADA1 | ADA RESTROOM UPGRADE | 1381 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 40000
1567EXT2 | EXTERIOR FINISHES | 1567 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 16200
1566SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 1566 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. International Building Code 2012 Chapter 10 was referenced for this project. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3875
1538INT2 | INTERIOR FINISHES | 1538 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1567INT2 | INTERIOR DOOR REPLACEMENT | 1567 | The interior doors in this building are hollow core units and most are damaged. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 3 interior doors was used in this estimate. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 3000
1567EXT3 | EXTERIOR DOOR REPLACEMENT | 1567 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 3000
1566EXT2 | EXTERIOR FINISHES | 1566 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 15500
1566ENR1 | LIGHTING UPGRADE | 1566 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5425
1382INT2 | CONCRETE FLOOR REPLACEMENT | 1382 | The concrete flooring in the utility room is damaged and has reached the end of its useful life. It is recommended that the concrete flooring be replaced. This project would provide for removal and disposal of the existing concrete and installation of new concrete flooring. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1559INT2 | INTERIOR FINISHES | 1559 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1559PLM1 | BACKFLOW PREVENTION | 1559 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1559PLM2 | EXTERIOR FINISHES | 1559 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1559PLM3 | RESTROOM FIXTURES REPLACEMENT | 1559 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 3 water closets; 1 urinal; 2 sinks, and 2 faucets. | COMFORT STATION #8 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1599INT2 | FLOORING REPLACEMENT | 1599 | The wood flooring in the Fee Station is damaged and reaching the end of its useful life. This project would provide for removal and disposal of the wood flooring and the installation of a new subfloor and 12x12 VCT with a 6" base. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1350
1549PLM2 | RESTROOM FIXTURES REPLACEMENT | 1549 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures including 3 water closets, 1 urinal, 2 sinks and 2 faucets. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1549PLM1 | BACKFLOW PREVENTION | 1549 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1384INT2 | INTERIOR FINISHES | 1384 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1599HVA1 | ELECTRIC HEATER REPLACEMENT | 1599 | There is an electric heater in the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1568EXT2 | ROOF REPLACEMENT | 1568 | The asphalt roof on the building is in poor condition and had active leaks at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new single-ply roofing system. This will allow the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. | SEWER PLANT COVER | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1985 | 630 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 7560
1549EXT2 | EXTERIOR FINISHES | 1549 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
15492 | INTERIOR FINISHES | 1549 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #7 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 378 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1382PLM1 | BACKFLOW PREVENTION | 1382 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2906EXT2 | EXTERIOR/ INTERIOR FINISHES | 2906 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | HIDDEN BEACH CXT RESTROOM | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2000 | 81 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1620
1386PLM1 | BACKFLOW PREVENTION | 1386 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1386EXT2 | EXTERIOR FINISHES | 1386 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1386INT2 | INTERIOR FINISHES | 1386 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1386PLM2 | RESTROOM FIXTURES REPLACEMENT | 1386 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #4 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1250 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1384PLM1 | BACKFLOW PREVENTION | 1384 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1384PLM2 | RESTROOM FIXTURE REPLACEMENT | 1384 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2376EXT2 | EXTERIOR FINISHES | 2376 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP USE RAMADA | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1124 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4496
1382EXT2 | EXTERIOR FINISHES | 1382 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1382INT3 | INTERIOR FINISHES | 1382 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1382PLM2 | RESTROOM FIXTURE REPLACEMENT | 1382 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1548PLM1 | BACKFLOW PREVENTION | 1548 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2902EXT1 | EXTERIOR FINISHES | 2902 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE SOUND BOOTH | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 152 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1520
1382ADA2 | ACCESSIBLE ENTRANCE RAMP | 1382 | This facility has an ADA accessible ramp located in front of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have proper landings or handrails. This project would provide for an upgrade to the ramp to make it fully ADA compliant. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | COMFORT STATION #2 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1384EXT2 | EXTERIOR FINISHES | 1384 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #3 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2016 | 654 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
0651EXT2 | EXTERIOR/ INTERIOR FINISHES | 0651 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MEMORIAL POINT COMFORT STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1998 | 1200 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1593ENR1 | LIGHTING UPGRADE | 1593 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
1593ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1593 | The building has a woodshop which does not have a complete dust collection system. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project recommends installing a new dust collection system. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1593SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 1593 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1365
1593EXT2 | EXTERIOR FINISHES | 1593 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 5460
1377EXT3 | EXTERIOR FINISHES | 1377 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 31260
1593HVA1 | ELECTRIC HEATER REPLACEMENT | 1593 | There is a ceiling mounted electric heater in the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2901EXT2 | EXTERIOR FINISHES | 2901 | It is important to maintain the finish, weather resistance and appearance of the stage. This project would provide funding to protect the exterior of the stage. Included in the cost are cleaning and sealing the masonry and to caulk and paint the stage and handrails. It is recommended that the stage and masonry be sealed and painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE STAGE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 2590 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 25900
1377INT4 | INTERIOR FINISHES | 1377 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 31260
2901INT2 | INTERIOR FINISHES | 2901 | It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE STAGE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 2590 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 25900
1381PLM1 | BATHROOM FIXTURE REPLACEMENT | 1381 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 4 water closets; 2 urinals; 6 sinks, and 6 faucets. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1381INT2 | INTERIOR FINISHES | 1381 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1381EXT2 | EXTERIOR FINISHES | 1381 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2015 | 499 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 12500
1603INT2 | INTERIOR FINISHES | 1603 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BOAT RAMP FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 48 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 480
1603EXT2 | EXTERIOR FINISHES | 1603 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOAT RAMP FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 48 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 480
1575SFT3 | STORAGE REMOVAL | 1575 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, "Storage shall be maintained 2 feet or more below the ceiling in nonsprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings." This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 1000
1598HVA1 | ELECTRIC HEATER REPLACEMENT | 1598 | There is an electric heater in the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | WELL HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 640 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2902INT1 | INTERIOR FINISHES | 2902 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHAKESPEARE SOUND BOOTH | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1999 | 152 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1520
1566INT1 | INTERIOR FINISHES | 1566 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15500
1538PLM1 | RESTROOM FIXTURES REPLACEMENT | 1538 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 3 water closets; 1 urinal; 2 sinks, and 2 faucets. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1567INT1 | INTERIOR FINISHES | 1567 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1620 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16200
1568EXT1 | EXTERIOR FINISHES | 1568 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | SEWER PLANT COVER | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1985 | 630 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 2520
1575SFT1 | SAFETY CABINETS | 1575 | The storage room is located on the ground floor and contains many different paints, stains and other hazardous products. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1575INT1 | INTERIOR FINISHES | 1575 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1566INT2 | FLOORING REPLACEMENT | 1566 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
1598EXT1 | EXTERIOR FINISHES | 1598 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | WELL HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 640 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
1593INT1 | INTERIOR FINISHES | 1593 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | WOOD SHOP | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 546 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5460
2903EXT1 | EXTERIOR FINISHES | 2903 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | BOAT RAMP KIOSK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 | 60 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
2904PLM1 | VALVE REPLACEMENT | 2904 | The CLA-VAL pressure reducing valve is not operating and should be replaced. The valve is located on the 2" water line between the well and the storage tank. Staff noted that the valve is undersized and does not function properly requiring the flow to be manually operated. This project would provide for removal and disposal of the existing valve and replacement with a properly sized pressure reducing valve. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | FIRE PUMP HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 280 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 3000
1538EXT2 | EXTERIOR FINISHES | 1538 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
1538PLM2 | BACKFLOW PREVENTION | 1538 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. | COMFORT STATION #5 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1599EXT2 | EXTERIOR DOOR REPLACEMENT | 1599 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1566ELE1 | ELECTRICAL UPGRADE | 1566 | A portion of the building is used as office space by the staff. This space is required to be operational at all times, under all conditions. This project will provide for some additional capacity and hardware needed to operate the building's electrical system via the emergency generator. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | MAIN OFFICE COMPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 1550 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1575EXT1 | EXTERIOR FINISHES | 1575 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | STORAGE/ MAINTENANCE OFFICE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 400 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4000
1548INT2 | INTERIOR FINISHES | 1548 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
15482 | EXTERIOR FINISHES | 1548 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 4480
2904INT1 | INTERIOR FINISHES | 2904 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | FIRE PUMP HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 280 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2904EXT1 | EXTERIOR FINISHES | 2904 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | FIRE PUMP HOUSE | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 280 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2905EXT1 | EXTERIOR FINISHES | 2905 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and the fence surrounding it to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. The square footage used is the area of the water tank walls (1,120 s.f.) plus the area of the top of the tank (700 s.f.) plus the area of the fence (1,120 s.f.). This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | WATER TANK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 2004 | 707 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29400
9927SIT10 | PEST CONTROL - COMFORT STATIONS | 9927 | The Comfort Stations have visible damage from carpenter ants which have infested the buildings. Carpenter ants may cause severe damage and could compromise the structural integrity of wood framed structures if left unchecked. This project would provide for a licensed pest control contractor to eradicate the ants from the Comfort Stations. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 5000
9927SIT9 | SLURRY SEAL ASPHALT PAVING | 9927 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 400,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 300000
1599EXT3 | ROOF REPLACEMENT | 1599 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year metal roofing system and new underlayments. This estimate includes removal and disposal of the old roof. | MAIN FEE STATION | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 90 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
1377SIT1 | EXTERIOR LIGHTING | 1377 | This project recommends installing or replacing general security lighting fixtures around the parking area at the residential duplex to LED lighting. Cost includes light fixtures, wiring, trenching and installation. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1548PLM2 | RESTROOM FIXTURES REPLACEMENT | 1548 | The existing restroom fixtures are original to the building. They are worn and damaged from many years of use and should be scheduled for replacement. This project recommends the replacement of the existing fixtures, to include: 3 water closets; 1 urinal; 2 sinks, and 2 faucets. | COMFORT STATION #6 | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 448 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9927SFT5 | EXTERIOR STAIR HANDRAIL INSTALLATION | 9927 | Exterior stairs have been installed behind the Memorial Point Comfort Station. They start at the parking lot and extend down to the nature trails and do not have handrails or guardrails. This project recommends the installation of handrails and guardrails from the parking area to the trails. Chapter 10 Section's 1012 and 1013 of the 2012 IBC were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 18000
1377ENR1 | ELECTRIC HEATER REPLACEMENT | 1377 | There are several electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1377SFT2 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1377 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails with proper returns and supports per International Residential Code 2012 Section R311. This project or a portion thereof was previously recommended in the FCA reports dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 6000
1377SFT1 | SMOKE ALARM INSTALLATION | 1377 | International Residential Code (IRC) 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA reports dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 4000
9927SIT5 | SIDEWALK REPLACEMENT, PHASE 3 | 9927 | The existing sidewalks serving the boat ramp and boat beach have deteriorated and are failing. In some areas, cracks wider than four inches have been identified, and there are potholes and settling in a number of locations. This project addresses removal and replacement of existing sidewalks as needed. The sidewalks should include flared curb cuts for site accessibility. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | LAKE TAHOE NEVADA-SAND HARBOR STATE PARK | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 0 |  | 2015-10-28 | Four to Ten Years | Long-Term Needs | 3 | 100000
1377EXT1 | ROOF REPLACEMENT | 1377 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA reports dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESIDENTIAL DUPLEX | 9927 | CNR | Parks |  | Lake Tahoe/Sand Harbor | 1970 | 3126 | 2015-10-28 | Immediate to Two Years | Currently Critical | 1 | 37512
1325EXT2 | EXTERIOR FINISHES | 1325 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 24 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 240
9928ADA1 | ADA SIGNAGE | 9928 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed or upgraded at each accessible parking area and accessible paths of travel throughout the park. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | LAKE TAHOE NV-SPOONER LAKE STATE PARK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 |  | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9928ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 9928 | This site contains water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of six drinking fountains to meet the ADA requirements. | LAKE TAHOE NV-SPOONER LAKE STATE PARK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 |  | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1325EXT1 | ROOF REPLACEMENT | 1325 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | PUMP HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 24 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 288
2699EXT1 | EXTERIOR/ INTERIOR FINISHES | 2699 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | HOBART CXT TOILET | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2006 | 81 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 810
3672EXT1 | CONSERVE AND PROTECT VACANT BUILDING | 3672 | The wood structure is over 80 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time for presentation and displays. This project would provide for caulking the flashing, fixtures and windows, replacing metal roof panels as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HANNA'S HIDEAWAY | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1929 | 168 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5600
1290EXT2 | ROOF REPLACEMENT | 1290 | The asphalt roll roofing on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing asphalt roll roofing. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | COMFORT STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 448 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 5376
1323ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 1323 | The electrical transformer that provides electrical services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 5000
1376EXT1 | EXTERIOR/ INTERIOR FINISHES | 1376 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH CANYON CXT TOILET | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2000 | 81 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 810
1323EXT2 | ROOF REPLACEMENT | 1323 | The roof is due for replacement. This project would provide funds for: the demolition of the tar and gravel roof; the demolition of the underlayment; the installation of a new single-ply membrane roof; and the installation of sheet metal over the rafter tails. Additionally, this project will provide funds to fabricate the drip edge over the rafter tails to prevent the collection of snow and moisture and to keep the moisture from running back into the building. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1323INT1 | INTERIOR FINISHES | 1323 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 10000
1323EXT1 | EXTERIOR FINISHES | 1323 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WELL HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1000 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 10000
1371EXT2 | ROOF REPLACEMENT | 1371 | The wood shingle roof was installed in 1989. It is recommended that this building be re-roofed in the next 4-5 years with a new standing seam metal roof and new underlayments. This estimate includes removal and disposal of the old roofing. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | SPENCER'S CABIN | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1920 | 280 | 2015-10-27 | Immediate to Two Years | Currently Critical | 1 | 4760
1372EXT2 | ROOF REPLACEMENT | 1372 | The wood shingle roof was installed in 1989. It is recommended that this building be re-roofed in the next 4-5 years with a new standing seam metal roof and new underlayments. This estimate includes removal and disposal of the old roofing. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RED HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1910 | 947 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 16099
2697EXT2 | ROOF REPLACEMENT | 2697 | The wood shingle roofing on the building is original and should be scheduled for replacement. This project would remove and dispose of the existing wood shingle roofing and install new pre-painted metal panels in the next 4-5 years. | SPOONER SUMMIT TRT KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 50 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 850
3756INT1 | INTERIOR FINISHES | 3756 | It is recommended to stain the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based stain should be utilized in wet areas for durability. | SPOONER CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 340 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3400
1292EXT2 | EXTERIOR FINISHES | 1292 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK CONCESSION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1142 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 11420
2698EXT2 | ROOF REPLACEMENT | 2698 | The asphalt roll roofing covering the building is original and should be scheduled for replacement. This project would remove and dispose of the existing asphalt roll roofing and install new pre-painted metal panels in the next 2-3 years. | BARK BEETLE KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 36 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 612
3757INT1 | INTERIOR FINISHES | 3757 | It is recommended to stain the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based stain should be utilized in wet areas for durability. | WILDCAT CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 230 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
3757EXT1 | EXTERIOR FINISHES | 3757 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WILDCAT CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 230 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
3758INT1 | INTERIOR FINISHES | 3758 | It is recommended to stain the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to staining, all surfaces should be repaired and adequately prepared to receive the coating. | DEMONSTRATION CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 80 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
2696EXT2 | ROOF REPLACEMENT | 2696 | The wood shingle roof on this building was installed in 1989. It is recommended that this building be re-roofed in the next 4-5 years with a new standing seam metal roof and new underlayments. This estimate includes removal and disposal of the old roofing. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | BUNK HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1911 | 338 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 5746
3756EXT1 | EXTERIOR FINISHES | 3756 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SPOONER CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 340 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3400
1374EXT1 | EXTERIOR/ INTERIOR FINISHES | 1374 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | TRT CXT TOILET - MARLETTE CAMPGROUND | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2006 | 81 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 810
1375EXT1 | EXTERIOR/ INTERIOR FINISHES | 1375 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | MARLETTE LAKE CXT TOILET | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 2000 | 81 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 810
3758EXT1 | EXTERIOR FINISHES | 3758 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DEMONSTRATION CABIN | 9928 | CNR | Parks |  | Incline Village | 1998 | 80 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
1291EXT1 | EXTERIOR FINISHES | 1291 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building, excluding the roof. Included in the cost is; sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | FEE STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1991 | 160 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 1600
1291INT1 | INTERIOR FINISHES | 1291 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | FEE STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1991 | 160 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 1600
1372EXT1 | EXTERIOR FINISHES | 1372 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | RED HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1910 | 947 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 9470
1292INT1 | INTERIOR FINISHES | 1292 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | PARK CONCESSION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 1142 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11420
1290INT1 | INTERIOR FINISHES | 1290 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | COMFORT STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 448 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4480
1371EXT1 | EXTERIOR FINISHES | 1371 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | SPENCER'S CABIN | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1920 | 280 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2696EXT1 | EXTERIOR FINISHES | 2696 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | BUNK HOUSE | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1911 | 338 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 3380
2698EXT1 | EXTERIOR FINISHES | 2698 | It is important to maintain the finish, weather resistance and appearance of the kiosk. This project would provide funding to protect the exterior of the kiosk excluding the roof. Included in the cost is power washing and staining the wood. It is recommended that the building be stained in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | BARK BEETLE KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 36 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 500
9928SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9928 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas, and park pathways. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 279,875 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 07/01/2003 and 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | LAKE TAHOE NV-SPOONER LAKE STATE PARK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 |  | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 349844
2697EXT1 | EXTERIOR FINISHES | 2697 | It is important to maintain the finish, weather resistance and appearance of the kiosk. This project would provide funding to protect the exterior of the kiosk excluding the roof. Included in the cost is power washing and staining the wood. It is recommended that the building be stained in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | SPOONER SUMMIT TRT KIOSK | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 0 | 50 | 2015-10-27 | Four to Ten Years | Long-Term Needs | 3 | 500
1290EXT1 | EXTERIOR FINISHES | 1290 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 10/03/2006. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/27/2015. | COMFORT STATION | 9928 | CNR | Parks |  | Lake Tahoe/Spooner | 1977 | 448 | 2015-10-27 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4480
9929ADA8 | DAY USE AREAS ADA IMPROVEMENTS | 9929 | There are 5 day use areas located throughout the park which are in need of miscellaneous ADA improvements. This project would provide for one accessible table, one accessible BBQ and one accessible parking stall in each of the 5 day use areas. Also included is ADA signage, two high/low drinking fountains and removal of AC paving at existing non-compliant ADA parking and accessible routes and replacement with PC concrete pavement and walkways which meet ADA accessibility requirements. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 95000
9929ADA9 | EQUESTRIAN AREA SITE & ADA IMPROVEMENTS | 9929 | There is an equestrian area that is lacking some ADA accessibility items in the comfort station, shade Ramada, parking area, route of travel and walkways. This project would provide for 2 accessible parking stalls, ADA signage, 1 high / low drinking fountain, 1 accessible table at the Ramada, 1 accessible BBQ at the Ramada, remodel one of the restrooms into a unisex ADA compliant restroom and an accessible ramp from the parking area to the restroom. This project also includes the replacement of a damaged pole light. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 51000
9929EXT4 | EXTERIOR FINISHES, SHADE RAMADAS | 9929 | There are 43 steel shade ramadas in different locations throughout the site which measure 11'x11' each for a total of 5,203 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures. This project should be done on a cyclical basis based on environmental conditions. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 10406
2800EXT1 | EXTERIOR FINISHES | 2800 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | STORAGE SHED - WETLANDS | 9929 | CNR | Parks |  | Washoe Lake | 0 | 64 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 320
2799INT1 | INTERIOR FINISHES | 2799 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - WETLANDS | 9929 | CNR | Parks |  | Washoe Lake | 0 | 252 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1260
2798EXT1 | EXTERIOR FINISHES | 2798 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION #2 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 112 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 560
2794EXT1 | EXTERIOR FINISHES | 2794 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | SOUTH BEACH SANI-HUT STRUCTURE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 36 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 180
2798INT1 | INTERIOR FINISHES | 2798 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #2 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 112 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2797EXT1 | EXTERIOR FINISHES | 2797 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION #1 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 224 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1120
2795EXT1 | EXTERIOR FINISHES | 2795 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS SHED | 9929 | CNR | Parks |  | Washoe Lake | 0 | 64 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 320
2796INT1 | INTERIOR FINISHES | 2796 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | FEE BOOTH - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 165 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 825
2796EXT1 | EXTERIOR FINISHES | 2796 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | FEE BOOTH - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 165 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 825
2799EXT1 | EXTERIOR FINISHES | 2799 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - WETLANDS | 9929 | CNR | Parks |  | Washoe Lake | 0 | 252 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1260
2797INT1 | INTERIOR FINISHES | 2797 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #1 - LITTLE WASHOE | 9929 | CNR | Parks |  | Washoe Lake | 0 | 224 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
0483SFT3 | INSTALL EXIT SIGNS AND EGRESS LIGHTING | 0483 | The building does not have any emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency exit lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1500
0595HVA1 | HEATER REPLACEMENT | 0595 | The building is heated by one wall mounted electric heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement of the unit including connections to utilities. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9929ADA12 | LITTLE WASHOE LAKE ADA IMPROVEMENTS | 9929 | The designated ADA accessible parking area appears to exceed the maximum 2% slope and is missing directional signage to the ADA comfort station. This project would provide for the removal of the A. C. paving at the parking areas and installation of new P. C. parking areas including signage and route of travel to the comfort station. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 7000
0587EXT2 | REROOF COMFORT STATION | 0587 | The comfort station roof appears to be original to the building. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. This project would provide for a new 40 year asphalt composition shingle roof including underlayments to be installed. Removal and disposal of the existing roof and underlayment is included in this estimate. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3825
0481EXT1 | EXTERIOR FINISHES | 0481 | This large steel shade ramada in the Group Area covers picnic tables and a built-in barbecue. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure. This project should be done on a cyclical basis based on environmental conditions. | GROUP AREA RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 5480 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 10960
0482EXT2 | DOOR SIGNAGE | 0482 | There are no signs on the doors to the building to direct visitors to the correct restroom. This project would provide for purchase and installation of one sign for each restroom and one sign for the utility room. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1200
0482PLM3 | PLUMBING / RESTROOM REPAIR | 0482 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0482INT1 | INTERIOR FINISHES | 0482 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275
0866PLM1 | PLUMBING UPGRADE | 0866 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0868INT1 | INTERIOR FINISHES | 0868 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 234 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
0868SEC1 | LIGHTING TIME SWITCH REPLACEMENT | 0868 | There is a Tork Time Switch installed in the building which controls the exterior lighting including the sign lighting. It was installed in 1982 and is no longer operating. This project would provide for replacement of the time switch and all required connections to utilities. | HEADQUARTERS FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 234 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0867EXT1 | EXTERIOR FINISHES | 0867 | This large steel shade ramada in the Equestrian Area covers picnic tables and a built-in barbecue. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure. This project should be done on a cyclical basis based on environmental conditions. | EQUESTRIAN AREA RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 625 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1250
0867EXT2 | ROOF REPLACEMENT | 0867 | The roof on this structure was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this structure be re-roofed in the next two to three years with a 40 year asphalt composition roofing shingle and new underlayments. | EQUESTRIAN AREA RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 625 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9375
0866EXT1 | EXTERIOR FINISHES | 0866 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1350
0866INT1 | INTERIOR FINISHES | 0866 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 675
9929ADA10 | CAMPGROUND A ADA IMPROVEMENTS | 9929 | This project would provide for 2 existing campsites to be upgrades to ADA accessible campsites including new P.C. concrete walkways and pads, signage, parking, remodeling one restroom into an accessible unisex restroom, remodel one shower into an accessible shower, and add a new high / low drinking fountain. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 32000
0866EXT4 | REPLACE VAULT DOORS | 0866 | The access to the vault below the building has four steel doors with wooden frames. They are showing signs of wear and deterioration and have reached the end of their expected life. Due to the condition of the doors and frames, this project recommends the installation of new metal doors, metal frames and hardware and includes the disposal of the existing door assemblies. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0869EXT1 | EXTERIOR FINISHES | 0869 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | SOUTH BEACH PUMP HOUSE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 16 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 160
0598EXT1 | EXTERIOR FINISHES | 0598 | This large steel shade ramada in the North Ramp Area covers a picnic area. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure. This project should be done on a cyclical basis based on environmental conditions. | NORTH RAMP RAMADA | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 386 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 772
0595EXT1 | EXTERIOR FINISHES | 0595 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 3460
1029INT1 | INTERIOR FINISHES | 1029 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
0595INT1 | INTERIOR FINISHES | 0595 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1730
0593INT1 | INTERIOR FINISHES | 0593 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 675
0591EXT1 | EXTERIOR FINISHES | 0591 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 240 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2400
0590EXT1 | EXTERIOR FINISHES | 0590 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP PUMP HOUSE | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 64 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 640
0866EXT2 | ROOF REPLACEMENT | 0866 | The roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to three years with a 40 year asphalt composition roofing shingle and new underlayments. | COMFORT STATION - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 1980 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2025
0593EXT1 | EXTERIOR FINISHES | 0593 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1350
1029EXT1 | EXTERIOR FINISHES | 1029 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2500
2375EXT1 | EXTERIOR FINISHES | 2375 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP GARAGE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 400 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 4000
2791EXT1 | EXTERIOR FINISHES | 2791 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 707 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 11312
2792EXT1 | EXTERIOR FINISHES | 2792 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | KIOSK -CAMPGROUND LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 0 | 45 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 225
2793EXT1 | EXTERIOR FINISHES | 2793 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | KIOSK - EQUESTRIAN | 9929 | CNR | Parks |  | Washoe Lake | 0 | 63 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 315
9929ADA7 | WETLANDS ADA IMPROVEMENTS | 9929 | The Wetlands area has a comfort station and viewing platform which are lacking ADA accessible routes from the parking area. This project would provide for an accessible concrete walkway from the parking area to the comfort station and viewing platform. Signage and ADA parking space striping is included in this estimate. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 8000
0594EXT1 | EXTERIOR FINISHES | 0594 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 1350
0868EXT1 | EXTERIOR FINISHES | 0868 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS FEE STATION | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 234 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2340
0594ADA1 | ADA RESTROOM UPGRADE | 0594 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0593ADA1 | ADA RESTROOM UPGRADE | 0593 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
1029EXT2 | WINDOW REPLACEMENT | 1029 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1029EXT3 | EXTERIOR DOOR REPLACEMENT | 1029 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of one new wood door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1029HVA1 | FURNACE INSTALLATION | 1029 | The building does not have any type of heating equipment. This project would provide for installation of a gas fired furnace and includes all required connections to utilities. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1029HVA2 | EVAPORATIVE COOLER REPLACEMENT | 1029 | This building is cooled by a wall mounted evaporative cooler located on the south side of the building. This equipment has reached the end of its expected life and should be scheduled for replacement in the next 2 to 3 years. This project would provide for replacement of the evaporative cooler and includes removal and disposal of the existing unit and all required connections to utilities. | HEADQUARTERS MAINTENANCE OFFICE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 250 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
9929EXT5 | ROOF REPLACEMENT | 9929 | Of the 43 steel shade ramadas, 10 of them were installed in 1980 with asphalt composition shingle roofs. The roofs on these structures were in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that these structures be re-roofed in the next two to three years with a new metal roof and underlayments to match the newer Ramadas. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18150
0483ELE1 | HIGH-SPEED INTERNET INSTALLATION | 0483 | This building is not equipped with a high-speed internet connection. The staff currently uses a dial-up connection to conduct daily business which is time consuming and leaves other responsibilities neglected. In order to provide State employees with responsive access to email and data, the site should be provided with a high-speed internet connection. High-speed internet access fees are not included in the estimated cost. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2500
0595ADA1 | ADA RESTROOM UPGRADE | 0595 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0594INT1 | INTERIOR FINISHES | 0594 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 675
0483INT1 | INTERIOR FINISHES | 0483 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0587ADA1 | ADA RESTROOM UPGRADE | 0587 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0585EXT2 | EXTERIOR FINISHES | 0585 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 1280 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 12800
0585INT2 | INTERIOR FINISHES | 0585 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NORTH RAMP RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 1280 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
0584EXT1 | EXTERIOR FINISHES | 0584 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NORTH RAMP RESIDENCE STORAGE SHED | 9929 | CNR | Parks |  | Washoe Lake | 1995 | 96 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 480
0485EXT1 | EXTERIOR FINISHES | 0485 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 3570
0485INT1 | INTERIOR FINISHES | 0485 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1785
0485ADA2 | ACCESSIBLE WATER FOUNTAIN | 0485 | This building has a water fountain. IBC-2006 Section 1109.5 states that where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of an ADA compliant high / low water fountain. The installation of the water fountain must comply with ICC/ANSI A117.1-2003 and the most current edition of the Americans with Disabilities Act Accessibility Guidelines (ADAAG). | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 4000
9929ADA11 | CAMPGROUND B ADA IMPROVEMENTS | 9929 | This project would provide for 2 existing campsites to be upgrades to ADA accessible campsites including new P.C. concrete walkways and pads, signage, parking, remodeling one restroom into an accessible unisex restroom, and remodel one shower into an accessible shower. The IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 28000
0587INT1 | INTERIOR FINISHES | 0587 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1275
0483EXT1 | EXTERIOR FINISHES | 0483 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 19200
0484EXT2 | EXTERIOR FINISHES | 0484 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | HEADQUARTERS RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1820 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 18200
0483EXT2 | WINDOW REPLACEMENT | 0483 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0483EXT3 | EXTERIOR DOOR REPLACEMENT | 0483 | The existing exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of four new wood doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. The main entrance door, threshold and hardware is not ADA compliant, this project would provide for ADA compliant door hardware and threshold. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0483INT2 | INTERIOR DOOR REPLACEMENT | 0483 | The existing interior doors and frames are damaged from abuse and age. This project would provide for the removal of the existing hollow core doors and frames and the purchase and installation of four new solid core wood doors and frames. All hardware, painting and framing materials are included in this estimate. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0483ADA1 | MISCELLANEOUS ADA UPGRADES | 0483 | The door hardware, signage and information counter are not ADA compliant. Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Section 4.13.9 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 15000
0483ADA2 | ADA RESTROOM UPGRADE | 0483 | The Men's and Women's restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and door hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility. The other restroom will be designated Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 10000
0483ENR1 | LIGHTING UPGRADE | 0483 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures, ballasts and lighting to current standards, resulting in increased efficiency and reduced costs associated with illumination. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
0483SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0483 | The building is partially a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26880
0483HVA1 | HVAC UPGRADE | 0483 | This building is cooled by a window mounted evaporative cooler and heated by a wall mounted gas furnace. This equipment has reached the end of its expected life and should be scheduled for replacement in the next 2 to 3 years. This project would provide for replacement of the evaporative cooler and gas fired furnace and includes removal and disposal of the existing units and all required connections to utilities. | HEADQUARTERS OFFICE/SHOP/STORAGE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1920 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0482EXT1 | EXTERIOR FINISHES | 0482 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2550
0484INT1 | INTERIOR FINISHES | 0484 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | HEADQUARTERS RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 1820 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9100
9929SIT4 | SLURRY SEAL ASPHALT PAVING | 9929 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including campground roads, access roads, parking areas and the Headquarters storage yard and parking - access area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 300,000 square feet of asphalt area was used to generate this estimate. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 180000
0587EXT1 | EXTERIOR FINISHES | 0587 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Four to Ten Years | Long-Term Needs | 3 | 2550
0485PLM1 | PLUMBING / RESTROOM REPAIR | 0485 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. One of the restroom stalls was not in operation. This project would provide funds for the repair of the plumbing, fixtures and restroom stall. This will provide for a fully operational comfort station. | COMFORT STATION - LOOP A | 9929 | CNR | Parks |  | Washoe Lake | 1985 | 357 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0587PLM1 | PLUMBING /RESTROOM REPAIR | 0587 | The Comfort Station plumbing and fixtures were not operating properly at the time of the survey. One of the restroom stalls was not in operation. This project would provide funds for the repair of the plumbing, fixtures and restroom stall. This will provide for a fully operational comfort station. | COMFORT STATION - NORTH RAMP | 9929 | CNR | Parks |  | Washoe Lake | 1988 | 255 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0593PLM1 | PLUMBING UPGRADE | 0593 | The Comfort Station plumbing and fixtures (sink) were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - DAY USE #1 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0594PLM1 | PLUMBING UPGRADE | 0594 | The Comfort Station plumbing and fixtures (sink) were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - DAY USE #2 | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 135 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
0595PLM1 | PLUMBING UPGRADE | 0595 | The Comfort Station plumbing and fixtures (sink) were not operating properly at the time of the survey. This project would provide funds for the repair of the plumbing and fixtures. This will provide for a fully operational comfort station. | COMFORT STATION - GROUP USE | 9929 | CNR | Parks |  | Washoe Lake | 1978 | 346 | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 2500
9929PLM1 | REPLACE FREEZE PROOF FIRE HYDRANT | 9929 | There is a freeze proof fire hydrant in Campground A between site's 3 and 4 that is damaged. This project would provide for the replacement of the broken hydrant with a new freeze proof fire hydrant. | WASHOE LAKE STATE PARK | 9929 | CNR | Parks |  | Washoe Lake | 1977 |  | 2018-08-09 | Immediate to Two Years | Currently Critical | 1 | 1200
0482PLM2 | WATER HEATER REPLACEMENT | 0482 | The average life span of a water heater is eight to ten years. The existing 28 gallon natural gas water heater is approaching the end of its expected life and should be scheduled for replacement in the next 2 to 3 years. This project would provide for the removal and disposal of the old water heater and installation of a new 28 gallon water heater. | COMFORT STATION - LOOP B | 9929 | CNR | Parks |  | Washoe Lake | 1979 | 255 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0585PLM1 | INSTALL WATER SOFTENER / FILTER | 0585 | The water at the site is a well system, the water is full of minerals, and smells bad. This project recommends the installation of a water filtration system to improve water quality and extend the life of plumbing and appliances. This project or a portion thereof was previously recommended in the FCA report dated 06/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/01/2008. | NORTH RAMP RANGER RESIDENCE | 9929 | CNR | Parks |  | Washoe Lake | 1996 | 1280 | 2018-08-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1159EXT1 | EXTERIOR FINISHES | 1159 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CATTLE FEEDER SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 389 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3890
1162EXT1 | EXTERIOR FINISHES | 1162 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5890
1155SIT1 | DRAINAGE IMPROVEMENTS | 1155 | The rafters are cracked, broken, missing bolts and were in need of replacement at the time of the survey. It is recommended that new rafters, sheathing, underlayment, and a new 50 year asphalt composition roofing system be installed within the next 2-3 years. This estimate includes removal and disposal of the old rafters, sheathing, underlayment and roofing system and installation of new. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1155EXT3 | GUTTER AND DOWNSPOUT INSTALLATION | 1155 | The building does not have gutters or downspouts to control the runoff from the roof. The water currently sheet drains off the roof causing extensive erosion to the grade around the foundation and contributes to the drainage problems at the rear of the building. This will eventually lead to failure of the foundation undermining the integrity of the entire structure. This project would provide funding for the installation of a seamless gutter and downspout system for the building. This project should coincide with the Drainage Improvements project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1156EXT1 | EXTERIOR FINISHES | 1156 | It is important to maintain the finish, weather resistance and appearance of the structure excluding the roof. This project would provide for cleaning and sealing the wood and the concrete masonry and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10368
1157EXT1 | EXTERIOR FINISHES | 1157 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact. It is recommended that the building be painted within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 21120
1157INT1 | INTERIOR FINISHES | 1157 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21120
1157ENR1 | LIGHTING UPGRADE | 1157 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16896
1157SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1157 | The exit signs do not meet current standards and there is no emergency egress lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1000
1157SFT2 | SAFETY CABINETS | 1157 | The shop contains many different paints, stains, pesticides and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building is exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10000
1153SFT1 | EXTERIOR LANDING INSTALLATION | 1153 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 5000
1160EXT1 | EXTERIOR FINISHES | 1160 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CALVING SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 569 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5690
1155ENR1 | LIGHTING UPGRADE | 1155 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15696
1163EXT1 | EXTERIOR FINISHES | 1163 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1250
1163INT1 | REPLACE INSULATION | 1163 | The building has a layer of insulation installed on the interior walls that has reached the end of its useful life. It is falling off the walls and ceiling and should be scheduled for replacement in the next 1-2 years. This project recommends replacement with a foil-backed R-30 insulation. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 250
1164EXT1 | EXTERIOR FINISHES | 1164 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | PUMP CONTROL/ SEASONAL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 237 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2370
1167EXT2 | EXTERIOR FINISHES | 1167 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact.. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9250
1167INT2 | INTERIOR FINISHES | 1167 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 9250
1155SFT3 | FIRE ALARM SYSTEM INSTALLATION | 1155 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 IFC. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 7848
1154EXT2 | EXTERIOR FINISHES | 1154 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE FEE BOOTH | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 64 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 640
1147EXT1 | HISTORIC BUILDING MAINTENANCE | 1147 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HISTORIC BLACKSMITH SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 437 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6555
1158EXT2 | ROOF REPLACEMENT | 1158 | The building’s roof system has major structural problems and the asphalt composition shingles are due for replacement. The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood roofing shingle and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1151EXT1 | EXTERIOR FINISHES | 1151 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 4020
1148EXT1 | HISTORIC BUILDING MAINTENANCE | 1148 | The wood structure is over 100 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit pieces. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HISTORIC BUNKHOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 322 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4830
1152EXT1 | EXTERIOR FINISHES | 1152 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood siding, re-pointing the stone masonry as needed and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4210
1171EXT1 | HISTORIC BUILDING MAINTENANCE | 1171 | The metal clad wood structure is over 100 years old. It is important to maintain the finish, weather resistance and appearance of the building. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for caulking the metal panels, sealing the wood door, replacing the metal roof and wall panels as needed and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HISTORIC STORAGE SHED | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 120 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
1174EXT1 | HISTORIC BUILDING MAINTENANCE | 1174 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WILSON RESIDENCE/ SANDSTONE CABIN | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 681 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10215
1149EXT1 | EXTERIOR FINISHES | 1149 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the sealing and painting of the exterior of the building. Included in the cost is sealing the stone, repairing the cracks and caulking the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12960
1149SIT1 | DRAINAGE IMPROVEMENTS | 1149 | The west wall is largely below grade and experiences water weeping through it during inclement weather. The water erodes the mortar and is causing major cracks in the wall. This project provides for waterproofing the exterior wall below grade and installing a french drain. The work will include excavation to expose the entire wall, applying a 100% polymer waterproof membrane to the wall, backfilling and installing a french drain along the length of the wall. This project should coincide with the Gutter and Downspout Installation project. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1149EXT2 | GUTTER AND DOWNSPOUT INSTALLATION | 1149 | The rafters are cracked, broken, missing bolts and were in need of replacement at the time of the survey. It is recommended that new rafters, sheathing, underlayment, and a new 50 year asphalt composition roofing system be installed within the next 2-3 years. This estimate includes removal and disposal of the old rafters, sheathing, underlayment and roofing system and installation of new. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1150EXT1 | EXTERIOR FINISHES | 1150 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry and caulking of the windows, doors, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4020
1155HVA1 | EXHAUST FAN INSTALLATION | 1155 | The welding shop area does not have adequate ventilation. This project would provide for the purchase and installation of an exhaust fan assembly for the welding shop including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10000
1150ADA1 | ADA RESTROOM UPGRADE | 1150 | The designated ADA accessible restrooms do not fully meet the ADA requirements. This project would provide for remodeling two of the restrooms into ADA compliant restrooms including but not limited to proper signage, sink, toilet, grab bars, tissue dispensers, mirror, electric hand dryers and door hardware. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 4000
1155SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1155 | The exit signs do not meet current standards and there is no emergency egress lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1962
1151INT1 | INTERIOR FINISHES | 1151 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4020
1151EXT2 | DOOR HARDWARE REPLACEMENT | 1151 | The exterior metal doors are in good shape, but staff has had continuous problems with the hardware. The handles and locks are damaged from age and general wear and tear and have reached the end of their useful life. This project would provide for the replacement of the hardware on six doors. Removal and disposal of the existing hardware is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1151ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1151 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 4000
1153EXT1 | EXTERIOR FINISHES | 1153 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 1230
1153EXT2 | ROOF REPLACEMENT | 1153 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayments. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1845
1155EXT1 | EXTERIOR FINISHES | 1155 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19620
1155INT1 | INTERIOR FINISHES | 1155 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19620
1155EXT2 | OVERHEAD DOOR REPLACEMENT | 1155 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They have reached the end of their useful life and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | WORK SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 1962 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
1153EXT3 | EXTERIOR SIDING REPLACEMENT | 1153 | The storage shed has painted T1-11 siding that is damaged, in poor condition, and due for replacement. This project recommends removing the damaged T1-11 siding and replacing it with new T1-11 siding finished with an oil-based stain or paint. | DOG KENNEL | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 123 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
1150INT1 | INTERIOR FINISHES | 1150 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4020
1635INT1 | INTERIOR FINISHES | 1635 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
1158EXT1 | EXTERIOR FINISHES | 1158 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1172ENR2 | HVAC EQUIPMENT REPLACEMENT | 1172 | The existing HVAC system consists of window mounted HVAC systems and a split system. This project would provide for replacing the existing equipment with exterior ground mounted packaged units that provide heating and air conditioning. Ducting and vents will need to be installed in the attic. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 63420
1173EXT1 | EXTERIOR FINISHES | 1173 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9120
1173ADA1 | ADA SIGNAGE | 1173 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 900
9930ADA3 | ADA PROGRAM ACCESSIBILITY | 9930 | The site has historic structures and other ranch features that are open to the public for viewing. There are also guided tours of the site offered at various times throughout the week. There is no designated ADA access to most of these areas across the ranch. This project would provide for an ADA accessible location inside of the Visitor's center for an audio/ visual (A/V) presentation of the historic structures and other inaccessible features of the site. This project includes funds for an audio/ visual consultant to outline and document the inaccessible areas and purchase and installation of all required A/V equipment including signage, TDD equipment and minor remodeling of the public area of the building as required to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1173ENR1 | WINDOW REPLACEMENT | 1173 | The windows are original, dual pane construction in a metal frame and have reached the end of their useful life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1173SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1173 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 12768
1173SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1173 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 3648
1154INT1 | INTERIOR FINISHES | 1154 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | THEATRE FEE BOOTH | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 64 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 640
1635EXT1 | EXTERIOR FINISHES | 1635 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, cleaning and sealing the stone and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
1169EXT1 | EXTERIOR FINISHES | 1169 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #5 - SPRING HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 620 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6200
1636EXT1 | EXTERIOR FINISHES | 1636 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
1636INT1 | INTERIOR FINISHES | 1636 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
1636ENR1 | AIR CONDITIONER REPLACEMENT | 1636 | The wall-mounted air conditioner was installed in 1997. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the purchase and installation of a new wall-mounted air conditioner. This project includes removal and disposal of the existing unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3043EXT1 | EXTERIOR FINISHES | 3043 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting, and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DOMESTIC WELL/ PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 2005 | 96 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
9930ADA2 | ADA PARKING SPACE UPGRADE | 9930 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Ranger’s Office, Theatre area and Visitors Center are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate for each location. It is recommended that this project coincide with the paving projects. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 90000
9930SIT1 | SLURRY SEAL ASPHALT PAVING | 9930 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving at the main parking lot near the Picnic Area. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62500
9930SFT3 | WOOD ROOF FIRE RETARDANT TREATMENT | 9930 | There are 13 structures throughout the site that have wood shingle roofs. Altogether the square footage adds up to about 12,124 square feet of wood roof area. Due to the historic nature of the site and structures, these wood roofs should not be replaced with another roofing material. It is recommended to develop an annual roof maintenance program to address the fire resistance of the shingles. This project would provide for the purchase and application of a fire retardant coating for the wood roofs. This project should be scheduled on an annual basis to ensure that the structures are thoroughly protected. The structures included are: 1147 Historic Blacksmith Shop, 1149 Chinchilla Shed, 1152 Milking Barn, 1157 Hay & Horse barn/ Corral/ Shop, 1159 Cattle Feeder Shed, 1160 Calving Shed, 1162 Chicken Coop, 1163 Power Control Shed, 1169 Residence #5 - Spring House, 1170 Residence #6 - Cowhand House, 1172 Visitor's Center, 1174 Wilson Residence/ Sandstone Cabin, and 1635 Entrance Station. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | SPRING MOUNTAIN RANCH STATE PARK | 9930 | CNR | Parks |  | Spring Mountain | 0 |  | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 6062
1157SFT3 | STAIR HANDRAIL & LANDING INSTALLATION | 1157 | There is an exit door which has a stairway down into the shop area of the building. There are no handrails nor proper landings at this exit. This project would provide for a concrete exterior landing and a new wood framed stairway, landing and handrails on the interior. The ICC 2012 Chapter 10, Section's 1008, 1009 and 1012 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1200
1634INT1 | INTERIOR FINISHES | 1634 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | THEATRE/ PAVILION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 6230 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62300
1167ENR2 | LIGHTING UPGRADE | 1167 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7400
1152INT1 | INTERIOR FINISHES | 1152 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4210
1152ELE1 | WIRING CLEANUP | 1152 | The wiring in the Milk Barn is disorganized and not in proper electrical boxes. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1152EXT2 | WINDOW REPLACEMENT | 1152 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. | MILKING BARN | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 421 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1151HVA1 | ELECTRIC HEATER REPLACEMENT | 1151 | There is an electric heater in the pipe chase/ janitor area of the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1151ADA2 | ADA RESTROOM UPGRADE | 1151 | The designated ADA accessible restrooms do not fully meet the ADA requirements. This project would provide for remodeling two of the restrooms into ADA compliant restrooms including but not limited to proper signage, sink, toilet, grab bars, tissue dispensers, mirror, electric hand dryers and door hardware. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. | COMFORT STATION #2 - GROUP USE | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 15000
1150HVA1 | ELECTRIC HEATER REPLACEMENT | 1150 | There is an electric heater in the pipe chase/ janitor area of the building that has reached the end of its life expectancy. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1150ELE1 | GFCI OUTLETS | 1150 | The existing receptacles in the Comfort Station #1 are standard duplex receptacles. The 2011 (NEC) National Electrical Code 210.8 requires these locations to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | COMFORT STATION #1 | 9930 | CNR | Parks |  | Spring Mountain | 1981 | 402 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1149SFT1 | SAFETY CABINET | 1149 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 10000
1172INT1 | INTERIOR FINISHES | 1172 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42280
1167ENR1 | WINDOW REPLACEMENT | 1167 | The windows are original, dual pane construction in a metal frame and have reached the end of their expected life. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1170EXT1 | EXTERIOR FINISHES | 1170 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #6 - COWHAND HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 432 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1167ENR3 | HVAC UPGRADE | 1167 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations and mitigating the earth to wood contact.. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1167PLM2 | WATER HEATER REPLACEMENT | 1167 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1168EXT2 | EXTERIOR FINISHES | 1168 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations and mitigating the earth to wood contact.. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
1168INT2 | INTERIOR FINISHES | 1168 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
1168ENR3 | WINDOW REPLACEMENT | 1168 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1168ELE3 | EXTERIOR OUTLET REPLACEMENT | 1168 | The building has exterior electrical outlets that do not meet current building codes. These outlets should be changed to GFCI type outlets with covers per the 2011 NEC. This project would provide for the purchase and installation of 4 GFCI duplex outlets. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 1600
1168ENR2 | LIGHTING UPGRADE | 1168 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19520
1168ENR1 | HVAC EQUIPMENT REPLACEMENT | 1168 | The building is heated and cooled by two electric roof mounted packaged units. They are reaching the end of their serviceable life and should be scheduled for replacement. This project provides for disposal of the existing units and replacement with two new roof mounted packaged units including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1172EXT1 | EXTERIOR FINISHES | 1172 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, doors, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42280
1149EXT3 | ROOF REPLACEMENT | 1149 | The rafters are cracked, broken, missing bolts and were in need of replacement at the time of the survey. It is recommended that new rafters, sheathing, underlayment, and a new 50 year asphalt composition roofing system be installed within the next 4-5 years. This estimate includes removal and disposal of the old rafters, sheathing, roofing system and underlayment, and installation of the new roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 19440
1172ENR1 | WINDOW REPLACEMENT | 1172 | Most of the windows have been upgraded, but there are two older units left to replace. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units including vinyl frames. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1634EXT2 | EXTERIOR FINISHES | 1634 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE/ PAVILION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 6230 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 62300
1157SFT4 | EXTERIOR DOOR LANDING INSTALLATION | 1157 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1635ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 1635 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 30000
1163HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1163 | A window air conditioning unit is installed on the side of this building. It was not working at the time of the survey and has reached the end of its useful and expected life. This project would provide for a new air conditioning unit to be installed including all required connections to utilities. The estimate includes removal and disposal of the old air conditioning unit. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1162EXT2 | ROOF REPLACEMENT | 1162 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8835
1162SFT1 | EXTERIOR LANDING INSTALLATION | 1162 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1162EXT3 | WINDOW REPLACEMENT | 1162 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHICKEN COOP | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 589 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1160EXT2 | ROOF REPLACEMENT | 1160 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CALVING SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 569 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8535
1159EXT2 | ROOF REPLACEMENT | 1159 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CATTLE FEEDER SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 389 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8535
1159INT1 | INTERIOR FINISHES | 1159 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CATTLE FEEDER SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 389 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6828
1158ENV1 | PEST CONTROL | 1158 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1163EXT2 | ROOF REPLACEMENT | 1163 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1875
1157ENV1 | DUST COLLECTION SYSTEM INSTALLATION | 1157 | The existing wood working equipment has only partial dust collection capacity. In order to reduce the possibility of damage or injury, each piece of equipment should have full collection capability. This project will provide for the replacement of the existing system and installation of additional capacity to minimize explosion hazard and disruption to production. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1164SFT1 | EXTERIOR DOOR LANDING INSTALLATION | 1164 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | PUMP CONTROL/ SEASONAL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 237 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1157HVA1 | ELECTRIC HEATER REPLACEMENT | 1157 | There are two electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. | HAY & HORSE BARN/ CORRAL/ SHOP | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 2112 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1156ADA1 | ADA TABLE UPGRADE | 1156 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 2 of the fixed seats, which will allow access for wheel chairs. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 2000
1156SIT1 | SITE DRAINAGE UPGRADES | 1156 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1156ENR1 | ENTERIOR LIGHTING REPLACEMENT | 1156 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1156EXT3 | ROOF AND RAFTER REPLACEMENT | 1156 | The rafters are cracked, broken, missing bolts and were in need of replacement at the time of the survey. It is recommended that new rafters, sheathing, underlayment, and a new 50 year asphalt composition roofing system be installed within the next 2-3 years. This estimate includes removal and disposal of the old rafters, sheathing, roofing system and underlayment, and installation of the new roof. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129600
1156ADA2 | ADA BARBEQUE UPGRADE | 1156 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the barbeques shall be ADA compliant. This project would provide funding to remove 3 of the barbeques, and install ADA complaint barbeques which will allow access for wheel chairs. | GROUP USE SHELTER | 9930 | CNR | Parks |  | Spring Mountain | 1983 | 2592 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 4500
1149STR1 | STRUCTURAL REPAIRS | 1149 | The Chinchilla Shed has a major crack in the masonry wall. It is recommended that a structural investigation and assessment be done by a licensed professional to evaluate this construction. Future recommendations will be based on the report. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | CHINCHILLA SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 1296 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1173INT2 | INTERIOR FINISHES | 1173 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9120
1170INT2 | INTERIOR FINISHES | 1170 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #6 - COWHAND HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 432 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1158ELE1 | WIRING CLEANUP | 1158 | The wiring in the northwest electrical room is disorganized and not in proper electrical boxes, particularly around the irrigation controls. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | VERA'S STABLES | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 500 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1173ADA3 | BREAK ROOM REMODEL | 1173 | The kitchenette and associated cabinets in the employee break room are original to the building. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 15000
1636PLM1 | PUMP REPLACEMENT | 1636 | The pump in the Irrigation Pump House was problematic at the time of the survey. The irrigation pump reached the end of its expected life and is due for replacement. It is recommended to replace the pump with a 10 H.P. Berkeley Pump. This project includes removal and disposal of the existing pump and all required connections to utilities. | IRRIGATION PUMP HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1997 | 117 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1635PLM1 | WATER HEATER REPLACEMENT | 1635 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ENTRANCE STATION | 9930 | CNR | Parks |  | Spring Mountain | 1992 | 225 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1634ADA1 | ACCESSIBLE ENTRANCE RAMP | 1634 | The Theatre/ Pavilion is in need of an accessible entrance into the basement. This building is required to have an accessible entrance to the basement per the ADA regulations. This project would provide for an accessible ramp to access the basement of the building. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | THEATRE/ PAVILION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 6230 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 35000
1633EXT2 | EXTERIOR FINISHES | 1633 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE CONCESSION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 400 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 4000
1633INT2 | INTERIOR FINISHES | 1633 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | THEATRE CONCESSION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 400 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 4000
1633HVA1 | EVAPORATIVE COOLER REPLACEMENT | 1633 | An evaporative cooler is installed on the side of this building. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | THEATRE CONCESSION | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 400 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1173EXT2 | ROOF REPLACEMENT | 1173 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 13680
1173ENR2 | LIGHTING UPGRADE | 1173 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 7296
1163SFT1 | EXTERIOR DOOR LANDING INSTALLATION | 1163 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | POWER CONTROL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1940 | 125 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1173PLM1 | WATER HEATER REPLACEMENT | 1173 | There is a 6 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 1000
2410EXT2 | EXTERIOR FINISHES | 2410 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | THEATRE STORAGE | 9930 | CNR | Parks |  | Spring Mountain | 1988 | 196 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 1960
1172PLM1 | PLUMBING REPLACEMENT | 1172 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105700
1172SFT1 | SMOKE CARBON MONOXIDE ALARM | 1172 | IRC 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. | VISITOR'S CENTER | 9930 | CNR | Parks |  | Spring Mountain | 1948 | 4228 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 5000
1171SIT1 | SITE DRAINAGE UPGRADES | 1171 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | HISTORIC STORAGE SHED | 9930 | CNR | Parks |  | Spring Mountain | 1870 | 120 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1170EXT2 | WINDOW REPLACEMENT | 1170 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #6 - COWHAND HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 432 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1169INT1 | INTERIOR REMODEL | 1169 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #5 - SPRING HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 620 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31000
1169EXT2 | WINDOW REPLACEMENT | 1169 | The windows are original, single pane construction in a wooden frame. These older windows are drafty, not energy efficient and the wooden frames have deteriorated significantly. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units including wooden frames. Removal and disposal of the existing windows is included in this estimate. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | RESIDENCE #5 - SPRING HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1930 | 620 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1168EXT3 | ROOF REPLACEMENT | 1168 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 8-9 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roofing system. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Four to Ten Years | Long-Term Needs | 3 | 29280
1168INT3 | FLOORING REPLACEMENT | 1168 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new sheet vinyl with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19520
1167ENV1 | PEST CONTROL | 1167 | There are numerous signs throughout this building of insect infestation including ants. Due to the potential risk of disease and damage to the building, this project provides for treatment and cleanup of the insects by a licensed pest control business. It is recommended that the building be treated in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1164EXT2 | ROOF REPLACEMENT | 1164 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new wood shingle roofing system and new underlayment. This estimate includes removal and disposal of the old roof. | PUMP CONTROL/ SEASONAL SHED | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 237 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3555
1173ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 1173 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements and need to be updated. This project would provide for an updated concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | RANGER'S OFFICE/ GUEST HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1955 | 912 | 2016-12-15 | Immediate to Two Years | Currently Critical | 1 | 30000
1168PLM1 | WATER SOFTENER INSTALLATION | 1168 | The domestic water supply is a gravity fed water system and the water is full of minerals. This project recommends the installation of a water softening system to extend the life of the plumbing system, fixtures and appliances. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003 and 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1167PLM1 | WATER SOFTENER INSTALLATION | 1167 | The domestic water supply is a gravity fed water system and the water is full of minerals. This project recommends the installation of a water softening system to extend the life of the plumbing system, fixtures and appliances. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003 and 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #3 - FOREMAN'S HOUSE | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 925 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1168INT1 | KITCHEN CABINET REPLACEMENT | 1168 | The kitchens in both duplexes were in fair to poor condition at the time of the survey. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003 and 05/13/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/15/2016. | RESIDENCE #4 - OLD BUNKHOUSE/ DUPLEX | 9930 | CNR | Parks |  | Spring Mountain | 1957 | 2440 | 2016-12-15 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
1907EXT2 | GARAGE DOOR REPLACEMENT | 1907 | The overhead garage door is cracked down the middle due to wind exposure and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the overhead garage door and replacement with a new door. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 2800
9931SIT6 | ASPHALT PAVING INSTALLATION | 9931 | The access road to the Shop/ Maintenance Building and Ranger Residences and the parking areas around these buildings are not paved. This project would provide asphalt cement paving for a 20' wide access road, for parking around the Residences and paving the vehicle yard around the Shop/ Maintenance Building. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 250000
9931EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9931 | There are 43 steel shade ramadas in different locations throughout the site which are 400 s.f. each and a Bus Stop Shelter that is 43 s.f. for a total of 17,243 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures in the next 4-5 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 34486
9931SIT3 | SITE DRAINAGE ASSESSMENT | 9931 | There are several areas throughout the site that have drainage problems. A large amount of runoff travels through the property during inclement weather. The drainage features include culverts, ditches and rip rap berms which have eroded over time and no longer control the runoff properly. This project would provide for a site survey and drainage report to be completed by a licensed professional to determine what measures should be taken to prevent future flooding. Future projects may arise from the results of this report. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9931SFT1 | RELOCATE SHADE RAMADAS | 9931 | There are five shade ramadas that need to be relocated. They are located on the north side of the day use area near the river. The banks of the river have eroded and are undermining the slabs and footings of the ramadas. This has created a safety hazard around the structures where the public is at risk of tripping, falling off the edge or the slab breaking while people are on it. This project would provide for extracting the ramadas from their existing footings, removing the existing footings and slabs, installing the ramadas in new footings and pouring new slabs. State Parks provided a cost for this project of $5,000 per ramada. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 25000
1907EXT1 | EXTERIOR FINISHES | 1907 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 10500
1907SIT1 | DRIVEWAY REPLACEMENT | 1907 | The concrete driveway has extensive cracking and settling damage and is due for replacement. This project would provide for the installation of a new 4" thick concrete slab driveway in front of the garage door. Removal and disposal of the existing concrete is included in this estimate. 400 square feet of area was used to generate this estimate. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2349SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2349 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 4000
9931SIT2 | CRACK / FOG SEAL ASPHALT PAVING | 9931 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and fog sealing of the three large parking lots and the walkways throughout the day use areas. Striping is included in this estimate. The access roads throughout the site are maintained by NDOT and are not included in this project. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 150,000 square feet of asphalt area was used to generate this estimate. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112500
9931SIT4 | STORAGE STRUCTURE INSTALLATION | 9931 | There is a need for a storage structure in the maintenance area. The trucks, agricultural equipment and building materials are exposed to the sun causing preventable damage and maintenance costs. This project would provide a three sided steel structure 24' x 40' to be constructed in the maintenance yard. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62400
2349ADA1 | ADA PARKING UPGRADES | 2349 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not entirely meet the requirements of the code, specifically because it is not 18 feet long. This project provides funding to bring the existing ADA parking space up to code including regrading to add length to the parking space, placement of P.C. concrete, updated signage, re-striping, and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 2000
1907INT1 | INTERIOR FINISHES | 1907 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
1908EXT1 | EXTERIOR FINISHES | 1908 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and wood, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1540
2349HVA1 | A.C. COMPRESSOR REPLACEMENT | 2349 | An air conditioner condenser is installed on the side of this building and the compressor has failed. It was not operational at the time of the survey and should be scheduled for replacement. This project would provide for a new compressor to be installed including all required connections to utilities. The estimate includes removal and disposal of the old unit. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
9931SIT5 | CXT COMFORT STATION | 9931 | The north side of the day use area does not have a restroom. Given the distance of this area from existing restroom facilities, health concerns exist due to visitors not using the restroom facilities at other areas. It is recommended that a CXT or similar style Men's and Women's comfort station be installed which meets current ADA requirements. This project would provide for the purchase and installation of a two stall CXT restroom including an ADA compliant concrete parking and loading zone adjacent to the restroom. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
1907ENV2 | TERMITE CONTROL | 1907 | There are numerous signs throughout this building of insect infestation including Termites. Due to the potential risk of disease and damage to the building, this project provides for treatment and clean up of the insects by a licensed pest control business. It is recommended that the building be treated in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain control of the pests. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 1000
1907INT2 | COUNTERTOP REPLACEMENT | 1907 | The countertops in the kitchen are showing signs of wear and tear particularly at the Formica edges and corners. The countertops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. This project would provide funding for the removal and replacement of the countertops. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1907ENR1 | WINDOW REPLACEMENT | 1907 | The windows are original, dual pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. | RANGER RESIDENCE #1 | 9931 | CNR | Parks |  | Laughlin | 1995 | 1873 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2349ENR1 | LIGHTING UPGRADE | 2349 | The existing lighting fixtures are the older T-8 fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. T-5 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom, office, storage rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1908ADA3 | ADA RESTROOM REMODEL | 1908 | The Men's and Women's designated ADA restrooms do not entirely meet the Americans with Disabilities Act (ADA) requirements. This project would provide funding for improvements to bring the restrooms into compliance. Improvements may include adjusting existing fixtures or installing new fixtures such as sinks, toilets, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 5000
1908INT1 | INTERIOR FINISHES | 1908 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted and the ceramic tile be repaired at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1540
9931ADA2 | ADA PARKING, ACCESSIBLE ROUTE | 9931 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are several existing ADA parking spaces in the boat ramp and day use areas that are not fully compliant. This project would provide for signage, curb ramps and walkways from the parking spaces to site features. This may require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 05/05/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 02/02/2011. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 10000
2861INT1 | INTERIOR FINISHES | 2861 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RANGER RESIDENCE #2 | 9931 | CNR | Parks |  | Laughlin | 2007 | 1400 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2859EXT1 | EXTERIOR FINISHES | 2859 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco and wood, sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2C - CAMPGROUND | 9931 | CNR | Parks |  | Laughlin | 2007 | 1230 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 6150
2859INT1 | INTERIOR FINISHES | 2859 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION #2C - CAMPGROUND | 9931 | CNR | Parks |  | Laughlin | 2007 | 1230 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6150
2860EXT1 | EXTERIOR FINISHES | 2860 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the stucco, sealing the concrete masonry units and wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE STATION | 9931 | CNR | Parks |  | Laughlin | 2007 | 288 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 1440
2860INT1 | INTERIOR FINISHES | 2860 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ENTRANCE STATION | 9931 | CNR | Parks |  | Laughlin | 2007 | 288 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2861EXT1 | EXTERIOR FINISHES | 2861 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RANGER RESIDENCE #2 | 9931 | CNR | Parks |  | Laughlin | 2007 | 1400 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 7000
2862EXT1 | EXTERIOR FINISHES | 2862 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure in the next 5-6 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 CARPORT | 9931 | CNR | Parks |  | Laughlin | 2007 | 200 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 400
2349INT1 | INTERIOR FINISHES | 2349 | The interior finishes are in fair condition. It is recommended that the finished interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project does not apply to the open framed walls and ceilings in the main shop area. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1800
2349EXT1 | EXTERIOR FINISHES | 2349 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Four to Ten Years | Long-Term Needs | 3 | 8000
1908EXT2 | CONCRETE SLAB REPAIRS | 1908 | The concrete slab is settling especially at the corners and has extensive cracking. The grade is shifting away from the building, pulling the concrete with it. The settling and shifting will continue and cause extensive damage to the concrete slab and eventually to the buildings footings. This project would provide for regrading and compacting next to and underneath the slab and replacing the concrete as needed. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 5000
1908ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1908 | There is a water fountain in front of the building. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | COMFORT STATION #1 - DAY USE | 9931 | CNR | Parks |  | Laughlin | 1995 | 308 | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 4000
9931SIT7 | BOAT DOCK DECKING REPLACEMENT | 9931 | The 2x decking on the boat dock is approaching the end of its expected life and should be scheduled for replacement. The decking is warping, bending and desurfacing. It is important for the deck to be smooth and flat to avoid a safety hazard around the boats and water. This project would provide for purchase and installation of new decking for the entire boat dock. Additional bracing may be necessary to provide a solid framework depending on what product is used in the replacement. Removal and disposal of the existing deckng is included in this estimate. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
2349HVA2 | EVAPORATIVE COOLER REPLACEMENT | 2349 | An evaporative cooler is installed on the side of this building that has reached the end of it's useful and expected life and is no longer operational. This project would provide for a new commercial size evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | SHOP/MAINTENANCE BUILDING | 9931 | CNR | Parks |  | Laughlin | 1998 | 1600 | 2017-12-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
9931SIT8 | EROSION/ FLOOD CONTROL | 9931 | The water level of the Colorado river varies by as much as 9 feet depending on the flow controls from the power plants upstream. This is already causing extensive damage to the beach and Day Use areas on the north side of the site and the erosion is ongoing. Approximately 40 feet of beach has already been lost and the erosion is now threatening the ramadas, parking lot and access road. This project would provide for long term erosion controls along the north shoreline to prevent further loss of shoreline and facilities. This project may qualify for one of three FEMA grant programs to alleviate some of the high cost of the work. These are PDM (Pre-Disaster Mitigation), FMA (Flood Mitigation) or RFC (Repetitive Flood Claims) in which the State would need to provide a 25% match. | BIG BEND STATE RECREATION AREA | 9931 | CNR | Parks |  | Laughlin | 0 |  | 2017-12-13 | Immediate to Two Years | Currently Critical | 1 | 4200000
0969ENR1 | LIGHTING UPGRADE | 0969 | The existing lighting fixtures are a mix of the older fluorescent type and metal halide lamps. This project will upgrade fluorescent fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Additional light fixtures are also included in this estimate. Any electrical wiring upgrades are not included in this estimate. | ANNEX | 9932 | CultAffr | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0861EXT3 | EXTERIOR FINISHES | 0861 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 105360
0969EXT2 | EXTERIOR FINISHES | 0969 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | ANNEX | 9932 | CultAffr | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 24000
0861INT1 | INTERIOR FINISHES | 0861 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52680
0861ADA1 | INTERIOR ADA RAMP UPGRADE | 0861 | There is an ADA ramp inside the building on the North side that provides access to the main floor of the museum. The ramp does not fully meet ADA requirements, specifically the slope is greater than 1:12. This project would provide for removing the existing ramp and replacing it with a new ADA compliant ramp. Americans with Disabilities Act Accessibility Guidelines (ADAAG) Section 4.8 - 1998 was referenced for this project. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 50000
0969SFT2 | SMOKE DETECTOR UPGRADE | 0969 | According to NAC 477.915 (3), "Upon failure of a smoke detector which is powered by a battery and installed in a building owned or occupied by the state, the smoke detector must be replaced by a smoke detector which is connected to the wiring of the building and has a battery as a backup source of power." The existing smoke detectors appeared to not be working and additional smoke detectors should be installed throughout the building. | ANNEX | 9932 | CultAffr | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 6000
0861INT2 | CARPET REPLACEMENT | 0861 | The carpet in the staff office and souvenir shop is showing signs of extreme wear. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
0861INT3 | JANITORS CLOSET REPAIR | 0861 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0861SFT2 | EGRESS LIGHTING UPGRADE | 0861 | The existing emergency lights are old and in need of replacement. This project would provide for the replacement of the emergency lights inside of the facility. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 3000
0861PLM1 | WATER HEATER REPLACEMENT | 0861 | The average life span of a water heater is eight to ten years. The existing 17 gallon electric water heater in the building has reached the end of its expected life and is not energy efficient. It is recommended that a new gas appliance be installed for more efficient use of energy. This estimate includes removal and disposal of the old water heater and: 100 feet of gas pipe, fittings, couplers, and labor for installation. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0104EXT3 | EXTERIOR FINISHES | 0104 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | NELSON HOUSE | 9932 | CultAffr | M&H | NSRM | Carson City | 1935 | 720 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 7200
0104INT1 | INTERIOR FINISHES | 0104 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NELSON HOUSE | 9932 | CultAffr | M&H | NSRM | Carson City | 1935 | 720 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
0969HVA3 | HVAC INSTALLATION | 0969 | This building is used to restore historical artifacts and equipment. There is inadequate heating, no cooling and no humidification control in the building, which can adversely affect the lifespan of the artifacts and equipment. It is recommended that the heating equipment be upgraded and cooling equipment installed to maintain minimum and maximum temperatures in the building. The regulated indoor temperatures will slow down the deterioration of the building and equipment as well as provide comfort for the occupants. This project also recommends the installation of a humidification control system for the building. This project should be implemented concurrent with or following the "Building Insulation" project. | ANNEX | 9932 | CultAffr | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
1416HVA1 | HVAC INSTALLATION | 1416 | The building does not have any heating, ventilation and air conditioning (HVAC) equipment. At the time of the survey of 2008, there was a portable propane fired heater available to heat portions of the building. This is not an efficient source of heat and the extreme changes in temperature will cause accelerated deterioration of this historical building. It is recommended that the building be retrofitted with an HVAC system to maintain constant temperatures in the building. Along with this equipment, insulation should be installed according to current standards to ensure energy efficiency. An R-19 wall and R-38 ceiling insulation is suggested. The regulated indoor temperatures will slow down the deterioration of the building and provide comfort for the occupants. The estimate has been inflated to provide for costs related to design and construction of a building on the National Register of Historical Buildings. | WABUSKA DEPOT | 9932 | CultAffr | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0861EXT4 | GUTTER REPLACEMENT | 0861 | The existing gutter and downspouts around the building have numerous joints that have proven impossible to seal against leaks. There is also a large section of gutter missing on the west elevation. This project would replace the existing segmented gutter with seamless gutter and downspouts. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
9932SFT1 | INSTALL FIRE ALARM SYSTEM | 9932 | This site houses historical documents and irreplaceable artifacts related to the history of the V&T Railroad and the Comstock region. There is no fire alarm to protect these items. This project would provide for the installation of a site wide alarm system and upgrade to the existing system where applicable. The alarm controls should be centrally located in the Interpretive Center and encompass the Annex buildings, Restoration Shop, Wabuska Depot and Nelson House. Costs were based on the total square footage of the buildings. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 153528
0104SFT1 | FIRE SPRINKLER INSTALLATION | 0104 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is classified as a R occupancy. CIP 07-S03 does not currently encompass this building, but it is in the process of being added as an alternate. The estimate is based off of that project. | NELSON HOUSE | 9932 | CultAffr | M&H | NSRM | Carson City | 1935 | 720 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 12960
9932ELE2 | POLE LIGHTING INSTALLATION | 9932 | This site houses historical documents and irreplaceable artifacts related to the history of the V&T Railroad and the Comstock region as well as expensive machinery in the Restoration Shop. There is not enough lighting around the site which may be contributing to recent thefts. This project would provide funding for purchase and installation of sixteen 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. These will be installed around the entire perimeter of the site and in the parking areas. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 147264
9932SIT4 | STORAGE BUILDING | 9932 | There are a couple of fenced areas on the west side of the site for storage of rail cars, equipment and other miscellaneous items for use in the restoration efforts. The equipment is exposed to the elements and subject to theft and vandalism. This project recommends construction of a 60' x 120' storage building to provide more adequate storage for this equipment. An engineered steel building was used for this estimate. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 576000
9932SIT5 | FENCE REPLACEMENT | 9932 | The wood split rail fencing around certain areas of the site is reaching the end of its expected life. This fencing serves to keep visitors off of planted areas as well as directing people to proper walkways when traveling to and from the buildings. This project would provide funding for removal and installation of 1,320 lineal feet of two rail, 3' high cedar fencing. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 19140
9932SIT6 | SIGN REPLACEMENT | 9932 | The sign for the Railroad Museum on highway 395 is old, dilapidated and in need of replacement. Staff reported that 75% of the visitors to the museum are drive-by visitors. The new sign should be designed for better curb appeal in order to attract visitors to the museum. This project would provide funding for removal and disposal of the existing sign and replacement the sign with an aesthetically pleasing. The new sign may need to conform to Carson City and NDOT requirements due to the location on Highway 395. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9932SIT7 | SIDEWALK INSTALLATION | 9932 | There is no sidewalk from the Chamber of Commerce building to the existing walkways at the Railroad Museum. This building is an information center for visitors on activities in Carson City including the adjacent Railroad Museum. The staff has indicated that there is a need for a sidewalk between these buildings. This project would provide for the installation of 800 SF of 4" thick Portland Cement concrete sidewalk. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 8000
9932SIT8 | TURNTABLE RESTORATION | 9932 | The railroad turntable located on the south side of the site is in need of re-leveling and restoration. The structure is vital to the movement of the railroad cars and engines. It is in desperate need of repair and rehabilitation. This project would provide funding to bring the structure back to a restored fully functioning condition including timber restoration or replacement and leveling. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 150000
9932SIT9 | SLURRY SEAL ASPHALT PAVING | 9932 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 100,000 square feet of asphalt area was used to generate this estimate. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 60000
1647EXT3 | EXTERIOR FINISHES | 1647 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | COMFORT STATION | 9932 | CultAffr | M&H | NSRM | Carson City | 1990 | 373 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 3730
1416INT1 | INTERIOR FINISHES | 1416 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This work will be mostly located in the ticket office and ticket counter rooms on the North side of the building. | WABUSKA DEPOT | 9932 | CultAffr | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1437EXT3 | EXTERIOR FINISHES | 1437 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TOWER | 9932 | CultAffr | M&H | NSRM | Carson City | 1987 | 400 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 4000
0970ENR1 | LIGHTING UPGRADE | 0970 | The existing lighting fixtures are a mix of the older fluorescent type and metal halide lamps. This project will upgrade fluorescent fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Additional light fixtures are also included in this estimate. Any electrical wiring upgrades are not included in this estimate. | RESTORATION SHOP | 9932 | CultAffr | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
1416ELE1 | ELECTRICAL UPGRADE | 1416 | The building was constructed without electrical service. After relocating the structure to it's current location, the electrical system within the building has been retrofitted and rewired as the needs of the agency have changed over the years. This project would provide funding for the entire system to be upgraded to meet the evolving needs of the building. | WABUSKA DEPOT | 9932 | CultAffr | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
1416ENR1 | LIGHTING UPGRADE | 1416 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. | WABUSKA DEPOT | 9932 | CultAffr | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
1416EXT3 | EXTERIOR FINISHES | 1416 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WABUSKA DEPOT | 9932 | CultAffr | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 19200
0971EXT1 | EXTERIOR FINISHES | 0971 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | ANNEX ADDITION | 9932 | CultAffr | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 38000
0971ENV1 | HAZARDOUS MATERIALS CONTAINMENT | 0971 | There is a maintenance office and shop in the south-east corner of the building. This area has two hazardous storage containers, but is in need of two more to maintain OSHA compliance. This project provides funding for the purchase of two hazardous storage containers for this shop area. | ANNEX ADDITION | 9932 | CultAffr | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0971ENR1 | LIGHTING UPGRADE | 0971 | The existing lighting fixtures are a mix of the older fluorescent type and metal halide lamps. This project will upgrade fluorescent fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Additional light fixtures are also included in this estimate. Any electrical wiring upgrades are not included in this estimate. | ANNEX ADDITION | 9932 | CultAffr | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57000
0971HVA2 | HVAC INSTALLATION | 0971 | The building does not have any heating, ventilation and air conditioning (HVAC) equipment. It is recommended that the building be retrofitted with an HVAC system to maintain constant temperatures in the building. Along with this equipment, insulation should be installed according to current standards to ensure energy efficiency. An R-19 wall and R-38 ceiling insulation is suggested and recommended in another project. | ANNEX ADDITION | 9932 | CultAffr | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
0970EXT2 | EXTERIOR FINISHES | 0970 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | RESTORATION SHOP | 9932 | CultAffr | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Four to Ten Years | Long-Term Needs | 3 | 14000
0970SFT1 | SMOKE DETECTOR UPGRADE | 0970 | According to NAC 477.915 (3), "Upon failure of a smoke detector which is powered by a battery and installed in a building owned or occupied by the state, the smoke detector must be replaced by a smoke detector which is connected to the wiring of the building and has a battery as a backup source of power." The existing smoke detectors appeared to not be working and additional smoke detectors should be installed throughout the building. | RESTORATION SHOP | 9932 | CultAffr | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0970HVA1 | HVAC UPGRADE | 0970 | This building is used to restore historical artifacts and equipment. There is inadequate heating, no cooling and no humidification control in the building, which can adversely affect the lifespan of the artifacts and equipment. It is recommended that the heating equipment be upgraded and cooling equipment installed to maintain minimum and maximum temperatures in the building. The regulated indoor temperatures will slow down the deterioration of the building and equipment as well as provide comfort for the occupants. This project also recommends the installation of a humidification control system for the building. | RESTORATION SHOP | 9932 | CultAffr | M&H | NSRM | Carson City | 1980 | 6400 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
1647INT1 | INTERIOR FINISHES | 1647 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | COMFORT STATION | 9932 | CultAffr | M&H | NSRM | Carson City | 1990 | 373 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1865
9932SIT3 | PAVE FIRE ACCESS ROAD | 9932 | The site is served by dirt and gravel fire access roads, which are often impassable in inclement weather. The 2006 International Fire Code 503.2 addresses requirements for all-weather access roads. This project would provide for the installation of asphalt concrete paving and compacted base on the fire access road surrounding the site. Final acceptance falls to the responding fire authority, which should be consulted for additional local requirements if required prior to beginning design and construction. Additional comments by the Fire Marshal's office may impact final cost. The unit costs were adjusted for a thicker base and finish to support the loads of response equipment. 5" of asphalt and 8" of base was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 195000
9932SEC2 | REPLACE EXTERIOR DOORS AND OPENERS | 9932 | Problems exist with the exit doors and overhead doors at the Annex, Annex Addition, and Restoration Shop. Most of the doors are original equipment. Repairs to these doors is difficult because the doors are no longer manufactured or they are custom sizes. This project recommends replacing the overhead doors with motorized equipment and controls. The exit doors should be replaced with a commercial grade door system with locks to match the existing site master lock system. Estimates are based on 10 overhead doors, at $8,000.00 each, and 8 exit doors at $4,000.00 each. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
0969INT1 | INSTALL BUILDING INSULATION | 0969 | This building has no insulation. The temperature extremes are contributing to accelerated decay of the contents, which include railroad cars and other historical artifacts awaiting restoration and/or display. This project will install batt insulation in the walls and ceilings to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX | 9932 | CultAffr | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
0969EXT1 | REROOF BUILDING | 0969 | Half of the building was re-roofed recently with a single-ply membrane system. The remaining original metal roof was in fair condition at the time of the survey. The rest of this building should be re-roofed as soon as possible to match the age and type of membrane as close as possible. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX | 9932 | CultAffr | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90000
9932SEC1 | INSTALL SECURITY ALARM SYSTEM | 9932 | This site houses historical documents and irreplaceable artifacts related to the history of the V&T Railroad and the Comstock region. There is no security alarm to protect these items. This project would provide for the installation of a sitewide security system. The alarm controls should be centrally located in the Interpretive Center and encompass the Annex buildings, Restoration Shop, Wabuska Depot and Nelson House. Costs were based on the total square footage of the buildings. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 127940
0971INT1 | INSTALL BUILDING INSULATION | 0971 | This building has no insulation. The temperature extremes are contributing to accelerated decay of the contents, which include railroad cars and other historical artifacts awaiting restoration and/or display. This project will install batt insulation in the walls and ceilings to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. R-19 for walls and R-38 for ceilings is recommended. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX ADDITION | 9932 | CultAffr | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66500
1416SFT1 | FIRE SPRINKLER INSTALLATION | 1416 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is classified as a B occupancy. This project is in design under CIP 07-S03 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | WABUSKA DEPOT | 9932 | CultAffr | M&H | NSRM | Carson City | 1906 | 1920 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 34560
0861SFT1 | FIRE SPRINKLER INSTALLATION | 0861 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is partially classified as a B occupancy. This project is in design under CIP 07-S03 and the estimate is based off of that project. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Immediate to Two Years | Currently Critical | 1 | 189648
0861ELE1 | LIGHTING UPGRADE | 0861 | The museum's existing lighting fixtures are a mixture of T-8 and T-12 ballasted fluorescent lights, high pressure lighting, and track display units. This project will upgrade general lighting fixtures in the offices and common areas to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. The project provides a modular track lighting system for display areas, permitting the option of general or pinpoint lighting, depending on the illumination needs at the time. Additional funds are included to provide color corrected and specialty lights for these new fixtures. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84288
0861HVA1 | HVAC SYSTEM REPLACEMENT | 0861 | This building is used to store and display historical artifacts and equipment. There is inadequate heating, no cooling and no humidification control in the building, which can adversely affect the lifespan of the artifacts and equipment. Of the four suspended heaters, two are due for replacement. It is recommended that the heating equipment be upgraded and cooling equipment installed to maintain minimum and maximum temperatures in the building. The regulated indoor temperatures will slow down the deterioration of the building and equipment as well as provide comfort for the occupants. This project also recommends the installation of a humidification control system for the building and replacement of the non-operational ceiling fans. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | JACOBSEN INTERPRETIVE CENTER | 9932 | CultAffr | M&H | NSRM | Carson City | 1988 | 10536 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0969INT2 | INSTALL CONCRETE WALKWAYS | 0969 | The building interior has a mix of dirt and concrete floors. This project recommends concrete flat work be installed for the main walkways between the rail cars. This project would provide for the installation of 4,000 SF of 4" thick concrete sidewalk. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX | 9932 | CultAffr | M&H | NSRM | Carson City | 1978 | 13600 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0971INT2 | INSTALL INTERIOR CONCRETE WALKWAYS | 0971 | The majority of the building interior has dirt floors. This project recommends concrete flat work be installed for the main walkways between the rail cars. This project would provide for the installation of 3,200 SF of 4" thick concrete sidewalk. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | ANNEX ADDITION | 9932 | CultAffr | M&H | NSRM | Carson City | 1997 | 19000 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
1647EXT2 | REPLACE ROOF | 1647 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. The extreme temperature fluctuations throughout the year, consistent wind and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next two to four years with a 50 year asphalt composition roofing shingle and new underlayments. Color to match the other structures on site This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | COMFORT STATION | 9932 | CultAffr | M&H | NSRM | Carson City | 1990 | 373 | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5595
9932ELE1 | ELECTRICAL UPGRADE | 9932 | The buildings at the site share a common electrical transformer and feed off the main service panel. The main panel and sub panels for the Annex and Restoration Shop are at their maximum capacity. This project recommends replacing and upgrading the main service panel and sub panels at the Annex, Annex Addition and Restoration Shop to provide needed additional capacity. This estimate assumes that the existing underground conduit feed could be used, therefore, no earthwork is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/13/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/17/2008. | NEVADA STATE RAILROAD MUSEUM CC SITE | 9932 | CultAffr | M&H | NSRM | Carson City | 0 |  | 2017-09-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
9933SIT1 | WEED ABATEMENT | 9933 | Most of the site is covered with weeds. This project would provide for the removal and disposal of the weeds on the site and treatment of the area with an herbicide to control future weed growth. | ELY WILDLIFE OLD FIELD OFFICE SITE | 9933 | Wildlife |  |  | Ely |  |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0635SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0635 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5760
0635INT1 | INTERIOR FINISHES | 0635 | The interior finishes are in fair to poor condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0635EXT1 | EXTERIOR FINISHES | 0635 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls, wood trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
9933SIT2 | ASPHALT PAVING INSTALLATION | 9933 | The access road and parking areas on the site are not paved. Any existing concrete or asphalt paving has deteriorated to the point of complete failure. This project would provide asphalt cement paving for a 20' wide access road and parking spaces. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | ELY WILDLIFE OLD FIELD OFFICE SITE | 9933 | Wildlife |  |  | Ely |  |  | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37500
0635SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0635 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 10080
0635PLM1 | PLUMBING SYSTEM REPLACEMENT | 0635 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines, the plumbing fixtures and the septic system. This estimate includes removal and disposal of the existing system as required. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0635SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0635 | There are no emergency egress lights or exit signs in the building. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0635INT2 | FLOORING REPLACEMENT | 0635 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. The flooring should be tested for asbestos containing materials (ACM) and additional costs should be added if it is necessary to abate it. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
0635EXT3 | EXTERIOR DOOR REPLACEMENT | 0635 | The 3 exterior wood doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0635EXT2 | WINDOW REPLACEMENT | 0635 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0635ELE1 | ELECTRICAL UPGRADE | 0635 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. If occupied, it would be utilized to its current maximum potential. The electrical panels and receptacles would be at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0635ENV1 | UNDERGROUND TANK REMOVAL | 0635 | At the south exterior wall there is an underground heating oil fuel tank that is no longer needed because new propane-fired equipment will be installed. This project allows for removal of the underground tank and associated soils surrounding the installation. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 15000
0635HVA1 | HVAC EQUIPMENT REPLACEMENT | 0635 | The oil fired furnace is original to the building and is no longer operational. There is no other HVAC equipment in the building. This project would provide for installation of a new HVAC packaged unit to provide heating and cooling, cleaning of the existing duct work and replacement of the vent grilles. This project includes removal and disposal of the existing furnace and all required connections to utilities. Propane gas service will be required and is included in the cost. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28800
0635ENR1 | LIGHTING UPGRADE | 0635 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2160
0636EXT3 | OVERHEAD DOOR REPLACEMENT | 0636 | There are two 10'x10' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with new manually operated coiling doors. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0636SFT1 | FIRE ALARM SYSTEM INSTALLATION | 0636 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 3072
0635SFT4 | EXTERIOR LANDING INSTALLATION | 0635 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The two doors on the east side of the building do not comply with this code and pose a safety hazard. This project would provide for the installation of a compliant landing for each door. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 2000
0636SFT2 | EXTERIOR LANDING INSTALLATION | 0636 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the north side of the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 1000
0635EXT4 | OVERHEAD DOOR REPLACEMENT | 0635 | There are two 8'x8' overhead doors on the east side of the building which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead doors and replacement with two new manually operated overhead doors. Removal and disposal of the existing doors is included in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0635INT3 | INTERIOR DOOR REPLACEMENT | 0635 | The interior doors in this building are hollow core units and are damaged or missing altogether. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 5 interior doors was used in this estimate. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0635ADA1 | ADA SIGNAGE | 0635 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 500
0635INT4 | CEILING REPLACEMENT | 0635 | The ceiling in the building is covered with acoustical ceiling tiles. The ceiling tiles are damaged and stained and some are coming loose from the substrate. This project would provide for the replacement of the ceiling tiles. Removal and disposal of the existing tiles is included in this estimate. The ceiling tiles and adhesive should be tested for asbestos containing materials (ACM) and additional costs should be added if it is necessary to abate it. | OLD WILDLIFE ADMINISTRATIVE OFFICE | 9933 | Wildlife |  |  | Ely | 1955 | 1440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
0636EXT1 | EXTERIOR FINISHES | 0636 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0636EXT2 | EXTERIOR DOOR REPLACEMENT | 0636 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | WILDLIFE STORAGE/GARAGE | 9933 | Wildlife |  |  | Ely | 1950 | 768 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0620ENV1 | ABANDON SEPTIC TANK | 0620 | The Office building was connected to the city sewer system in 1998 and disconnected from the on-site septic system. There is no record of the existing septic system having been demolished. This project provides funds to pump and fill the old tank in compliance with state health regulations. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0620INT0 | FLOORING REPLACEMENT | 0620 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0620ENR1 | LIGHTING UPGRADE | 0620 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12620
0619ENR1 | LIGHTING UPGRADE | 0619 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7320
9934SIT2 | SIDEWALK REPLACEMENT | 9934 | The sidewalks serving the buildings and vehicle storage areas on this site are deteriorated and failing. In some areas cracks wider than four inches have been identified, and there is settling in many locations. The accessible route from the parking space to the entrance of the building is also compromised by the failing concrete. This project addresses removal and replacement of existing sidewalks as needed. 1,200 SF of 4" thick concrete sidewalk was used for this estimate. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0620ADA1 | ADA RESTROOM REMODEL | 0620 | The building does not have an accessible restroom. The existing restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, exhaust fans, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 30000
0619ENV2 | RESTROOM REMODEL | 0619 | The restroom in the building is original to the building and in overall poor condition. The finishes, fixtures, toilet, sink and shower are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0619SFT3 | INTERIOR STAIRWAY REPLACEMENT | 0619 | The stairs and handrails between the first floor and the storage mezzanine do not meet the requirements in the 2012 International Building Code sections 1009 and 1012. This project would provide funding to remove and replace the stairway and handrail. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 9000
0619SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0619 | The emergency egress lighting is insufficient and the exit signs are made of paper and do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2440
0619SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0619 | The building is an H-4 occupancy per the 2012 International Building Code. Pursuant to IBC 903.2.5.1, an automatic sprinkler system shall be installed in Group H occupancies. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 68320
9934ELE1 | GENERATOR INSTALLATION | 9934 | The site does not have an emergency back-up generator. As an emergency management facility, it is important to have backup power to the buildings. This project would provide for a new diesel powered 150 KVA generator including required connections to utility systems. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0619ENV3 | GREASE/ SAND INTERCEPTOR INSTALLATION | 0619 | The shop has a wash area for vehicles which drains into the city sewer. There is no evidence that a grease/ sand interceptor is provided. This project recommends installing a grease/ sand interceptor in accordance with state health regulations. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
2323SFT1 | LATH HOUSE REPAIRS | 2323 | The Lath House is deteriorated and requires basic maintenance and some structural repairs. There is earth to wood contact, warping of the boards and dry rot. It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for repairs and painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF LATH HOUSE | 9934 | CNR | Forestry |  | Elko | 1981 | 3000 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2323ENV1 | BACKFLOW PREVENTION | 2323 | The existing Lath House structure includes an irrigation system to water the plants and trees. State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of backsiphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF LATH HOUSE | 9934 | CNR | Forestry |  | Elko | 1981 | 3000 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9934ADA2 | ADA PARKING SPACE | 9934 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space does not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking space up to code including removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 5000
9934PLM1 | SANITARY SEWER LINE REPLACEMENT | 9934 | The sanitary sewer line leading from the Shop to the Office is failing and should be scheduled for replacement. The pipe is not sloped properly which causes backups and clogging. In cold temperatures, the pipe has frozen and broken at least twice. This project would provide for the complete replacement of the sanitary sewer line from the Shop to the Office. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9934SIT9 | CRACK FILL & SEAL ASPHALT PAVING | 9934 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. It is recommended that this project coincide with the ADA Parking Space project. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Four to Ten Years | Long-Term Needs | 3 | 30000
9934SIT3 | DRAINAGE UPGRADES | 9934 | The grade across the site does not slope away from the buildings effectively which allows water to infiltrate the buildings to some extent. Water also pools up next to the buildings and damages the exterior finishes and foundations. Sand bags have been used during heavy rains to protect the buildings. This project would create positive flow away from the buildings by regrading, paving and installing additional drainage swales as needed. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0619EXT2 | ROOF REPLACEMENT | 0619 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 58560
0619EXT4 | OVERHEAD DOOR REPLACEMENT | 0619 | There is one 12'x14' and two 10'x10' overhead garage doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. The springs, rollers and hinges are worn from general wear and tear. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead garage doors and replacement with new manually operated overhead garage doors. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0619INT4 | CONCRETE FLOORING REHABILITATION | 0619 | The concrete flooring in the building has extensive cracking and is due for repairs. This project would provide for crack-filling, patching and sealing the concrete flooring in the building. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21900
0619EXT3 | EXTERIOR DOOR REPLACEMENT | 0619 | The 5 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0619EXT5 | CONCRETE APRON REPAIRS | 0619 | The 3 exterior concrete aprons and sidewalks around the building have extensive cracking and are due for repairs. This project would provide for crack-filling, patching and sealing the concrete aprons at the vehicle garage doors and the sidewalks and pads around the building. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0619INT3 | VCT FLOORING REPLACEMENT | 0619 | The VCT (vinyl composite tile) flooring in the office space is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0619INT5 | INTERIOR DOOR REPLACEMENT | 0619 | The interior doors in this building are damaged and do not function properly. There are 3 hollow core wood doors and 3 hollow core metal doors. This project would provide for the installation of new metal solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 6 interior doors was used in this estimate. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0620SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0620 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 71176
0620PLM1 | WATER HEATER REPLACEMENT | 0620 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0620HVA3 | HEATING UPGRADES | 0620 | The radiant heating equipment in the Garage is insufficient for the extreme temperatures in the area. The Garage is uncomfortably cold in the winter. It is recommended to install additional propane-fired heating equipment in the Garage to ensure a comfortable work environment. This project would provide for the purchase and installation of three natural gas fired heaters including all required connections to existing utilities. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0620HVA2 | AIR CONDITIONER INSTALLATION | 0620 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0620SFT3 | FIRE ALARM SYSTEM INSTALLATION | 0620 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 20336
0620SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0620 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2542
0619HVA2 | HVAC REPLACEMENT | 0619 | The existing HVAC system consists of ceiling mounted heaters and does not have any cooling equipment other than a small wall-mounted air conditioner for the office. The equipment is not energy efficient and has reached the end of its expected and useful life. There is a need for cooling equipment as well to provide a comfortable work environment in the summer. The new system shall be designed to significantly reduce electrical and propane gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project would provide for replacing the existing heaters and installing evaporative coolers for cooling. This project or a portion thereof was previously recommended in the FCA reports dated 08/21/2002 and 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29280
9934ADA1 | MEMORIAL TREE GROVE ACCESSIBILITY | 9934 | The site has a public trail system for the Mike P. Jordan Memorial Tree Grove located adjacent to the Lath House. The 36" wide trail consists of 2"x6" wood curbing filled with pea gravel. This area is frequented by the public including school children on field trips. The trail is not accessible and does not meet the criteria for Americans with Disability Act (ADA). This project would provide for the installation of a 2" thick polymer based pavement system for the trail system to provide accessibility through the tree grove. A product under the brand name PolyPavement was used as a pricing guide for this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 9000
0619INT2 | INTERIOR FINISHES | 0619 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
0620ELE1 | MINOR ELECTRICAL REPAIRS | 0620 | The building has several electrical outlets and switches missing covers, extension cords being used to supply electrical power, and nonmetallic sheathed cable being used in the attic. This project would provide funding to replace broken or missing covers, install a dedicated electrical outlet to the computer server and to replace the nonmetallic sheathed cable being used in the attic. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0619ELE1 | ELECTRICAL REPAIRS | 0619 | There are many safety issues throughout the building having to do with electrical fixtures and equipment. There are numerous electrical outlets and switches which are missing covers or are broken, extension cords being used to supply permanent electrical power, the GFCI outlet in the restroom is broken and the exterior outlets are not GFCI protected and are missing covers. This project would provide for repairs and/ or replacement of the damaged electrical outlets and removing extension cords from permanent locations. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0619HVA1 | RESTROOM EXHAUST FAN | 0619 | The existing exhaust fan in the restroom is original equipment and does not provide adequate ventilation. This project would provide for the removal of the existing exhaust fan assembly and the purchase and installation of a new exhaust fan assembly including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 3000
0619INT1 | INTERIOR LANDING INSTALLATION | 0619 | The west side of the shop has an exit door with an interior landing approximately 6" below the exterior landing. Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door. There is a wood ramp constructed to eliminate the step down but it has created a tripping hazard and does not meet code. This project would provide funding to pour a 3'-0"x3'-0" concrete landing on the interior of the building to eliminate the tripping hazard. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 2500
0619STR1 | STRUCTURAL ASSESSMENT | 0619 | A storage area has been constructed inside of the metal shop building accessed via a wood stair case. The 2003 ICC has a minimum requirement of 125 p.s.f. for light storage in non-residential spaces. There is no record of a CIP project or structural plans for this construction and could be a potential safety issue due to collapse. This project recommends that a licensed engineer perform a structural investigation to assess the load carrying capacity of this area. Future projects would be based on this report. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 5000
0619EXT1 | EXTERIOR FINISHES | 0619 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24400
0620ADA3 | ADA SIGNAGE | 0620 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0619SFT7 | FIRE ALARM SYSTEM INSTALLATION | 0619 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 19520
0620EXT2 | EXTERIOR DOOR REPLACEMENT | 0620 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0620INT1 | INTERIOR FINISHES | 0620 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25420
0620EXT1 | EXTERIOR FINISHES | 0620 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5084
0620EXT3 | GUTTER REPLACEMENT | 0620 | The existing gutters and downspouts on the building are damaged and should be scheduled for replacement. They have numerous joints that have proven impossible to seal against leaks and have been bent and broken over time. The leaking gutters will cause premature deterioration to the building finishes and the site hardscape. This project would replace the existing segmented gutter with seamless gutter and new downspouts. It is recommended to extend the downspouts at least 5'-0" away from the building exterior. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17500
0619SFT8 | SAFETY CABINETS | 0619 | The Shop contains many different paints, stains, oils, vehicle repair fluids, cleaning products and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 10000
0619ENR2 | WINDOW REPLACEMENT | 0619 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 7 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5250
0619ENV4 | SPILL CONTAINMENT | 0619 | The Shop does not have a method for containing spills or leakage from oil drums. This project would add secondary containment pallets for all containers in the building and install placards on the building exterior. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 3500
0619EXT6 | COOK SHED DEMOLITION | 0619 | The Shop has a small Cook Shed addition on the north side of the structure. It contains numerous code and safety issues including but not limited to broken windows, broken or missing electrical fixtures, temporary metal and wood flooring, dry rot, cooking and washing dishes without proper equipment or ventilation and no life safety systems. The addition is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the addition. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
0620ADA2 | KITCHENETTE REPLACEMENT | 0620 | The sink, faucet and associated cabinets in the hallway are original to the building. This project recommends the replacement of the existing kitchenette with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes disposal of the existing materials. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0620EXT4 | WINDOW REPLACEMENT | 0620 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 12 units. Removal and disposal of the existing windows is included in this estimate. | NDF NORTHERN REGION 2 OFFICE/GARAGE | 9934 | CNR | Forestry |  | Elko | 1980 | 5084 | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9934SIT7 | SITE BOLLARDS | 9934 | The Regional Office building has three large apparatus bay doors for fire fighting equipment. The paved approach does not have any protection to prevent vehicles from damaging the building. This project would provide for six 8" diameter pipe bollards, filled with concrete at each side of the apparatus bay doors. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0619SFT6 | VEHICLE EXHAUST EXTRACTION SYSTEM | 0619 | The Shop Building services and repairs vehicles for use by NDF. There is no exhaust extraction system which removes toxic exhaust fumes. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | NDF NORTHERN REGION 2 SHOP | 9934 | CNR | Forestry |  | Elko | 1981 | 4880 | 2013-09-19 | Immediate to Two Years | Currently Critical | 1 | 50000
9934SIT8 | WHEEL STOPS | 9934 | The Regional Office building has parking for employees along the west side of the apparatus bay portion of the building. The parking spaces lack wheel stops to prevent vehicles from damaging the structure. This project would provide for the installation of concrete wheel stops along the parking area. This project or a portion thereof was previously recommended in the FCA report dated 09/28/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/19/2013. | ELKO NORTHERN REGION 2 NDF HDQS. SITE | 9934 | CNR | Forestry |  | Elko |  |  | 2013-09-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1312EXT1 | EXTERIOR FINISHES | 1312 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
1313SFT2 | REMODEL FRONT ENTRY / STAIRWAY | 1313 | The existing front entry to the residence has a non conforming stairway and landing. The entry floor is cantilevered above grade and is supported by two posts sitting on an exposed concrete pier. This project would provide for a new concrete pier / foundation support for the floor and new landing and stairs, wood framed stairs with handrails and a concrete slab-on-grade landing at the bottom. The other entry is similar and is also recommended to be replaced. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 4000
1311EXT1 | EXTERIOR FINISHES | 1311 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | UTILITY SHED | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 200 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
1313EXT2 | REPAIR VINYL SIDING | 1313 | The north side of the building had an attached carport that has since been removed. The vinyl siding was installed before the carport was removed and the siding does not extend up the entire wall. This project recommends removing the old wood siding at the gable end and installing vinyl siding to match the rest of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1312INT1 | INTERIOR FINISHES | 1312 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
1313INT1 | INTERIOR FINISHES | 1313 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 3 to 4 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
1602EXT1 | EXTERIOR FINISHES | 1602 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, block sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESTROOM #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1980 | 200 | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 1000
9935EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9935 | There are steel shade ramadas in different locations throughout the site which measure about 12'x12' each. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures. This project should be done on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/7/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 7/23/2014 | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 3400
9935SIT3 | CRACK FILL / SLURRY SEAL ASPHALT PAVING | 9935 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 120,000 square feet of asphalt area was used to generate this estimate which includes the new paving in the campgrounds. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 72000
2317EXT1 | EXTERIOR FINISHES | 2317 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE GARAGE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 2002 | 900 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2316INT1 | INTERIOR FINISHES | 2316 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 3 to 4 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE GARAGE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1990 | 672 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
1602INT1 | INTERIOR FINISHES | 1602 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/20/2003 and 05/29/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 10/28/2015. | RESTROOM #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1980 | 200 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1316EXT1 | EXTERIOR FINISHES | 1316 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, block sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #3 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
9935SIT2 | AC PAVING INSTALLATION | 9935 | The AC paving behind the visitors center has failed and is in need of replacement. This project would provide for the removal of the damaged paving and installation of new 3" thick AC paving over a compacted base. It may be possible to grind in place the damaged paving and use for base which could reduce project cost. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Four to Ten Years | Long-Term Needs | 3 | 93750
1316INT1 | INTERIOR FINISHES | 1316 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 2 to 3 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #3 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
1315EXT1 | EXTERIOR FINISHES | 1315 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1315EXT3 | REPLACE OVERHEAD COILING DOORS | 1315 | There are four 12'x10' overhead coiling doors which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with two motorized doors. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
1313EXT1 | EXTERIOR FINISHES | 1313 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11520
2316EXT1 | EXTERIOR FINISHES | 2316 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 3 to 4 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESIDENCE GARAGE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1990 | 672 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
1315INT1 | INTERIOR FINISHES | 1315 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17000
1315ADA1 | ADA PARKING UPGRADE | 1315 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The main entrance to the building has an ADA parking stall which does not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking area up to code including a compliant path of travel from the parking space to the building entrance, updated signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 5000
1314INT1 | INTERIOR FINISHES | 1314 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 507 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2535
1315HVA1 | HVAC UPGRADE | 1315 | The building is heated by a propane fired forced air unit installed in 1982. It is original to the building and has reached the end of its expected life. This project would provide for replacement of the heater and includes removal and disposal of the existing unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1315EXT2 | WINDOW REPLACEMENT | 1315 | There are six windows in the building approximately 3'x7' with an exposed bottom edge less than 18" above the floor. IBC 2012 - Section 2406 requires these windows to have safety glass labeled due to their hazardous location. This project recommends replacing the windows with safety glazed windows. This estimate is for the replacement of 6 units. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1315SFT3 | INSTALL EXIT SIGNS AND EGRESS LIGHTING | 1315 | The building does not have any exit signs or emergency lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency exit lighting to provide illumination along the egress route. IBC - 20012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 3500
1315SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1315 | This building is lacking a fire alarm and detection system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 17000
1315SFT1 | INSTALL FIRE SUPPRESSION SYSTEM | 1315 | This building does not have an automatic fire suppression system. Nevada State Fire Marshal NAC 477.915 (c) requires buildings having a floor area exceeding 12,000 s.f. on any floor or 24,000 s.f. on all floors, or which contain a B or R-1 occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of, or addition to the building. Backflow prevention is included in this estimate. This building is partially classified as a B occupancy. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | PARK OFFICE/SHOP | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 3400 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 47600
1316ADA2 | ADA IMPROVEMENTS | 1316 | The existing restrooms and parking area are in need of some minor ADA accessibility upgrades. This project would provide for a no parking sign to be installed at the access isle, restroom signage, plumbing jackets on the sinks, and the installation of grab bars in the restroom containing the ADA accessible shower. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | RESTROOM #3 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 400 | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 5000
1314EXT1 | EXTERIOR FINISHES | 1314 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, block sealing, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/23/2014. | RESTROOM #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 507 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2535
9935ADA1 | SITE ADA ISSUES | 9935 | The parking in the Day Use area and the route of travel from the parking space to the accessible picnic table are not fully ADA compliant. It is recommended that the parking area and route of travel be made accessible including updated signage. A concrete ADA parking space is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2002 and 11/7/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 7/23/2014 | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 10000
1313HVA1 | HVAC REPLACEMENT | 1313 | There is an existing propane fired furnace that is approaching 20 years old and is in need of replacement. This project would provide for the removal and disposal of the old unit and installation of a new propane gas fired furnace including all required connections to existing utilities. Cleaning of the existing ductwork is also included in this estimate. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1313INT3 | REPLACE FLOORING | 1313 | The existing carpet and vinyl flooring has reached the end of it's useful life. This project would provide for the removal and disposal of the existing flooring and installation of new vinyl and carpet flooring throughout the residence. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1312INT2 | REPLACE FLOORING | 1312 | The existing carpet and vinyl flooring has reached the end of it's useful life. This project would provide for the removal and disposal of the existing flooring and installation of new vinyl and carpet flooring throughout the residence. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1313ENR1 | WINDOW REPLACEMENT | 1313 | The existing windows are old aluminum dual pane type and are in need of replacement. This project would provide for the removal and disposal of the existing windows and installation of new vinyl dual pane window units. A total of 9 window units was used for this estimate. | RESIDENCE #2 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1312HVA1 | HVAC REPLACEMENT | 1312 | There is an existing propane fired furnace that is approaching 20 years old and is in need of replacement. This project would provide for the removal and disposal of the old unit and installation of a new propane gas fired furnace including all required connections to existing utilities. Cleaning of the existing ductwork is also included in this estimate. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1312ENR1 | WINDOW REPLACEMENT | 1312 | The existing windows are old aluminum dual pane type and are in need of replacement. This project would provide for the removal and disposal of the existing windows and installation of new vinyl dual pane window units. A total of 9 window units was used for this estimate. | RESIDENCE #1 | 9935 | CNR | Parks |  | Wild Horse SRA | 1982 | 2304 | 2014-07-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
9935SIT5 | WATER STORAGE TANK REPLACEMENT | 9935 | There is a 10,000 gallon underground water storage tank that is leaking and no longer in use according to staff. This project would provide for the removal of the existing tank and installation of a new 10,000 gallon water storage tank including all required excavation and connections to existing water system. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 27500
9935SIT6 | WELL SYSTEM TELEMETRY REPLACEMENT | 9935 | The existing well water telemetry system is no longer operational. Staff has to manually activate well pumps to fill tanks. This is not efficient. This project would provide for a new telemetry system including software to be installed. | WILD HORSE STATE RECREATION AREA SITE | 9935 | CNR | Parks |  | Wild Horse SRA |  |  | 2014-07-23 | Immediate to Two Years | Currently Critical | 1 | 10000
9936SIT4 | FISH CLEANING STATION INSTALLATION | 9936 | There is no fish cleaning station installed at the site. This equipment is important to have on site because it reduces environmental hazards that would be prevalent without the equipment and also encourages people to visit the park for its convenient facilities. The estimate includes 2,500 feet of piping from the campground to the main water line. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
9936SIT1 | ASPHALT PAVING INSTALLATION | 9936 | The campground loop and the individual campsite parking areas are not currently paved. This project would provide asphalt paving for a 10' wide access road around the campground and 10' wide parking spaces at each campsite. The estimate includes grading, compaction and installation of 4" thick asphalt cement. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 364000
9936EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9936 | There are 59 steel shade ramadas in different locations throughout the site for a total of 8,864 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures. This project should be done on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3456
9936SIT3 | BOAT DOCK AND RAMP REPLACEMENT | 9936 | The boat dock and concrete ramp are approaching the end of their expected life due to extreme climatic conditions and heavy use. The existing ramp and dock should be scheduled for replacement. The concrete ramp is cracking and spalling. It is important for the concrete to be in good shape to insure proper traction for tow vehicles and to prevent accidents. This project would provide for purchase and installation of a new boat dock and concrete ramp. Removal and disposal of the existing concrete ramp and dock is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
2737EXT1 | EXTERIOR/ INTERIOR FINISHES | 2737 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | FISHERMAN'S POINT CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 98 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245
2753EXT1 | EXTERIOR FINISHES | 2753 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | IRRIGATION PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 144 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
9936SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9936 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 312,000 square feet of asphalt area was used to generate this estimate which includes the new paving in the campground. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187200
3352EXT1 | EXTERIOR FINISHES | 3352 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE 1 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
0546INT1 | INTERIOR FINISHES | 0546 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
0580HVA1 | HEATER REPLACEMENT | 0580 | There is an electric heater in the chlorinator room that is no longer operating. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2301INT1 | INTERIOR FINISHES | 2301 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2301EXT2 | EXTERIOR DOOR REPLACEMENT | 2301 | The exterior wood man door appears to be original to the building. It is damaged from age and general wear and tear. The frame has not held up over time and is causing the door to bind. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2321ADA1 | ADA SIGNAGE & STRIPING | 2321 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The asphalt parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | EAST BOAT RAMP CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 0 | 250 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 1500
2737ADA1 | ADA PARKING INSTALLATION | 2737 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | FISHERMAN'S POINT CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 98 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
3350EXT1 | EXTERIOR/ INTERIOR FINISHES | 3350 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | SADDLE DAM CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2008 | 98 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 245
3353INT1 | INTERIOR FINISHES | 3353 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE 2 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
3351EXT1 | EXTERIOR/ INTERIOR FINISHES | 3351 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | COYOTE COVE CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2014 | 196 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 490
3353EXT1 | EXTERIOR FINISHES | 3353 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE 2 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
3352INT1 | INTERIOR FINISHES | 3352 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE 1 | 9936 | CNR | Parks |  | South Fork SRA | 2012 | 1500 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 7500
3354EXT1 | EXTERIOR FINISHES | 3354 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK | 9936 | CNR | Parks |  | South Fork SRA | 0 |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0580EXT2 | EXTERIOR DOOR REPLACEMENT | 0580 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the two exterior doors with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3350ADA1 | ADA PARKING INSTALLATION | 3350 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SADDLE DAM CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 2008 | 98 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0547EXT1 | EXTERIOR FINISHES | 0547 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17320
2321EXT1 | EXTERIOR/ INTERIOR FINISHES | 2321 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | EAST BOAT RAMP CXT RESTROOM | 9936 | CNR | Parks |  | South Fork SRA | 0 | 250 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 625
2301EXT1 | EXTERIOR FINISHES | 2301 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing and staining the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be stained and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2301HVA1 | HEATER INSTALLATION | 2301 | The building is heated by several small wall mounted electric heaters. These units were not installed as part of the original building design and are insufficient for their application. This project provides for purchase and installation of propane fired heaters and associated connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | GARAGE/STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA |  | 1200 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5200
2300EXT1 | EXTERIOR FINISHES | 2300 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | WEST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 100 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2300INT1 | INTERIOR FINISHES | 2300 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | WEST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 100 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2299EXT1 | EXTERIOR FINISHES | 2299 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | EAST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 40 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
2299INT1 | INTERIOR FINISHES | 2299 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | EAST FEE BOOTH | 9936 | CNR | Parks |  | South Fork SRA |  | 40 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
0581EXT1 | DEMOLISH STRUCTURE | 0581 | This building is not currently being used. It contains numerous code and safety issues including but not limited to rodent infestation, broken windows, broken or missing electrical fixtures, dry rot and possible structural damage due to the age. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition and disposal of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SHOP (VACANT) | 9936 | CNR | Parks |  | South Fork SRA | 1937 | 912 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9120
0580EXT1 | EXTERIOR FINISHES | 0580 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units, painting the wood and metal trim and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 520
2741EXT1 | EXTERIOR/ INTERIOR FINISHES | 2741 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #3 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 490
0578EXT1 | EXTERIOR FINISHES | 0578 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | STORAGE BUILDING | 9936 | CNR | Parks |  | South Fork SRA | 1937 | 1064 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5320
9936SIT5 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9936 | The visitors parking lot, maintenance yard and carport parking area have insufficient lighting. This project would provide for the installation of 10 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
0547SIT1 | CONCRETE PAVING INSTALLATION | 0547 | The building could use sidewalk upgrades and additional concrete around the exterior and under the carport. Some of the existing concrete is cracked and failing and is due for replacement. There are unpaved areas around the exterior of the building that staff walk on regularly. Areas around the building are walked on often and are not paved. The four-bay carport on the North side of the building is not paved and the dirt is insufficient for the heavy use and extreme climate. The drainage away from the building is also insufficient due to erosion of the dirt which also makes it difficult to remove snow from the perimeter of the building. This project would provide for 2,000 square feet of concrete to replace deteriorated concrete sidewalks, installation of new concrete sidewalks, installation of proper parking spaces under the carport and improved drainage. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0547ADA1 | ADA SIGNAGE | 0547 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0580SFT1 | CHLORINE ALARM INSTALLATION | 0580 | The pump house has two rooms, one houses the water pump and the other houses the chlorination system. There is a monitoring and alarm system for the pump, but not for the chlorination system. This project would provide for a continuous area monitoring and alarm system to be installed to detect a chlorine leak in the chlorination system. The audible and visual alarm should be mounted on the exterior of the building. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0547SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0547 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0547ENR1 | LIGHTING UPGRADE | 0547 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5196
0547ELE1 | ELECTRICAL UPGRADE IN SHOP | 0547 | This building was constructed before the high demand for electrical services were needed for shop equipment and computers. As time has progressed, the shops electrical demand and equipment has changed and is now lacking sufficient electrical outlets. This project would provide for the purchase and installation of 10 additional duplex outlets. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
9936PLM2 | ISOLATION VALVE REPLACEMENT | 9936 | Two of the isolation valves for the site are no longer operating correctly. The main water line that serves each of the buildings on the site is in need of an isolation valve. This will allow the maintenance staff to do repairs to the plumbing without shutting down the whole site. More importantly, a leak in the building can be shut down quickly minimizing damage in an emergency. This estimate provides for a 2-1/2" gate valve to be installed at each building. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2741ADA1 | ADA PARKING INSTALLATION | 2741 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #3 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
2740ADA1 | ADA PARKING INSTALLATION | 2740 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #2 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 2500
0580INT1 | INTERIOR FINISHES | 0580 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PUMP HOUSE | 9936 | CNR | Parks |  | South Fork SRA | 1992 | 104 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 520
2739EXT1 | EXTERIOR/ INTERIOR FINISHES | 2739 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #1 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 98 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 245
0547SFT1 | FIRE ALARM UPGRADE | 0547 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10392
2740EXT1 | EXTERIOR/ INTERIOR FINISHES | 2740 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | CXT RESTROOM #2 WEST | 9936 | CNR | Parks |  | South Fork SRA | 2006 | 196 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 490
0546EXT2 | EXTERIOR FINISHES | 0546 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 17280
0547ENR2 | HEATER REPLACEMENT | 0547 | The ceiling mounted heaters in the garage are not energy efficient and have reached the end of their expected and useful life. They have undergone numerous repairs and should be scheduled for replacement. The new units shall be designed to significantly reduce electrical and propane gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project would provide for replacing the existing heaters and all required connections to utilities. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
0547INT4 | JANITORS CLOSET REPAIRS | 0547 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0547ADA3 | ADA SHOWER REMODEL | 0547 | The staff restroom is ADA compliant except for the shower. The existing shower does not fully comply with the ADA accessible guidelines. This project would provide for new ADA compliant plumbing fixtures and shower seat to be installed. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 5000
0547EXT2 | EXTERIOR DOOR REPLACEMENT | 0547 | The exterior wood man door at the entrance appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0546ADA2 | ADA SHOWER AND RESTROOM REMODEL | 0546 | The designated ADA restrooms and showers do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms and one accessible shower room. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 15000
9936ADA3 | ADA UPGRADES - PRESENTATION AREA | 9936 | The Presentation Area in the campground is used by the rangers for educational and interpretive talks to the public. There are benches provided but there is no accessible path of travel or accessible viewing area for the disabled. This project would provide for the purchase and installation of 300 SF of 4" thick concrete for an ADA compliant sidewalk and viewing area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | SOUTH FORK STATE RECREATION AREA SITE | 9936 | CNR | Parks |  | South Fork SRA |  |  | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 3500
0547INT3 | INTERIOR FINISHES | 0547 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 4 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Four to Ten Years | Long-Term Needs | 3 | 17320
0547ADA2 | ADA ACCESSIBLE COUNTER | 0547 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/07/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/22/2014. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Immediate to Two Years | Currently Critical | 1 | 1000
0546HVA1 | HVAC REPLACEMENT | 0546 | The existing HVAC system consists of a propane-fired furnace and an air handler. The equipment is original to the building and does not provide sufficient heat in the colder months of the year. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | CAMPGROUND COMFORT STATION | 9936 | CNR | Parks |  | South Fork SRA | 1991 | 864 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0547STR1 | STRUCTURAL POST REPLACEMENT | 0547 | The wood posts supporting the roof overhang around the building are in various stages of deterioration and should be scheduled for replacement. The posts are drying out, twisting, splitting, pulling loose from the steel brackets and rotting at the bottom due to direct contact with dirt and moisture. To prevent the wood to ground contact from occurring in the future, the concrete footings will need to be widened and raised up. This project would provide for replacing 25 wood posts and concrete footings including all necessary hardware and painting or staining. | PARK OFFICE/SHOP | 9936 | CNR | Parks |  | South Fork SRA | 1994 | 3464 | 2014-07-22 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0674EXT1 | EXTERIOR FINISHES | 0674 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104040
0677EXT1 | EXTERIOR FINISHES | 0677 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504
9937ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 9937 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ELKO ARMORY SITE | 9937 | Military | NNG |  | Elko |  |  | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 30000
0674EXT2 | ROOF REPLACEMENT | 0674 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 1-2 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 124848
0674PLM1 | WATER HEATER REPLACEMENT | 0674 | The average life span of a water heater is eight to ten years. The existing 250 gallon gas water heater in the building has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 250 gallon gas water heater. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0674SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0674 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel brace. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 4000
0674INT1 | INTERIOR FINISHES | 0674 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104040
1490EXT1 | EXTERIOR FINISHES | 1490 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | STORAGE BUILDING | 9937 | Military | NNG |  | Elko | 1992 | 2160 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4320
0674HVA1 | MECHANICAL ROOM HEATER INSTALLATION | 0674 | The mechanical room does not have any heating or automatic louvers. The extreme weather has caused the pipes to freeze and burst in the past and resulted in portions of the plumbing system to be shut down. This project would provide for the room to be fitted with a natural gas fired unit heater as well as automatic wall mounted louvers to regulate the temperature in the room. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 5000
0674ADA1 | ADA SIDEWALK REPLACEMENT | 0674 | The concrete sidewalks around the building are in need of replacement. The sidewalks have cracks and are spalling. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 22500
0674INT3 | VCT REPLACEMENT | 0674 | The VCT flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58500
0674CUL1 | DISHWASHER REPLACEMENT | 0674 | The commercial dishwasher in the kitchen appears to be original to the building and is troublesome and problematic to operate. Considering the age of the dishwasher and the evolving needs of the facility it is recommended to be replaced. This project provides for removal and disposal of the existing dishwasher and replacement with new unit. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1490SFT2 | EXTERIOR LANDING INSTALLATION | 1490 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | STORAGE BUILDING | 9937 | Military | NNG |  | Elko | 1992 | 2160 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 5000
0674EXT3 | WINDOW REPLACEMENT | 0674 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Four to Ten Years | Long-Term Needs | 3 | 30000
0677SFT3 | SAFETY CABINETS | 0677 | The building contains many different paints, stains, gasoline, herbicides, pesticides and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 5000
0677SFT2 | HAZARDOUS MATERIALS STORAGE | 0677 | The Hazardous Waste Storage #1 building contains hazardous materials (i.e. gasoline, herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 30000
0677SFT1 | BATTERY STORAGE | 0677 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2012 IFC. | HAZARDOUS WASTE STORAGE #1 | 9937 | Military | NNG |  | Elko | 1990 | 252 | 2016-08-23 | Immediate to Two Years | Currently Critical | 1 | 25000
0674HVA2 | HVAC EQUIPMENT REPLACEMENT | 0674 | The five HVAC roof top units were installed in 2006. They are not energy efficient and will soon reach the end of their expected and useful life. This project would provide for installation of five new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | ARMORY | 9937 | Military | NNG |  | Elko | 1961 | 10404 | 2016-08-23 | Four to Ten Years | Long-Term Needs | 3 | 75000
9937SEC1 | EXTERIOR LIGHTING | 9937 | The Elko NNG site has minimal site lighting, which affects the ability to mobilize during hours of darkness and has security implications. This project would provide funding for the purchase and installation of ten LED light fixtures, 30 foot tall light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002 and 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ELKO ARMORY SITE | 9937 | Military | NNG |  | Elko |  |  | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
9937SIT2 | SLURRY SEAL ASPHALT PAVING | 9937 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 72,716 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | ELKO ARMORY SITE | 9937 | Military | NNG |  | Elko |  |  | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 90895
1490ELE2 | LIGHTING UPGRADE | 1490 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/19/2002 and 11/08/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/23/2016. | STORAGE BUILDING | 9937 | Military | NNG |  | Elko | 1992 | 2160 | 2016-08-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17280
0224ADA1 | ADA ENTRANCE DOORS | 0224 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0231SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0231 | The building is partially a B occupancy per the 2012 IBC and is over 12,000 square feet in area. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 288260
0224HVA1 | EXHAUST FAN REPLACEMENT | 0224 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0224SIT2 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0224 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0225ADA1 | ADA ENTRANCE DOORS | 0225 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0224INT1 | INTERIOR FINISHES | 0224 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19235
0225EXT3 | EXTERIOR DOOR REPLACEMENT | 0225 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0223SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0223 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0224EXT3 | EXTERIOR DOOR REPLACEMENT | 0224 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0233EXT4 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0233 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0224SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0224 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0228HVA4 | HVAC SYSTEM UPGRADE | 0228 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
9938SIT4 | SLURRY SEAL ASPHALT PAVING | 9938 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt area was used to generate this estimate. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0231EXT2 | EXTERIOR FINISHES | 0231 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 102950
0230INT3 | CLOTHES WASHER REPLACEMENT | 0230 | One of the commercial steam powered clothes washers/ extractors is original to the building, the other has been replaced recently. The older one is reaching the end of its useful life and should be scheduled for replacement. This project provides for removal and disposal of the existing washer/ extractor and replacing it with a new unit. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0230PLM3 | WATER VALVE REPLACEMENT | 0230 | The Belimo hot and cold water control valves for the mechanical system have had leaks since installation and should be replaced in the next two to three years. This project would provide for replacing the valves throughout the HVAC plumbing lines. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0223ADA8 | ADA SIGNAGE | 0223 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1200
0615INT2 | INTERIOR FINISHES | 0615 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36200
0615PLM1 | HOSE BIBB REPLACEMENT | 0615 | The hose bibbs on the exterior of the building have not stood up to the winter climate. They are broken and are no longer in use. This report recommends replacing 4 exterior hose bibbs with freeze-proof wall hydrants. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0223ENR4 | HVAC SYSTEM UPGRADE | 0223 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by a chiller located inside the building. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new air conditioning, furnaces and ducting throughout the building. Additional cooling will be included for the server room which currently gets overheated. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
9938ENR1 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 9938 | This project recommends the installation of an Energy Management System (EMS) for the site. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, natural gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
0223ADA5 | ADA PARKING AND SIGNAGE | 0223 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking spaces do not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking spaces up to code including removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 17500
0231INT5 | CEILING REPAIR | 0231 | The ceilings in the building consist of a 12x12 acoustical tile installed over wood T & G decking. The acoustical tiles are falling off throughout the building due to poor application and it is recommended that they be removed and replaced with gypsum board. This project would provide for removal and disposal of the acoustical tiles and installation of textured and painted gypsum board. Another option would be to remove tiles and paint exposed wood decking. The cost for this option would be $2.50 / SF or $51,475. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 164720
0233INT5 | INTERIOR DOOR REPLACEMENT | 0233 | The interior doors in this building are hollow core metal units and most are damaged from general wear and tear. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 14 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 28000
0231SFT1 | FIRE DAMPER INSPECTION/ REPAIR | 0231 | The fire dampers throughout the building's HVAC plenums are not functioning properly according to staff. These dampers are an integral part of the fire and smoke protection system of the building. This project would provide funds to inspect, test and if necessary, repair the fire dampers. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 11000
0230SIT1 | SITE DRAINAGE IMPROVEMENTS | 0230 | The building has a drainage problem on the north side where grade does not properly slope away from the building. This is causing water to pool up next to the building which may infiltrate the interior during inclement weather and cause damage to the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 3500
0230INT2 | INTERIOR FINISHES | 0230 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 79280
0230EXT3 | EXTERIOR FINISHES | 0230 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 79280
0229HVA2 | EXHAUST FAN REPLACEMENT | 0229 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0229SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0229 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0223ADA7 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0223 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0223ADA6 | ADA ENTRANCE DOOR | 0223 | The existing exterior entrance doors and thresholds to the Administration building is not accessible. This project would provide for new accessible door and threshold assemblies including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 2000
9938ENV1 | PEST ABATEMENT | 9938 | The site and buildings have been inhabited by swallows. The birds introduce a potential risk of disease, cause maintenance problems with the mechanical systems, and cost labor time for general clean-up. This project provides for removal and disposal of swallow debris, nests, eggs and carcasses from the site and buildings by a licensed pest control business. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 7500
9938ELE1 | SITEWIDE ELECTRICAL UPGRADE | 9938 | The site's electrical distribution system is original and now over 50 years old. The main switchgear, wiring and conduits have reached the end of there useful life and are in need of replacement. In each building, the electrical boxes, panels, outlets and switches are original and due for replacement as well. Maintenance staff also reported that the voltage varies between 400 and 500 volts at any given time. This causes premature wear to the equipment across the site and can damage safety equipment. This project would provide for a complete electrical upgrade including replacement of the main switchgear, transformers, conduit and wiring to all existing buildings on site including trenching and backfill and replacement of electrical equipment in each building. Removal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500000
9938SIT8 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9938 | There many existing light poles around the site which have caused continuous maintenance problems and some are not working. Problems include failing contactors, unavailable replacement parts, failing conduits and rusted metal poles. Due to insufficient lighting and cracked and heaving concrete sidewalks, there have been tripping hazards and complaints from individuals on the campus. This project would provide for the installation of 35 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and installing new electrical connections. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 227500
9938SIT6 | IRRIGATION UPGRADE | 9938 | The existing landscape irrigation lines throughout the site are reaching the end of their expected life and should be scheduled for replacement. The schedule 20 piping is not durable enough for the application and should be replaced with a stronger pipe. This project would provide for the removal of the existing irrigation lines and the purchase and installation of new lines. 12,000 linear feet was used to generate this estimate. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
0225HVA4 | HVAC SYSTEM UPGRADE | 0225 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
0231ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0231 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0231EXT3 | WINDOW REPLACEMENT | 0231 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 125 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 187500
0231EXT4 | EXTERIOR DOOR REPLACEMENT | 0231 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of 15 new hollow metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0232PLM2 | HOSE BIBB REPLACEMENT | 0232 | The hose bibbs on the exterior of the building have not stood up to the winter climate. They are broken and are no longer in use. This report recommends replacing six exterior hose bibbs with freeze-proof wall hydrants. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0232SFT6 | SAFETY CABINETS | 0232 | The building contains many different paints, stains, pesticides, liquid gases and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1000
0232SFT7 | VEHICLE EXHAUST EXTRACTION SYSTEM | 0232 | The vehicle maintenance garage has an exhaust extraction system that is no longer functioning. Table 403.7 in the 2012 Uniform Mechanical Code states that "Auto repair rooms where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes". This project would provide for the purchase and installation of a vehicle exhaust extraction system including, hoses, automatic shut off, electrical connections and roof mounted exhaust fans and equipment as provided by the manufacturer. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0233EXT2 | EXTERIOR FINISHES | 0233 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76580
0233INT2 | INTERIOR FINISHES | 0233 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 76580
0233SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0233 | The building is partially a B occupancy per the 2012 IBC and is over 12,000 square feet in area. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 214424
0233ADA2 | EXTERIOR DOOR REPLACEMENT | 0233 | The entrances to the building are a mix of single leaf and double leaf commercial grade metal door assemblies and a storefront entrance system at the main entrance. None of these are ADA compliant. The doors and frames are old damaged and are in need of replacement. This project would provide for the installation of new metal door assemblies with lever-operated hardware and a new storefront entrance system complete with all required ADA accessible hardware. Painting of the new doors and removal and disposal of the old doors is included in this estimate. 10 doors were used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 60000
0233INT3 | GYMNASIUM FLOOR REPLACEMENT | 0233 | The existing rubber flooring in the gymnasium is reaching the end of its useful life. This project would provide for the removal of the existing flooring and installation of a new wood floor. A 25/32" thick maple on a sleeper system was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 124020
0231INT4 | INTERIOR FINISHES | 0231 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be cleaned and sealed or painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 102950
0231ADA1 | ADA RESTROOM UPGRADE | 0231 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 100000
0229HVA3 | HVAC REPLACEMENT | 0229 | There are 6 FAU's located in the mechanical room which provide heat for this unit as well as the Adventurer Cottage. They are currently in good operational condition but due to age and expected life span, these units should be scheduled for replacement within the 6 to 8 years. Also included is one wall-mounted evaporative cooler, the other 3 have been recently replaced. This project address both the Frontier and Adventurer. A figure of $8,000 was used for the heaters and $3,000 for evaporative cooler. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51000
0231ADA4 | ADA SIGNAGE | 0231 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 7500
0232EXT2 | EXTERIOR FINISHES | 0232 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56320
0232INT2 | INTERIOR FINISHES | 0232 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56320
0232EXT3 | WINDOW REPLACEMENT | 0232 | The windows are original, single pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0232EXT4 | EXTERIOR DOOR REPLACEMENT | 0232 | The entrances to the shop areas in the building are single leaf, commercial grade metal door assemblies. The 6 doors and frames are old and damaged and are in need of replacement. This project would provide for the installation of new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0232ADA1 | ADA RESTROOM UPGRADE | 0232 | The four restrooms in the building are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration and none of them meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit of each restroom is necessary. This project would provide funding for construction of four unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 60000
0535INT2 | INTERIOR FINISHES | 0535 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0535HVA2 | EXHAUST FAN REPLACEMENT | 0535 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0535SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0535 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0615INT1 | NONABSORBANT FINISHES | 0615 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet, bathing and shower rooms that extend upward onto the walls at least 4 inches, within 2 feet of the sides of urinals and water closets to a height of not less than 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. This project recommends the installation of Fiberglass Reinforced Panel (FRP) or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0615EXT1 | EXTERIOR FINISHES | 0615 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36200
0233INT4 | BLEACHER REPLACEMENT | 0233 | The existing wood bleachers in the gymnasium are reaching the end of their useful life. This project would provide for the removal and disposal of the existing bleachers and installation of new bleachers. Wood, manually telescoping bleachers to seat 500 people were used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112500
0615HVA2 | HVAC EQUIPMENT REPLACEMENT | 0615 | The existing HVAC system consists of 2 ceiling mounted packaged units located above the walk-in cooler and freezer. These provide heat to the warehouse and cooling to the freezers and refrigerators, but do not provide cooling to the warehouse. There is a need for cooling equipment to provide a comfortable work environment in the summer. This project would provide for removal and replacement of the 2 HVAC packaged units to provide heating and air conditioning to the warehouse. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0234INT1 | INTERIOR FINISHES | 0234 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7280
0225SIT2 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0225 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0234EXT2 | EXTERIOR FINISHES | 0234 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7280
0225HVA2 | EXHAUST FAN REPLACEMENT | 0225 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0233INT8 | LOCKER REPLACEMENT | 0233 | The 30 existing lockers in the gymnasium are reaching the end of their useful life and should be scheduled for replacement when sports are reintroduced to the school. This project would provide for the removal and disposal of the existing lockers and installation of new lockers. An 18"x15"x72" steel, baked enamel locker was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 15000
0226ADA1 | ADA ENTRANCE DOORS | 0226 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0226EXT5 | EXTERIOR DOOR REPLACEMENT | 0226 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0231HVA3 | HEATING SYSTEM REPLACEMENT | 0231 | The existing steam boiler, burner, air handler, pumps and fan coils throughout the building are original equipment and they have reached the end of their expected life. The air handler pneumatics do not work and replacement parts are no longer available. This project would provide for the removal of this equipment and the purchase and installation of a new steam or hot water boiler heating system. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 200000
0232HVA1 | HVAC EQUIPMENT UPGRADE | 0232 | The existing HVAC system consists of a closed loop hot water system served by a boiler and several evaporative coolers. The boiler and water treatment systems are in good condition. Several ceiling mounted heating units are not operational due to missing parts and they have reached the end of their expected life. There are also several evaporative coolers that are not working or are in need of replacement. This project would provide for replacing all of the heating units and evaporative coolers. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 67584
0234SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 0234 | The concrete exterior stairs at the entry are lacking a handrail as required in section R311.7.8 of the 2012 International Residential Code. This project would provide for a tubular steel framed handrail to be installed in accordance with the code. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0233HVA3 | HVAC SYSTEM REPLACEMENT | 0233 | The existing HVAC system consists of a closed loop hot water system with heat exchangers located throughout the ceiling areas. The boiler is original to the building, the water tubes are leaking, the sheet metal panels are rusted and the air handler's pneumatics are non-operational. The Gymnasium also lacks cooling. This project would provide for a new boiler system with heat exchangers to provide heating and cooling of the building including connections to a site wide energy management system (EMS). This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 229740
0224HVA3 | HVAC SYSTEM UPGRADE | 0224 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by evaporative coolers which have been replaced recently. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 38470
0615SFT4 | EXTERIOR STAIR HANDRAIL REPLACEMENT | 0615 | The exterior stair handrails on the concrete stairs are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they do not have compliant extensions at the top and bottom of the stair. This project recommends the replacement of the handrails on both sides of the stairs. Removal and disposal of the existing railing is included. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/21/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0227HVA4 | HVAC SYSTEM REPLACEMENT | 0227 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
2268INT1 | INTERIOR FINISHES | 2268 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GENERATOR BUILDING | 9938 | HHS | DCFS | NYTC | Elko | 1995 | 520 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2600
2269EXT1 | EXTERIOR FINISHES | 2269 | It is important to maintain the finish, weather resistance and appearance of the building. The structure is rusting due to moisture infiltration and will fail if not sealed properly. This project would provide funding to protect the structure and exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 1-2 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WELL HOUSE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1997 | 128 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 640
2280EXT1 | EXTERIOR FINISHES | 2280 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S GARAGE | 9938 | HHS | DCFS | NYTC | Elko |  | 750 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
9938SIT2 | CONCRETE SIDEWALK REPLACEMENTS | 9938 | The site has several areas of damaged concrete sidewalks that have not been replaced recently. These areas pose tripping hazards from heaving and settling and the cracks will continue to grow from freeze/ thaw impacts. This project would provide for the removal and replacement of the damaged concrete sidewalks. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9938SIT3 | BACKFLOW PREVENTION | 9938 | The domestic water for the campus is fed from two water tanks which are supplied by a well. The domestic water system does not have a backflow prevention device. State law mandates that backflow prevention devices be installed on all domestic, fire protection and irrigation systems to prevent contamination. This project would provide for three backflow prevention devices to be installed in heated above ground vaults. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 75000
0233INT7 | BASKETBALL BACKSTOP REPLACEMENT | 0233 | The existing backstops in the gymnasium are reaching the end of their useful life and should be scheduled for replacement. The cables and mechanisms are worn out and do not function properly. This project would provide for the removal and disposal of the existing backstops and installation of new ones. An electrically operated, ceiling suspended, fold up basketball backstop was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16500
0233ADA4 | ADA LOCKER ROOM RESTROOM UPGRADE | 0233 | The restroom and shower fixtures in the locker rooms are worn and damaged from many years of use including the water closets, urinals, lavatories, faucets, shower heads and handles. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new ADA compliant units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
0233HVA2 | EXHAUST FAN REPLACEMENT | 0233 | The exhaust fans in the showers, restrooms and locker room areas are inadequate for their application contributing to moisture accumulation and possible mold growth. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. Removal and disposal of the existing equipment is included in this estimate. This project excludes the restrooms adjacent to the Lobby as they were addressed in CIP project 05-C35. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0232EXT5 | OVERHEAD DOOR REPLACEMENT | 0232 | There are eight 12'x12' overhead doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0234SFT2 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0234 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0228INT2 | INTERIOR FINISHES | 0228 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19235
0228HVA2 | EXHAUST FAN REPLACEMENT | 0228 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0228EXT4 | EXTERIOR DOOR REPLACEMENT | 0228 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0226SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0226 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0229ADA4 | ADA RESTROOM UPGRADE | 0229 | This cottage is designated as the "ADA" cottage according to staff. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, shower controls, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0227HVA2 | EXHAUST FAN REPLACEMENT | 0227 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0228SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0228 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0234SIT1 | SITE DRAINAGE | 0234 | The house has considerable damage to the siding and foundation from improper drainage. The grade does not slope away from the rear of the building. This is causing water to pool up against the rear wall and damage siding and the concrete foundation walls. This project would create positive flow away from the building by regrading and installing French drains as needed. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 3000
0228ADA1 | ADA ENTRANCE DOORS | 0228 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0227EXT4 | EXTERIOR DOOR REPLACEMENT | 0227 | The exterior metal door at the rear entrance is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0227SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 0227 | The building has considerable damage to the painted CMU from lawn sprinklers wetting the exterior walls. This project would create drip irrigated planters within three feet of the building and relocate sprinklers so they do not wet the building. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0227ADA1 | ADA ENTRANCE DOORS | 0227 | The exterior metal entrance doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames and lever-operated hardware. Removal and disposal of the existing doors is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 6000
0226HVA3 | HVAC SYSTEM UPGRADE | 0226 | The existing HVAC system consists of a site-wide closed loop hot water boiler system with hydronic coils. Cooling is provided by roof-mounted evaporative coolers. This system is in fair condition but the pneumatic controls are not working, there are several leaks in the chilled water piping and valves and staff noted that there appears to be leaks in the make-up water lines somewhere which has not been located. This project provides for installing a new HVAC system independent from the site hot water loop including removing the hydronic coils and pneumatic controls and installing new furnaces, air conditioners and ducting throughout the building. The new system shall be designed to significantly reduce electrical and natural gas usage in order to comply with the 2009 IECC and ASHRAE 90.1 and to reduce utility costs. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 57705
0229EXT2 | EXTERIOR FINISHES | 0229 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0226HVA2 | EXHAUST FAN REPLACEMENT | 0226 | The exhaust fans in the showers and restroom areas are inadequate for their application contributing to moisture accumulation and possible mold infiltration. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including ducting and connections to utilities. This report recommends the installation of high efficiency exhaust fans with humidity detection and delayed shut-off to exhaust all moisture and prevent future accumulation issues. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0229INT2 | INTERIOR FINISHES | 0229 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0535EXT2 | EXTERIOR FINISHES | 0535 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19950
0226PLM1 | RESTROOM FIXTURES REPLACEMENT | 0226 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0223SFT3 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0223 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1924
0615SFT5 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0615 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 3620
0225ENR2 | EXTERIOR ENERGY RETROFIT | 0225 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0233ADA1 | ADA SIGNAGE | 0233 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0227ENR2 | EXTERIOR ENERGY RETROFIT | 0227 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0233ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0233 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0228PLM1 | RESTROOM FIXTURES REPLACEMENT | 0228 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0224INT2 | KITCHEN REPLACEMENT | 0224 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0227ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0227 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0227ENR3 | LIGHTING UPGRADE | 0227 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0223ENR3 | LIGHTING UPGRADE | 0223 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0223ENR2 | EXTERIOR ENERGY RETROFIT | 0223 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 72 windows. This project or a portion thereof was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 108470
9938SFT5 | SITE FIRE ALARM UPGRADE | 9938 | This site is equipped with a fire detection and alarm system, but the system is old and inoperative in some buildings. Recurring problems have been noted with the system and related site communications systems since installation. It is recommended that the fire detection and alarm system be completely upgraded, including multiple point off-site notification pull stations or a similar system acceptable to the State Fire Marshal. The site could benefit from a wireless system, which may provide reduced costs and system redundancy in the event of lightning, floods or other problems which could otherwise disable the system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 250000
0229ENR2 | EXTERIOR ENERGY RETROFIT | 0229 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS, $1000.00 per window for 11 windows and $15,000 for the aluminum storefront entrance system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65900
0232ENV1 | DUST COLLECTION SYSTEM REPLACEMENT | 0232 | The building has a woodshop which has an inoperative dust collection system. The existing exhaust fan is undersized for the equipment being used. This project recommends the replacement of the dust collection system with a higher capacity system, including the fan, motor and ducting to each piece of equipment. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0225PLM1 | RESTROOM FIXTURES REPLACEMENT | 0225 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0228ENR3 | LIGHTING UPGRADE | 0228 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0228ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0228 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0231ENV1 | REFRIGERATED MEDICAL CABINET REPLACEMENT | 0231 | The infirmary has a medical grade refrigeration cabinet that is used to store temperature sensitive medications and materials. The cabinet is older and has been problematic, forcing staff to rely on a portable unit and a non-medical grade refrigerator, which are less secure and do not provide adequate storage. This project will provide for a new medical grade refrigerated storage cabinet and associated equipment. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0615ENR3 | ROLLUP DOOR REPLACEMENT | 0615 | The existing 10'x12' rollup door does not function properly due to age and abuse and repair parts are difficult to find. It is also uninsulated and not energy efficient. This project would provide for the removal and disposal of the existing door and the purchase and installation of a new manually operated insulated rollup door. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0233ENR2 | LIGHTING UPGRADE | 0233 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade T-12 lamps to T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination and HVAC load. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22974
0535ENR2 | LIGHTING UPGRADE | 0535 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5985
0535ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0535 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0229ENR3 | LIGHTING UPGRADE | 0229 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5985
0229ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0229 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0231EXT1 | ROOF REPLACEMENT | 0231 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 247080
0231INT1 | FLOORING REPLACEMENT | 0231 | The VCT (vinyl composite tile), carpet and ceramic tile flooring in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base, heavy duty commercial grade carpet and new ceramic tile in the next 2-3 years. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 164720
0231ENR2 | LIGHTING UPGRADE | 0231 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30885
0228ENR2 | EXTERIOR ENERGY RETROFIT | 0228 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0225INT1 | KITCHEN REPLACEMENT | 0225 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0225ENR3 | LIGHTING UPGRADE | 0225 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0225ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0225 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0227INT1 | KITCHEN REPLACEMENT | 0227 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0615ENR2 | LIGHTING UPGRADE | 0615 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10860
0234EXT1 | ROOF REPLACEMENT | 0234 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 17472
0310SEC1 | CONSERVE AND PROTECT VACANT BUILDING | 0310 | This residence is vacant and currently used for incidental storage. The structure is deteriorating including broken windows, doors falling off and roof failing. The broken windows in the building have allowed pigeons, bats and other pests access to the building, with related health hazards and allowed rain to enter the building. In order to preserve the building for future rehabilitation and reuse, this project recommends mothballing it in accordance with the Department of Interior Recommended Guidelines in Preservation Brief 31. Windows and doors will be secured and covered, some with louvers to permit ventilation of the structure. A basic security system including a smoke/fire alarm will also be installed. A sump and drain system will keep water from the under floor areas and basement. This project or a portion thereof was previously recommended in the FCA report dated 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ASSISTANT SUPERINTENDENT HOUSE | 9938 | HHS | DCFS | NYTC | Elko |  | 890 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 17800
0224ENR2 | EXTERIOR ENERGY RETROFIT | 0224 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0224PLM1 | RESTROOM FIXTURES REPLACEMENT | 0224 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0226INT1 | KITCHEN REPLACEMENT | 0226 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0226ENR3 | LIGHTING UPGRADE | 0226 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0226ENR1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0226 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0232SFT8 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0232 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 15000
0233SFT3 | OCCUPANT LOAD SIGNAGE | 0233 | The 2012 IBC Chapter 1004.3 states that an assembly occupancies shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. The gymnasium meets this criteria. This project provides for creating and installing compliant signage for the gymnasium. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0226ENR2 | EXTERIOR ENERGY RETROFIT | 0226 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1000.00 per window for 20 windows. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 58470
0232ENR2 | LIGHTING UPGRADE | 0232 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16896
0535PLM1 | RESTROOM FIXTURES REPLACEMENT | 0535 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0232SFT2 | FIRE SUPPRESSION SYSTEM REPLACEMENT | 0232 | This building has an outdated fire suppression system. The sprinkler heads appear to be a model that have been recalled, and the system will need to be replaced. Costs are estimated for complete system replacement, as the new design may require replacement of uprights, pipe and controls. This project recommends replacing the existing system and implementing a comprehensive testing and service schedule to prevent problems from occurring in the future. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 157696
0615PLM2 | WATER HEATER REPLACEMENT | 0615 | There is a 10 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0615SIT1 | ROOF DRAIN DOWNSPOUT MODIFICATIONS | 0615 | The roof drain downspouts currently terminate within inches of the building with no continuous drainage away from the foundation. This is causing the water to pool next to the foundation and damage the foundation and walls. This project would provide for the extension of the roof drains from the downspouts to approximately 5'-0" away from the perimeter of the building to prevent pooling and damage to the building. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0232SFT3 | PAINT BOOTH REPLACEMENT | 0232 | The building has a paint room which is used by the wood shop, automotive repair shop and various other uses. The equipment is antiquated and obsolete and is not presently used. This project provides funding to remodel the paint booth/ room in order to bring it up to current standards, including necessary electrical, egress and OSHA upgrades. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0615EXT3 | ROOF REPLACEMENT | 0615 | The standing seam metal roof on this building was in poor condition at the time of the survey and had at least one active leak. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | WAREHOUSE | 9938 | HHS | DCFS | NYTC | Elko | 1988 | 7240 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86880
0228INT1 | KITCHEN REPLACEMENT | 0228 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2268EXT3 | ROOF REPLACEMENT | 2268 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | GENERATOR BUILDING | 9938 | HHS | DCFS | NYTC | Elko | 1995 | 520 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6240
0231INT3 | ADA BREAK ROOM REMODEL | 0231 | The kitchenette and associated cabinets in the employee break room are original to the building. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards For Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2268EXT2 | EXTERIOR FINISHES | 2268 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the vents, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GENERATOR BUILDING | 9938 | HHS | DCFS | NYTC | Elko | 1995 | 520 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 2600
2280SIT1 | SITE DRAINAGE | 2280 | The garage has considerable damage to the siding and foundation from improper drainage. The grade does not slope away from the rear of the building. This is causing water to pool up against the rear wall and damage siding and the concrete foundation. This project would create positive flow away from the building by regrading and installing French drains as needed. | SUPERINTENDENT'S GARAGE | 9938 | HHS | DCFS | NYTC | Elko |  | 750 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0231SFT2 | COMMUNICATIONS SYSTEM UPGRADE | 0231 | This building is equipped with a communications system that is at least 20 years old. The system provides paging and phone communications to classrooms and is an integral component of the notification and safety procedures for the classrooms. The system is problematic and replacement parts are no longer available. It is recommended that the communication systems be upgraded including installation of a new bell clock system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/23/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 102950
0224ENR3 | LIGHTING UPGRADE | 0224 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, utility closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5771
0224SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0224 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 5000
0227PLM1 | RESTROOM FIXTURES REPLACEMENT | 0227 | The sink faucets and shower valves were replaced in 1995. The systems installed have not held up well under the high usage typical in a building of this type, and are beginning to fail. This project recommends replacing the faucets and shower mixing control valves with heavy duty rated commercial grade units and includes disposal of the existing fixtures. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0535ENR3 | EXTERIOR ENERGY RETROFIT | 0535 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU and replacing the windows with new dual-pane, higher efficiency units. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS, $1000.00 per window for 11 windows and $15,000 for the aluminum storefront entrance system. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65900
0535INT1 | KITCHEN REPLACEMENT | 0535 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. At the time of the survey, the stovetop, oven and refrigerator were not operating. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0229INT1 | KITCHEN REPLACEMENT | 0229 | The kitchen equipment and cabinets were replaced in the building in the mid 1990s. At the time of the survey, the stovetop, oven and refrigerator were not operating. The quality of construction and installation were inadequate for the high usage at these facilities, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion there of was previously recommended in the FCA reports dated 08/19/2002 and 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0226EXT1 | EXTERIOR FINISHES | 0226 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0226INT3 | INTERIOR FINISHES | 0226 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0227EXT5 | EXTERIOR FINISHES | 0227 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0227INT3 | INTERIOR FINISHES | 0227 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0227ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0227 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0223INT3 | INTERIOR FINISHES | 0223 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0223SIT1 | CONCRETE STAIRS REPLACEMENT | 0223 | The two sets of concrete stairs that access the building are deteriorating. Spalling and cracking have occurred. Exposure to the elements is a contributing factor and one set of stairs was closed due to tripping hazards. It appears these stairs are original to the building. An immediate replacement is recommended. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 12000
0228EXT5 | EXTERIOR FINISHES | 0228 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0231SFT6 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0231 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 10295
0233ADA5 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0233 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | GYMNASIUM | 9938 | HHS | DCFS | NYTC | Elko | 1976 | 15316 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0535ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0535 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0229EXT3 | EXTERIOR DOOR REPLACEMENT | 0229 | The exterior metal door at the rear of the building is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0229ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0229 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | FRONTIER COTTAGE #6 | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
9938ADA2 | ADA PARKING STALL STRIPING | 9938 | The ADA accessible parking area for the Gymnasium does not have striping to identify the parking stall and loading zone. The area should be re-striped to comply with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | NEVADA YOUTH TRAINING CENTER - ELKO | 9938 | HHS | DCFS | NYTC | Elko |  |  | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 1500
0232PLM3 | WATER HEATER REPLACEMENT | 0232 | There is a 65 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0232INT1 | INTERIOR DOOR REPLACEMENT | 0232 | The interior doors in this building are hollow core wood units and are damaged from general wear and tear. This project would provide for the installation of new solid core metal interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 10 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 08/22/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 09/18/2013. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0232EXT6 | SKYLIGHT REPLACEMENT | 0232 | There are ten 6’x6’ acrylic sky-lights located on the roof. Several of the units are allowing water to penetrate inside during rain or snow events. This project would provide for the removal, disposal and replacement of ten acrylic skylight units. Minor roof repairs are included in this estimate. | INDUSTRIAL/VOCATIONAL | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 11264 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0231PLM1 | WATER HEATER REPLACEMENT | 0231 | There is a 89 gallon gas-fired water heater in the building that is more than 10 years old. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CLASSROOMS & INFIRMARY | 9938 | HHS | DCFS | NYTC | Elko | 1972 | 20590 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0228ADA2 | DUAL LEVEL DRINKING FOUNTAIN | 0228 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | PIONEER COTTAGE #5 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0225INT3 | INTERIOR FINISHES | 0225 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0224ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0224 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0234ENR1 | HVAC REPLACEMENT | 0234 | The existing HVAC system consists of a natural gas fired furnace and a split system air conditioner. The equipment is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of new HVAC equipment and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21840
0234INT2 | CARPET REPLACEMENT | 0234 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
0224EXT4 | EXTERIOR FINISHES | 0224 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FORESTER COTTAGE #1 | 9938 | HHS | DCFS | NYTC | Elko | 1964 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0310EXT1 | ROOF REPLACEMENT | 0310 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. There are missing shingles and active leaks and the wood roof structure is failing. It is recommended that this building be re-roofed in the next 1-2 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | ASSISTANT SUPERINTENDENT HOUSE | 9938 | HHS | DCFS | NYTC | Elko |  | 890 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 10680
0226ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0226 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | EXPLORER R & C COTTAGE #3 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0230HVA1 | HEATER INSTALLATION | 0230 | The Laundry Room does not currently have any heating equipment and is uncomfortably cold in the winter. It is recommended to install heating equipment in the room to ensure a comfortable work environment. This project would provide for the purchase and installation of a natural gas fired heater including all required connections to existing utilities. | MULTIPURPOSE, DINING & CULINARY | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 15856 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0234PLM1 | WATER HEATER REPLACEMENT | 0234 | There is a 50 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SUPERINTENDENT'S RESIDENCE | 9938 | HHS | DCFS | NYTC | Elko | 1989 | 1456 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
0223EXT4 | EXTERIOR DOOR REPLACEMENT | 0223 | The 3 exterior wood man doors appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement of the wood doors with new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0223ADA9 | ADA RAMP REPLACEMENT | 0223 | This facility has an ADA accessible ramp located in front of the building. This ramp is on the accessible path of travel from the accessible parking space to the entrance of the building. The ramp does not have compliant landings, handrails or curbs. This project would provide for replacing the ramp with a fully ADA compliant ramp. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 45000
0225EXT5 | EXTERIOR FINISHES | 0225 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0223EXT3 | EXTERIOR FINISHES | 0223 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Four to Ten Years | Long-Term Needs | 3 | 19235
0225ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0225 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Immediate to Two Years | Currently Critical | 1 | 4000
0535EXT3 | EXTERIOR DOOR REPLACEMENT | 0535 | The exterior metal door at the rear of the building is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with new a metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | ADVENTURER COTTAGE | 9938 | HHS | DCFS | NYTC | Elko | 1966 | 3990 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0227SEC1 | MAGNETIC DOOR LOCK SYSTEM | 0227 | The existing sleeping room door locks are older and problematic. They are not designed for this application and have become a security and safety concern for the inhabitants. The existing locks require constant maintenance because they do not hold up to the abuse by the residents. This project would provide for a new electric door control system including magnetic locks, control panel and all required electrical connections. | INDIAN COTTAGE #4 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0225SEC1 | MAGNETIC DOOR LOCK SYSTEM | 0225 | The existing sleeping room door locks are older and problematic. They are not designed for this application and have become a security and safety concern for the inhabitants. The existing locks require constant maintenance because they do not hold up to the abuse by the residents. This project would provide for a new electric door control system including magnetic locks, control panel and all required electrical connections. | MOUNTAINEER COTTAGE #2 | 9938 | HHS | DCFS | NYTC | Elko | 1962 | 3847 | 2013-09-18 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
9939SIT2 | REMOVE MOBILES FROM SITE | 9939 | There are four mobile homes located on site that are being used as office space. These manufactured homes are not designed or intended for non-residential use. It would be cost prohibitive to bring the units into compliance with commercial coach requirements, to allow them to meet code and be used as offices. This project provides costs for disconnecting utilities, removal of the skirting, overhangs and steps, and removing the trailers from the site. Some of these costs could be recovered by selling the units to a mobile home dealer. | NEVADA ARMY NATIONAL GUARD CC SITE | 9939 | Admin | PubWorks | B&G | Carson City |  | 0 | 2002-06-17 | Immediate to Two Years | Currently Critical | 1 | 11542.4638
2228EXT1 | STABILIZE STRUCTURE | 2228 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | HORSE BARN | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 3440 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 17200
2229EXT1 | STABILIZE STRUCTURE | 2229 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | LOAFING SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1120 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 5600
2230EXT1 | ROOF REPAIRS | 2230 | The corrugated metal roof on this building was in poor condition at the time of the survey. The temperature fluctuations throughout the year and consistent wind which blows the panels off are contributing factors to wear and deterioration. It is recommended that the corrugated roof be repaired in the next two to three years. The roof will require new corrugated panels in many areas but the existing panels should remain where possible. If any existing panels remain, the fasteners should be checked for security and replaced if needed. This estimate includes removal and disposal of the old roofing as required. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | GRAIN STORAGE SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 510 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2550
2230EXT2 | SIDING REPAIRS | 2230 | The wood siding on this building was in poor condition at the time of the survey. It is recommended that the wood siding be repaired in the next two to three years. The siding will require new wood planks in many areas but the existing wood should remain where possible. If any existing wood remains, the fasteners should be checked for security and replaced if needed. This estimate includes removal and disposal of the old siding. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | GRAIN STORAGE SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 510 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1020
2231EXT1 | STABILIZE STRUCTURE | 2231 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | CCC OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 340 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 1700
2232EXT1 | STABILIZE STRUCTURE | 2232 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHEARING SHED | 9940 | Wildlife |  |  | Steptoe Valley | 1920 | 1650 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 8250
2233EXT1 | EXTERIOR FINISHES | 2233 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the doors, windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 2400
2233SFT1 | EXTERIOR LANDING INSTALLATION | 2233 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel equal to or greater that the size of the door. The exterior man door does not have a landing and poses a safety hazard. This project would provide for the installation of a building code compliant landing for the door. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 250
3027SFT1 | SAFETY CABINETS | 3027 | The storage building contains many different paints, stains, pesticides and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 336 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
9940SFT1 | SAFETY SIGNAGE FOR OUTBUILDINGS | 9940 | For security and safety purposes it is recommended to install "Authorized Personnel Only" signs throughout the site. Signs should be placed at all outbuildings to encourage visitors to stay out. Many of the outbuildings are structurally unsound and some are historic. It should be encouraged to protect these buildings from vandalism or theft of materials. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
9940SIT1 | ACCESS ROAD REPAIRS | 9940 | It is important to maintain the dirt and gravel access roads on the site. Several stretches of road are washed-out or are deeply rutted making it difficult to access all the areas of the site and altering established drainage flows. This project would provide for purchasing type 2 sub-base material and grading the roads where needed. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the roads and prevent premature failure. 5,000 square yards of road area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 125000
9940ENV1 | CXT COMFORT STATION INSTALLATION | 9940 | The Office area and several of the parking areas on the north side of the site do not have public restrooms. Given the distance of these locations from existing restroom facilities, health concerns exist due to visitors not using the restroom facilities at other areas. It is recommended that CXT or similar style unisex comfort stations be installed which meet current ADA requirements. This project would provide for the purchase and installation of three unisex CXT restrooms including an ADA compliant concrete parking and loading zone adjacent to the restrooms. One of the comfort stations is proposed to be installed adjacent to the office and should be coordinated with the ADA accessible parking proposed project. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 60000
9940ADA1 | ADA ACCESSIBLE PARKING | 9940 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the Office. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. 500 square feet of P.C. concrete was used to generate this estimate. This project should coincide with the WMA Office ADA entrance project. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA SITE | 9940 | Wildlife |  |  | Steptoe Valley |  |  | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 5000
2240INT2 | FLOORING REPLACEMENT | 2240 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next two to three years. Additional costs have been added for abatement of any asbestos containing materials that may be present. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6440
2238EXT2 | STABILIZE STRUCTURE | 2238 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | EQUIPMENT STORAGE/GARAGE | 9940 | Wildlife |  |  | Steptoe Valley | 1940 | 710 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3550
2241INT1 | INTERIOR FINISHES | 2241 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6350
2241INT2 | REPLACE BATHROOM FIXTURES | 2241 | The existing bathroom fixtures and finishes appear to be original and are in poor condition. This project would provide for the replacement of the bathroom fixtures including a toilet, sink, faucets and bathtub / shower combination unit. New flooring is included in this estimate. This bathroom would not need to be ADA accessible if the project for a new CXT comfort station is installed for public use adjacent to the office. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
2240ENR1 | WINDOW REPLACEMENT | 2240 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2240EXT2 | ROOF REPLACEMENT | 2240 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9200
2240INT1 | INTERIOR FINISHES | 2240 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
2240EXT1 | EXTERIOR FINISHES | 2240 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the windows, flashing, fixtures and all other penetrations as well as repairing some damaged siding. It is recommended that the building be cleaned and caulked in the next 2-3 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | RESIDENCE/BUNK HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 920 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4600
3027EXT1 | EXTERIOR FINISHES | 3027 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. Also, it is recommended that the earth to metal contact be removed to prevent premature failure of the siding. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 336 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 672
2239EXT1 | ROOF REPLACEMENT | 2239 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | BUNK HOUSE/STORAGE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 350 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2241EXT2 | ROOF REPLACEMENT | 2241 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next one to two years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 12700
2237EXT1 | DEMOLISH STRUCTURE | 2237 | The Log Dugout is over 100 years old and the structure has failed. The building is dilapidated and deteriorating and has reached the end of its useful life. This project would provide funding for the demolition of the building. Before demolition, the State Historic Preservation Office should be consulted due to the age of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | LOG DUGOUT | 9940 | Wildlife |  |  | Steptoe Valley | 1890 | 590 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5900
2236EXT2 | EXTERIOR FINISHES | 2236 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | OLD GENERATOR/WOOD STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1950 | 350 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
2236EXT1 | ROOF REPLACEMENT | 2236 | The rolled asphalt roofing on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with new rolled asphalt roofing and new underlayments. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | OLD GENERATOR/WOOD STORAGE BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1950 | 350 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2235EXT1 | STABILIZE STRUCTURE | 2235 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | LOG CABIN | 9940 | Wildlife |  |  | Steptoe Valley | 1890 | 430 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 2150
2234EXT1 | STABILIZE STRUCTURE | 2234 | The existing building is in poor condition. This project would provide for the sealing and protection of the exterior of the structure including roof and siding repairs and boarding up the large openings. It is recommended that this building be left in a state of arrested decay and not be used. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | ICE HOUSE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 200 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 1000
2233ENR1 | WINDOW REPLACEMENT | 2233 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2233SIT1 | CONCRETE APRON INSTALLATION | 2233 | The vehicle garage door does not have an exterior concrete apron. The dirt in front of the door gets muddy and rutted requiring constant maintenance. This project would provide for the installation of a new 4" thick concrete slab-on-grade apron at the vehicle garage door. 200 square feet of concrete was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | SHOP BUILDING | 9940 | Wildlife |  |  | Steptoe Valley | 1980 | 1200 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2239SFT2 | EXTERIOR LANDING INSTALLATION | 2239 | Section 1008.1 of the 2006 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The two exterior man doors do not have landings and pose a safety hazard. This project would provide for the installation of compliant landings for each door. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | BUNK HOUSE/STORAGE | 9940 | Wildlife |  |  | Steptoe Valley | 1970 | 350 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 500
2241ENR1 | LIGHTING UPGRADE | 2241 | The existing lighting fixtures are the older incandescent or fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. Compact fluorescent lamps and F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, closets and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1270
3026EXT1 | EXTERIOR/ INTERIOR FINISHES | 3026 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #4 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
3025EXT1 | EXTERIOR/ INTERIOR FINISHES | 3025 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #3 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
3024EXT1 | EXTERIOR/ INTERIOR FINISHES | 3024 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #2 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
3023EXT1 | EXTERIOR/ INTERIOR FINISHES | 3023 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | COMMINS LAKE CXT RESTROOM #1 | 9940 | Wildlife |  |  | Steptoe Valley | 0 | 84 | 2017-11-07 | Four to Ten Years | Long-Term Needs | 3 | 840
2241ADA1 | ADA ACCESSIBLE ENTRANCE UPGRADES | 2241 | The office is lacking an accessible entrance into the building and the existing stairs are not compliant with the building code. The building is open to the public during certain time periods and is also used as an office for Wildlife staff. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an accessible stairway, ramp and new door and hardware to provide access the building. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Immediate to Two Years | Currently Critical | 1 | 35000
2241ENR2 | WINDOW REPLACEMENT | 2241 | Some of the windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
2241EXT1 | EXTERIOR FINISHES | 2241 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. Also included is repairing the wood eaves and soffits as needed. It is recommended that the building be painted and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Please note that the siding appears to be a transite siding which may contain asbestos. Do not sand or otherwise disturb the siding without consulting a professional familiar with asbestos. This project or a portion thereof was previously recommended in the FCA report dated 09/30/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 08/24/2011. | STEPTOE VALLEY WMA OFFICE | 9940 | Wildlife |  |  | Steptoe Valley | 1930 | 1270 | 2017-11-07 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19050
1431HVA1 | HVAC REPLACEMENT | 1431 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1432HVA1 | HVAC REPLACEMENT | 1432 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1429PLM2 | WATER HEATER REPLACEMENT | 1429 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1430INT1 | INTERIOR FINISHES | 1430 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1430SEC1 | WINDOW REPLACEMENT | 1430 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1429EXT2 | EXTERIOR FINISHES | 1429 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1431INT1 | INTERIOR FINISHES | 1431 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1429INT1 | INTERIOR FINISHES | 1429 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1420EXT4 | ROOF REPLACEMENT | 1420 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
2242INT1 | INTERIOR FINISHES | 2242 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2242EXT2 | FASCIA REPLACEMENT | 2242 | The wood fascia around the eaves of the roof is worn and weathered. This project would provide for removal and disposal of the existing wood fascia and replacement with a new primed and painted wood fascia board. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2242EXT3 | EXTERIOR DOOR REPLACEMENT | 2242 | The entrance to the building is a single leaf, commercial grade metal door assembly. The door and frame is old and damaged and are in need of replacement. This project would provide for the installation of a new metal door assembly. Painting of the new door and removal and disposal of the old door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1617EXT1 | EXTERIOR FINISHES | 1617 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ESP SEWAGE GRINDER BUILDING | 9941 | Correct | ESP |  | Ely | 1999 | 860 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
1432EXT2 | EXTERIOR FINISHES | 1432 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1421INT1 | INTERIOR FINISHES | 1421 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1431EXT2 | EXTERIOR FINISHES | 1431 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1431SEC1 | WINDOW REPLACEMENT | 1431 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1430EXT2 | EXTERIOR FINISHES | 1430 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1425EXT3 | EXTERIOR STAIR REPAIRS | 1425 | The 2 sets of exterior concrete stairs on the south side of the building are worn and weathered which has caused significant spalling and cracking. This project recommends repairing the steps to ensure that they remain code compliant as well as to prevent further damage. Chapter 10, Section1012 of the 2012 IBC was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1425PLM1 | WATER HEATER REPLACEMENT | 1425 | There is a 30 gallon electric water heater in the Auto Shop. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1432SEC1 | WINDOW REPLACEMENT | 1432 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1428INT1 | INTERIOR FINISHES | 1428 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1423EXT5 | ROOF REPLACEMENT | 1423 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 678000
1426INT1 | INTERIOR FINISHES | 1426 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
2242EXT1 | EXTERIOR FINISHES | 2242 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, replacing missing screw attachments, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that it be scheduled on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | EQUIPMENT STORAGE | 9941 | Correct | ESP |  | Ely | 1999 | 400 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2729EXT1 | EXTERIOR FINISHES | 2729 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that it be scheduled on a cyclical basis based on environmental conditions. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | WATER TANK | 9941 | Correct | ESP |  | Ely | 1987 | 1488 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14880
1430HVA1 | HVAC REPLACEMENT | 1430 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1429HVA1 | HVAC REPLACEMENT | 1429 | The combination in-wall HVAC unit and small electric heater are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a new combination unit and electric heater. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1432PLM1 | RESTROOM FIXTURE REPLACEMENT | 1432 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1423EXT2 | EXTERIOR FINISHES | 1423 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 282500
1428EXT1 | EXTERIOR FINISHES | 1428 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1423INT2 | FLOORING REPLACEMENT | 1423 | The sheet vinyl flooring in the Infirmary and vinyl composition tile (VCT) in the Library, Chapel and the Visitor's Room is approaching the end of its useful life and has some damage. It is recommended that the flooring in the building be replaced. This project would provide for new 12x12 VCT and sheet vinyl to be installed. Removal and disposal of the old, damaged flooring is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 204000
1421EXT2 | EXTERIOR FINISHES | 1421 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1419PLM2 | BACKFLOW PREVENTER REPLACEMENT | 1419 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
1421PLM2 | BACKFLOW PREVENTER REPLACEMENT | 1421 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
1432INT1 | INTERIOR FINISHES | 1432 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5800
1423INT6 | INTERIOR FINISHES | 1423 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 5-6 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 282500
1425HVA1 | HEAT EXCHANGER REPLACEMENTS | 1425 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1423INT3 | COUNTERTOP REPLACEMENT | 1423 | The countertops throughout the building are showing signs of wear and tear particularly at the Formica edges and corners. The quality of construction and installation were inadequate for the high usage at these facilities, and the counter tops are delaminating and failing. This project recommends the replacement of the existing damaged countertops with heavy duty, quality finishes. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1423INT5 | JANITORS CLOSET REPAIRS | 1423 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of seven Janitors Closets. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9800
1422EXT2 | EXTERIOR FINISHES | 1422 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1422INT1 | INTERIOR FINISHES | 1422 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1431PLM1 | RESTROOM FIXTURE REPLACEMENT | 1431 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9941SIT11 | FENCE FOOTING REPAIR | 9941 | The concrete footing for the perimeter security fencing has many areas that are in need of repair. The concrete is cracking and deteriorating and could eventually compromise the structural integrity of the fencing. This project would provide for repair or replacement of damaged sections of concrete as needed. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
1425EXT5 | ROOF REPLACEMENT | 1425 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 424440
1422EXT4 | ROOF REPLACEMENT | 1422 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1423INT7 | BREAK ROOM REMODELS | 1423 | The kitchenette and associated cabinets in the employee break rooms are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
1425INT1 | INTERIOR FINISHES | 1425 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176850
1430PLM2 | WATER HEATER REPLACEMENT | 1430 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1617INT1 | INTERIOR FINISHES | 1617 | The interior finishes are in fair condition. It is recommended that the interior walls be sealed with a concrete and grout sealer at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to sealing, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ESP SEWAGE GRINDER BUILDING | 9941 | Correct | ESP |  | Ely | 1999 | 860 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
1421EXT4 | ROOF REPLACEMENT | 1421 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1429SEC1 | WINDOW REPLACEMENT | 1429 | The windows in the guard tower are original to the building. They are foggy and difficult to see through. Many of the seals are broken and dust and wind comes through. Due to the security issues of seeing clearly out of the tower, this project recommends replacing the windows. Removal and disposal of the existing windows is included in this estimate. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 24000
1425EXT2 | EXTERIOR FINISHES | 1425 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls, repairing stained and damaged CMU and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176850
1417PLM2 | BACKFLOW PREVENTER REPLACEMENT | 1417 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
1427EXT2 | EXTERIOR FINISHES | 1427 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
1427INT1 | INTERIOR FINISHES | 1427 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
1426EXT2 | EXTERIOR FINISHES | 1426 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1424EXT3 | ROOF REPLACEMENT | 1424 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 583200
1424INT5 | JANITORS CLOSET REPAIRS | 1424 | The mop sinks in the Janitors Closets are mounted adjacent to gypsum board and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. Typical of two Janitors Closets. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
1423ENR2 | LIGHTING UPGRADE | 1423 | The existing lighting fixtures are the older T-8 type which are of poor quality, and are failing prematurely. This project will upgrade fixtures to higher efficiency units with a longer life cycle. LED lamps are suggested to replace the T-8 lamps currently installed. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84750
1432PLM2 | WATER HEATER REPLACEMENT | 1432 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1424INT2 | CULINARY FLOORING REPLACEMENT | 1424 | The epoxy floor covering in the Culinary is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. The product must meet the requirements of the health department for food service and preparation. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
1424INT1 | INTERIOR FINISHES | 1424 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 243000
1424EXT2 | EXTERIOR FINISHES | 1424 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls, repairing cracked and damaged CMU and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 243000
1425HVA2 | BOILER BURNER REPLACEMENTS | 1425 | The three boilers are original to the building. The burner assemblies have become problematic and parts are hard to come by. They are reaching the end of their expected lifetime. This project provides for the removal and disposal of the existing burners and installation of new burner assemblies on all three boilers. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 75000
1431PLM2 | WATER HEATER REPLACEMENT | 1431 | There is a 7 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1426ADA1 | RESTROOM REMODEL | 1426 | The restroom is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. The ceramic tile in the showers is failing and many tiles have fallen off exposing the wood framing to water. This project would provide for a complete remodel of the restroom including complying with the 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design. The removal and disposal of the existing fixtures and finishes is included in this estimate. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 45000
1417ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1417 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1418ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1418 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1419ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1419 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1420ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1420 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1421ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1421 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1422ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1422 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
1417HVA1 | HEAT EXCHANGER REPLACEMENTS | 1417 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1419HVA1 | HEAT EXCHANGER REPLACEMENTS | 1419 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1421HVA1 | HEAT EXCHANGER REPLACEMENTS | 1421 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1426INT2 | BREAK ROOM REMODEL | 1426 | The kitchenette and associated cabinets in the break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1419EXT4 | ROOF REPLACEMENT | 1419 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1418EXT4 | ROOF REPLACEMENT | 1418 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
1417EXT4 | ROOF REPLACEMENT | 1417 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
0699PLM2 | BACKFLOW PREVENTER REPLACEMENT | 0699 | There is a backflow preventer on the main water line coming into the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 2000
1421PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1421 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
9941SIT7 | GATE OPERATOR REPLACEMENTS | 9941 | There is an automatic gate operator in the yard between the Administrative building and the Housing units and two at the Sally Port. The gate operators are malfunctioning, have been problematic, and have difficulty opening and closing the gates. This project recommends replacing the three gate operators with high quality operators that can handle heavy traffic as well as servicing the gates and related hardware to ensure prolonged operation. The gate operators will be required to meet UL Standard 325, per NRS 405.270. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1419PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1419 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service, and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1417PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 1417 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service, and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1426ADA2 | TDD INSTALLATION | 1426 | There is telephone in the building for inmates that is not equipped with a telecommunications device for the deaf (TDD). In order to comply with ADA requirements it is recommended to install a TDD system in the non-contact visitation area. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 20000
9941HVA5 | EXHAUST FAN REPLACEMENTS | 9941 | The existing exhaust fans that serve the buildings are original equipment and are not providing adequate ventilation. There are 4 large kitchen hoods and 17 smaller exhaust fans on the housing units that should be scheduled for replacement. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of new exhaust fan assemblies including connections to utilities. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1425ADA1 | ADA RESTROOM REMODELS | 1425 | The existing Staff and Inmate restrooms in the building do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling two restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 30000
1426EXT3 | ROOF REPLACEMENT | 1426 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #12 - TRUSTEE DORMITORY | 9941 | Correct | ESP |  | Ely | 1987 | 3600 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 43200
1420EXT2 | EXTERIOR FINISHES | 1420 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1420INT1 | INTERIOR FINISHES | 1420 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1419EXT2 | EXTERIOR FINISHES | 1419 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1419INT1 | INTERIOR FINISHES | 1419 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1418EXT2 | EXTERIOR FINISHES | 1418 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1418INT1 | INTERIOR FINISHES | 1418 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
9941SIT9 | SIDEWALK REPLACEMENT | 9941 | The sidewalks serving the entrances of Housing Units 5-8 are deteriorated and failing. In some areas cracks wider than four inches have been identified, and there is settling, spalling and ravelling in many locations. This project addresses removal and replacement of existing sidewalks as needed. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 50000
9941SIT6 | CRACK FILL & SEAL ASPHALT PAVING | 9941 | It is important to maintain the asphalt concrete paving and concrete drainage swales on the site. This project would provide for replacing the swales and crack filling and sealing of the paving site wide including access roads, parking areas, the perimeter road and maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 174,240 square feet of asphalt area was used to generate this estimate. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104544
0699EXT4 | ROOF REPLACEMENT | 0699 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
9941HVA4 | ROOFTOP PACKAGED UNIT REPLACEMENT | 9941 | There are 13 small HVAC roof top units on the buildings that were not addressed by the recent HVAC Replacement projects. These units were installed in 1989. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of 13 new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156000
1427EXT3 | ROOF REPLACEMENT | 1427 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 20160
9941SIT10 | ASPHALT CONCRETE REPLACEMENT | 9941 | The asphalt on the south side of the Warehouse near the fuel pumps is failing, with significant alligatoring, settling and cracks observed. The area sees high traffic volume and is used by heavy equipment which has contributed to the deterioration. This project covers the removal and replacement of the existing asphalt for the area. 4,000 square feet was used to generate this estimate. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0123ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0123 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
0123EXT3 | ROOF REPLACEMENT | 0123 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2008. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 358440
0699ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0699 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 4000
0699HVA1 | HEAT EXCHANGER REPLACEMENTS | 0699 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0699PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 0699 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service, and employee training provided by a qualified water treatment vendor. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1417EXT2 | EXTERIOR FINISHES | 1417 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
0123INT1 | INTERIOR FINISHES | 0123 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1427ADA1 | ADA RESTROOM REMODEL | 1427 | The building does not have an accessible restroom. The existing restroom does not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 15000
9941SIT8 | EXTERIOR SOLAR SITE LIGHTING UPGRADE | 9941 | There are approximately 20 existing light poles around the site not including the high mast lighting within the secured area. These older light fixtures are not energy efficient and several of the concrete bases are severely deteriorated. This project would provide for the installation of 20 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. Some of the existing poles and bases may be acceptable to re-use. If so, the estimate can be reduced accordingly. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130000
1428ENV1 | NONABSORBENT FINISHES | 1428 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extends upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. There are several areas of painted gypsum board near fixtures in the restrooms that do not meet these requirements. This project recommends adding tile to the non-compliant areas to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9941HVA3 | HVAC AIR HANDLER REPLACEMENT - PHASE 2 | 9941 | The HVAC roof top air handling units are over 20 years old. There are 24 units throughout the site, of which this phase covers the remaining 12 units. They are not energy efficient, need constant repairs and have reached the end of their expected and useful life. This project would provide for the installation of twelve new HVAC packaged units and cleaning of the existing duct work. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project is in design under CIP 15-M01 and construction is scheduled to begin on 07/11/2016. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500000
9941SEC3 | STENTOFON SWITCH REPLACEMENT | 9941 | At the time of the survey the staff reported that the Stentofon communications system was not operating properly. This project provides funding to replace the Stentofon communications switch that has failed and is causing problems with the system. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
9941SIT3 | IRRIGATION SYSTEM ADJUSTMENTS | 9941 | The existing irrigation system is spraying water on the side of the buildings inside the secured area, especially during windy conditions. There is noticeable damage to the exterior walls which can lead to extreme damage and possible mold growth if not addressed soon. This project would provide for the relocation of the sprinklers away from the buildings. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0123EXT2 | EXTERIOR FINISHES | 0123 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
0699INT1 | INTERIOR FINISHES | 0699 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
0699EXT2 | EXTERIOR FINISHES | 0699 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing and painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years, and that it be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1417INT1 | INTERIOR FINISHES | 1417 | The interior finishes are in fair condition. It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that it be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 149350
1430PLM1 | RESTROOM FIXTURE REPLACEMENT | 1430 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1427PLM1 | WATER HEATER REPLACEMENT | 1427 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9941SIT4 | CONCRETE SIDEWALK REPAIRS | 9941 | The concrete sidewalks are in generally good condition, but there are several areas that require attention. Deterioration, spalling and cracking has occurred, mainly from exposure to the weather. In some areas the sidewalks have lost their texture and cause a slipping hazard. This project would provide for the removal and replacement of the damaged concrete sidewalks. 10,000 SF of 4" thick concrete sidewalk was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
1427HVA1 | HVAC REPLACEMENT | 1427 | The existing HVAC system consists of a small unit heater and a rooftop air handler. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC units, ductwork and piping modifications, chemical treatment, temperature control modifications, testing, balancing and commissioning. | BUILDING #13 - ARMORY | 9941 | Correct | ESP |  | Ely | 1987 | 1680 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25200
1429PLM1 | RESTROOM FIXTURE REPLACEMENT | 1429 | The restroom fixtures in the Tower are worn and damaged from many years of use including the water closet, lavatory and faucet. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1428EXT2 | ROOF REPLACEMENT | 1428 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 16200
1428INT2 | JANITORS CLOSET REPAIRS | 1428 | The mop sink in the Janitors Closet is mounted adjacent to painted plywood and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1428PLM1 | WATER HEATER REPLACEMENT | 1428 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1428ADA1 | ADA ACCESSIBLE COUNTER | 1428 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The Security desk in the Gatehouse has a counter for the employees and public to approach which does not meet current requirements. Section 904.4 of the ADA Standards For Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #14 - GATEHOUSE | 9941 | Correct | ESP |  | Ely | 1987 | 1350 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 1500
1429EXT3 | ROOF REPLACEMENT | 1429 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #1 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1430EXT4 | ROOF REPLACEMENT | 1430 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #2 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1431EXT3 | ROOF REPLACEMENT | 1431 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #3 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1432EXT3 | ROOF REPLACEMENT | 1432 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2006. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | TOWER #4 | 9941 | Correct | ESP |  | Ely | 1987 | 290 | 2015-04-29 | Four to Ten Years | Long-Term Needs | 3 | 3480
1423ADA3 | ADA RESTROOM REMODEL | 1423 | The existing restrooms in the Law Library do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms into ADA compliant restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 30000
1424SFT2 | ANSUL SYSTEM REPLACEMENT | 1424 | The Ansul fire suppression system in the Culinary is approaching the end of its useful life. This project recommends replacing the existing suppression system and implementing a comprehensive testing and service schedule. Removal and disposal of the existing system is included in the estimate. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 43200
1423HVA3 | HEAT EXCHANGER REPLACEMENTS | 1423 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1423PLM1 | BACKFLOW PREVENTER REPLACEMENT | 1423 | There are two backflow preventers in the mechanical room. They are both leaking and should be scheduled for replacement. This project would provide for replacing both backflow preventers. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1423ADA2 | ADA PROJECTS | 1423 | The visitors area has eight non-contact visiting rooms. Visitors and inmates communicate via telephones. One set of the non-contact rooms should be equipped with telecommunications devices for the deaf and hearing impaired. This project includes two devices, associated power and wiring, and security devices to lock down or remove the devices when not in use. Funds are also included to remodel the counter at the guard observation area to comply with the proper height and configuration under accessibility requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 22000
1423ADA1 | ADA SIGNAGE | 1423 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 7500
1423EXT3 | WINDOW REPLACEMENT | 1423 | The existing windows in this building are older dual pane wire construction. Many have broken seals and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated window systems with higher insulation ratings. This project should be implemented concurrently with the Interior Wall Insulation project. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 69600
1423ELE1 | ELECTRICAL UPGRADE | 1423 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1130000
1423EXT4 | INTERIOR WALL INSULATION | 1423 | The building is constructed of concrete masonry units (CMU) with minimal insulation. The north facing exterior wall does not provide enough insulation in the colder months of the year. Maintenance staff has had ongoing difficulties balancing the heating to provide a comfortable work environment. This project recommends adding 2" rigid insulation, gypsum board and paint on the interior of the wall. The estimate is based on $12.00 per square foot of wall space. This project should be implemented concurrently with the Window Replacement project. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 43200
1424ENV2 | TRASH COMPACTOR REPLACEMENT | 1424 | The two existing trash compactors are original to the building and due for replacement. The compactors are rusted, have been damaged by heavy equipment and do not function properly anymore. This project would provide for replacing the existing compactors with two new 30 yard self-contained trash compactors. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
1424ADA1 | ADA RESTROOM REMODELS | 1424 | There are 5 restrooms throughout the building that do not meet the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding for construction of five accessible restrooms including two restrooms in the gymnasium, the inmate restroom in the Culinary and two restrooms in the Maintenance Shop. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 125000
0123SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 0123 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #2 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1424ELE1 | ELECTRICAL UPGRADE | 1424 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 972000
0699SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 0699 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #1 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1424INT4 | CLOTHES DRYER REPLACEMENTS | 1424 | Four of the commercial tumbler dryers in the laundry are original to the building and are troublesome and problematic to operate. Considering the age of the machines and the evolving needs of the facility it is recommended to replace them. This project provides for removal and disposal of the existing tumbler dryers with new units. A total of 4 dryers was used for this estimate. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32000
1424HVA4 | COMPRESSOR REPLACEMENTS | 1424 | There are 2 compressors on the roof serving the 5 refrigerators and 1 compressor serving the freezers. They were not included in the recent HVAC Replacement projects and should be scheduled for replacement. This project would provide for new condensers to be installed including all required connections to utilities. The estimate includes removal and disposal of the existing equipment. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1424HVA3 | BOILER REPLACEMENT | 1424 | The Kewanee steam boiler servicing the building was installed almost 30 years ago and should be scheduled for replacement. The life expectancy of this unit is 20 to 25 years with proper maintenance and water treatment programs. Replacement parts for performing routine and emergency maintenance are hard to find for this older equipment. The controls and mixing valves should be replaced for the same reasons. This project would provide for the removal and disposal of the existing boiler, controls and mixing valves and replacement with new equipment including all required connections to utilities and equipment. The estimate is based on a 150 PSI steam boiler, associated equipment and new equipment to replace the electric heaters. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125000
1424HVA2 | HEAT EXCHANGER REPLACEMENT | 1424 | The two shell and tube heat exchangers in the building were installed in 1987 and are original to the building. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of two new plate frame heat exchangers, one for the domestic water and one for the mechanical system. This project includes removal and disposal of the existing units and all required connections to utilities. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1424PLM1 | GREASE INTERCEPTOR REPLACEMENT | 1424 | The underground grease interceptor to the west of the building is not currently operating correctly. Maintenance staff reported that the metal structure is two thirds disintegrated underground. This project would provide for the purchase and installation of a new grease interceptor and connection to the existing sewer system. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1422SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1422 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #8 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1424SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1424 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #10 - WORK & RECREATION | 9941 | Correct | ESP |  | Ely | 1987 | 48600 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
9941SIT2 | SITE DRAINAGE AT MANHOLES | 9941 | The Ely State Prison site has several manholes with 4160V equipment installed below grade and the drainage doesn't prevent water accumulations. Due to their location, staff are required to manually inspect and, when needed, lower sump pumps into the hole to drain the excess water. This creates a potential electrocution hazard. This project provides funding to install catch basins, French drains and additional drain piping as needed to carry the water away from the manholes. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 100000
9941PLM1 | PLUMBING VALVE REPLACEMENTS | 9941 | The majority of the plumbing isolation valves on the site are gate valves original to the building. Many of these valves no longer completely stop water when closed. This project will provide funding to replace the faulty gate valves with ball valves. 18 valves was used for this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | ELY STATE PRISON SITE | 9941 | Correct | ESP |  | Ely | 1987 | 0 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
1423INT4 | HOSPITAL CRASH RAIL REPLACEMENT | 1423 | The medical wing has a crash guard system installed to protect the walls from damage from gurneys and medical equipment. Over the years, it has sustained moderate damage and is approaching the end of its useful life. This project provides for the replacement of the existing system with a new one, including vinyl cover and aluminum retaining clips. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #9 - SCHEDULED SERVICES | 9941 | Correct | ESP |  | Ely | 1987 | 56500 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1420SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1420 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #6 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1421SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1421 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #7 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1417SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1417 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #3 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1418SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1418 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #4 | 9941 | Correct | ESP |  | Ely | 1987 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
1425SFT1 | EXIT SIGN UPGRADE | 1425 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | BUILDING #11 - WAREHOUSE/CENTRAL PLANT | 9941 | Correct | ESP |  | Ely | 1987 | 35370 | 2015-04-29 | Immediate to Two Years | Currently Critical | 1 | 5000
1419SEC2 | ELECTRONIC LOCKS/ CONTROLS REPLACEMENT | 1419 | The controls for the door locks and security systems are built on a custom panel and interface. The controls are difficult to repair, parts are becoming increasingly difficult to locate, and the type and configuration of the switches are limited by the physical size of the consoles. This project recommends replacing the existing mechanical switching system with a computer system and electronic interface. Remote costs and secure facility allowance were included in the project estimates. This project or a portion thereof was previously recommended in the FCA report dated 06/04/2002 and 09/18/2007. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/29/2015. | HOUSING UNIT #5 | 9941 | Correct | ESP |  | Ely | 1989 | 29870 | 2015-04-29 | Two to Four Years | Necessary - Not Yet Critical | 2 | 565000
3018EXT1 | EXTERIOR/ INTERIOR FINISHES | 3018 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #4 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
2271EXT1 | EXTERIOR/ INTERIOR FINISHES | 2271 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WELL HOUSE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2001 | 80 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1792
2270EXT1 | EXTERIOR FINISHES | 2270 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27360
2270INT1 | INTERIOR FINISHES | 2270 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 27360
2270SFT1 | INTERIOR STAIRWAY REPLACEMENT | 2270 | The stairs and handrails between the first floor and the basement do not meet the sections 1009 and 1012 requirements of the 2012 IBC. This project would provide for the rebuilding of the stairway to provide for a code compliant stairway. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 10080
2270SIT1 | SIDEWALK REPLACEMENT | 2270 | The exterior walkway from the garage and driveway up to the entrance of the house does not meet code and is a safety hazard. The ramp/ walkway does not have acceptable slopes or proper landings nor does it have handrails. Due to the effects of the extreme weather conditions of the area, particularly ice and snow on the walkway, the existing sloped concrete surface poses a significant injury risk. This project would provide for an upgrade to the ramp/ walkway to make it fully compliant with 2012 IBC Chapter 10. A combination of concrete sloped walks and steps with handrails is suggested. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 11200
9942EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9942 | There are 15 steel shade ramadas in the campground which are 100 s.f. each for a total of 1,500 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WARD CHARCOAL OVENS STATE HISTORIC PARK | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  |  | 2017-07-11 | Four to Ten Years | Long-Term Needs | 3 | 6720
2270PLM1 | WATER HEATER REPLACEMENT | 2270 | There is a 50 gallon electric water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 3-4 years. It is recommended that a new propane-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
3017EXT1 | EXTERIOR/ INTERIOR FINISHES | 3017 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #3 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
3016EXT1 | EXTERIOR/ INTERIOR FINISHES | 3016 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #2 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
3015EXT1 | EXTERIOR/ INTERIOR FINISHES | 3015 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | CXT COMFORT STATION #1 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 0 | 104 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2329.6
9942ADA2 | ADA UPGRADES | 9942 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Day Use restroom are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and path of travel to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WARD CHARCOAL OVENS STATE HISTORIC PARK | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  |  | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 7840
2164EXT1 | EXTERIOR FINISHES | 2164 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RAMADA #3 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 0 | 104 | 2017-07-11 | Four to Ten Years | Long-Term Needs | 3 | 465.92
2270EXT2 | OVERHEAD DOOR REPLACEMENT | 2270 | There is a 10'x12' overhead garage door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead door and purchase and installation of a new door. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7840
3014EXT1 | EXTERIOR FINISHES | 3014 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | GROUP RAMADA - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1792
2272EXT1 | EXTERIOR FINISHES | 2272 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RAMADA #1 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  | 240 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1075.2
2270SFT2 | REMOVE AWNING | 2270 | There is a metal awning attached to the roof on the west side of the building near the front door. The main structure was not designed to carry this additional lateral load and the awning structure itself is not in good condition. It is recommended to remove and dispose of the structure. Included in the estimate is removing and disposing of the awning as well as patching the roof and concrete patio where attachments were made. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 1120
2273EXT1 | EXTERIOR FINISHES | 2273 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | RAMADA #2 - DAY USE | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  | 240 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1075.2
2277EXT2 | HISTORIC BUILDING MAINTENANCE | 2277 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #4 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2270INT2 | BASEMENT FLOOR REPAIRS | 2270 | The concrete floor in the basement is worn and damaged and should be resurfaced. This project provides for cleaning and repairing the existing concrete floor, applying a bonding agent, pouring a new polymer surface and applying an appropriate finish product. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9408
2276EXT2 | HISTORIC BUILDING MAINTENANCE | 2276 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #3 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2270SFT3 | SMOKE AND CARBON MONOXIDE ALARM INSTALLATION | 2270 | IRC 2012 Section R314 and R315.3 explain the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012 requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 2800
2275EXT2 | HISTORIC BUILDING MAINTENANCE | 2275 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #2 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2274EXT2 | HISTORIC BUILDING MAINTENANCE | 2274 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #1 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
2270EXT3 | WINDOW REPLACEMENT | 2270 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
2270HVA1 | HEATER REPLACEMENT | 2270 | There are five wall mounted heaters in the building that have reached the end of their expected life. This project recommends replacing the heaters with a packaged unit and new ductwork. The estimate includes removal and disposal of the existing equipment. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2270ENR1 | LIGHTING UPGRADE | 2270 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | RANGER RESIDENCE | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1995 | 2400 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21504
2278EXT2 | HISTORIC BUILDING MAINTENANCE | 2278 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #5 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
9942ADA1 | ADA PARKING SPACE UPGRADES | 9942 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area near the Group Ramada are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and compliant path of travel to the Group Ramada and the restroom. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/11/2017. | WARD CHARCOAL OVENS STATE HISTORIC PARK | 9942 | CNR | Parks |  | Ward Charcoal Ovens |  |  | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 15000
3017ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 3017 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | CXT COMFORT STATION #3 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 33600
3016ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 3016 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | CXT COMFORT STATION #2 - CAMPGROUND | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 2009 | 104 | 2017-07-11 | Immediate to Two Years | Currently Critical | 1 | 33600
2279EXT2 | HISTORIC BUILDING MAINTENANCE | 2279 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVEN #6 | 9942 | CNR | Parks |  | Ward Charcoal Ovens | 1876 | 600 | 2017-07-11 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
0524EXT2 | ROOF REPLACEMENT | 0524 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle or standing seam metal roofing system and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | OLD WELL/ PUMP HOUSE - CAMPGROUND | 9943 | CNR | Parks |  | Spring Valley | 1970 | 96 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1152
2265EXT2 | ROOF REPLACEMENT | 2265 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle or a standing seam metal roof system and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HORSETHIEF GULCH STORAGE BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1977 | 25 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0523ADA1 | ADA DOOR HARDWARE | 0523 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The exterior entrance door is on an accessible path of travel, but the door hardware and threshold are not compliant. This project would provide for ADA compliant door hardware and threshold on the exterior door. ADA compliant signage is also included in this project. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 1000
1219EXT1 | EXTERIOR FINISHES | 1219 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MILLET RANCH TACK SHED | 9943 | CNR | Parks |  | Spring Valley | 1941 | 135 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1350
0523SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0523 | The building is a B occupancy per the 2012 International Building Code (IBC). Pursuant to the Nevada State Fire Marshal (NSFM), Nevada Administrative Code (NAC) 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6480
2265EXT1 | EXTERIOR FINISHES | 2265 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HORSETHIEF GULCH STORAGE BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1977 | 25 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 250
2265INT1 | INTERIOR FINISHES | 2265 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HORSETHIEF GULCH STORAGE BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1977 | 25 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250
1220HVA1 | ELECTRIC HEATER REPLACEMENT | 1220 | This building is heated by an electric heater that has reached the end of its expected life. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0513ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 0513 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Comfort Station are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0513INT3 | JANITORS CLOSET REPAIRS | 0513 | The mop sinks in the plumbing chase are mounted adjacent to CMU and are showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1220EXT2 | WINDOW REPLACEMENT | 1220 | The windows are original, single pane construction in an aluminum frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 windows and the removal and disposal of the old windows. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0523SFT2 | FIRE EXTINGUISHER INSTALLATION | 0523 | The building does not have a portable fire extinguisher available. International Fire Code 2012 (IFC) Section 906 requires that portable fire extinguishers shall be installed in B occupancies. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinet, and the hardware necessary to install it. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 500
0524EXT1 | EXTERIOR FINISHES | 0524 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | OLD WELL/ PUMP HOUSE - CAMPGROUND | 9943 | CNR | Parks |  | Spring Valley | 1970 | 96 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0525SFT1 | INSTALL SMOKE DETECTORS | 0525 | International Residential Code (IRC) 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area, and in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. Nevada Administrative Code (NAC) 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
1177ADA2 | ADA RESTROOM UPGRADE | 1177 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2012 International Building Code (IBC) Chapter 11, ICC/ANSI A117.1-2009 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility, the other restroom will be assigned as Unisex as well. The removal and disposal of the old restroom fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 25000
0525INT1 | INTERIOR FINISHES | 0525 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 22800
0528EXT2 | ROOF REPLACEMENT | 0528 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND STORAGE #1 | 9943 | CNR | Parks |  | Spring Valley | 1970 | 140 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1680
0528INT1 | INTERIOR FINISHES | 0528 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND STORAGE #1 | 9943 | CNR | Parks |  | Spring Valley | 1970 | 140 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1177INT1 | INTERIOR FINISHES | 1177 | It is recommended to paint the partitions and ceilings and re-caulk the Fiberglass Reinforced Panels (FRP) at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3340
0528EXT1 | EXTERIOR FINISHES | 0528 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND STORAGE #1 | 9943 | CNR | Parks |  | Spring Valley | 1970 | 140 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0523INT1 | INTERIOR FINISHES | 0523 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2160
1220EXT3 | EXTERIOR DOOR REPLACEMENT | 1220 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1178EXT1 | EXTERIOR FINISHES | 1178 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
2925EXT1 | EXTERIOR FINISHES | 2925 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INFORMATION KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 175
2926EXT1 | EXTERIOR FINISHES | 2926 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND TRELLIS #1 | 9943 | CNR | Parks |  | Spring Valley | 2008 | 180 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 720
2927EXT1 | EXTERIOR FINISHES | 2927 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND TRELLIS #2 | 9943 | CNR | Parks |  | Spring Valley | 2008 | 180 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 720
9943EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9943 | There are 44 wood and steel shade ramadas in different locations throughout the site which are either 168 s.f., 256 s.f., 300 s.f. or 240 s.f. for a total of 9,088 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SPRING VALLEY STATE PARK SITE | 9943 | CNR | Parks |  | Spring Valley |  |  | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 36352
2921EXT1 | EXTERIOR FINISHES | 2921 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | LIFE JACKET KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 175
2920EXT1 | EXTERIOR FINISHES | 2920 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope, other than the roof including sealing and caulking around penetrations to maintain the building in good, weather tight condition. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS CARPORT | 9943 | CNR | Parks |  | Spring Valley | 2008 | 468 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1872
2267EXT1 | HISTORIC BUILDING MAINTENANCE | 2267 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HAMMOND CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 880 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13200
1177EXT1 | EXTERIOR FINISHES | 1177 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3340
1178ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1178 | The building contains a water fountain that is not Americans with Disabilities Act (ADA) compliant. The 2012 International Building Code (IBC) Section 1109.5 states "where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons." This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 4000
1218EXT1 | EXTERIOR FINISHES | 1218 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8270
1178INT1 | INTERIOR FINISHES | 1178 | It is recommended to maintain the Fiberglass Reinforced Plastic (FRP) at least once in the next 2-3 years. This will include cleaning all surfaces, if needed, adding additional adhesive or fasteners to the FRP, caulking and to make necessary repairs to expansion joints and moldings. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1218INT1 | INTERIOR FINISHES | 1218 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8270
2267EXT3 | HISTORIC STRUCTURES REPORT | 2267 | The building was constructed in 1870 and is currently not in use. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HAMMOND CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 880 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2266EXT1 | HISTORIC BUILDING MAINTENANCE | 2266 | The structure is made of unreinforced stone masonry. It is over 100 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6345
0513EXT2 | EXTERIOR FINISHES | 0513 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2990
2266INT1 | INTERIOR FINISHES | 2266 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4230
1220INT1 | INTERIOR FINISHES | 1220 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3330
2266EXT2 | HISTORIC STRUCTURE REPORT | 2266 | The building was constructed in 1870 and is currently operating as a living museum. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1180EXT1 | HISTORIC BUILDING MAINTENANCE | 1180 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for sealing the wood, replacing metal roof panels as needed, and to replace the wood siding as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TIMBER HORSE BARN | 9943 | CNR | Parks |  | Spring Valley | 1940 | 480 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2266SIT1 | DRAINAGE IMPROVEMENTS | 2266 | The site has a drainage problem around the Historic Stone Cabin where the grade does not properly slope away from the building. The rain accumulates in several areas adjacent to the building creating a water problem which may infiltrate the interior during inclement weather. This standing water also causes premature deterioration of the landscape improvements. This project would provide for a site survey and drainage report to be completed by a licensed professional and for that work to be performed by a licensed contractor. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | HISTORIC STONE CABIN | 9943 | CNR | Parks |  | Spring Valley | 1870 | 423 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1218SFT1 | FIRE EXTINGUISHER INSTALLATION | 1218 | The building does not have a portable fire extinguisher available. 2012 International Fire Code (IFC) Section 906 requires that portable fire extinguishers shall be installed in S occupancies. This project would provide funding for the purchase and installation of 2 fire extinguishers, cabinets and the hardware necessary to install them per IFC. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 1000
2924EXT1 | EXTERIOR FINISHES | 2924 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CAMPGROUND KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 175
1178EXT2 | EXTERIOR DOOR REPLACEMENT | 1178 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the seven door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
0513PLM1 | WATER HEATER REPLACEMENT | 0513 | There is an 80 gallon electric water heater in the building. The bottom of the water heater is rusted, due to leaking water from the inner tank, the water heater should be replaced immediately. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2200
3726EXT1 | EXTERIOR/ INTERIOR FINISHES | 3726 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 2010 | 98 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1960
3725EXT1 | EXTERIOR/ INTERIOR FINISHES | 3725 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 2010 | 98 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1960
2925EXT2 | ROOF REPLACEMENT | 2925 | The wood shingle roof on this kiosk was in poor condition at the time of the survey. It is recommended that this kiosk be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. | INFORMATION KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 216
2924EXT2 | ROOF REPLACEMENT | 2924 | The asphalt composition shingle roof on this Campground Kiosk was in poor condition at the time of the survey. It is recommended that this Campground Kiosk be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. | CAMPGROUND KIOSK | 9943 | CNR | Parks |  | Spring Valley | 2008 | 18 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 216
1220ELE1 | WIRING CLEANUP | 1220 | The wiring in the Park Headquarters Supply Room is disorganized and not in proper electrical boxes. This creates a safety issue. This project would provide for proper labeling, organization and for the wiring to be placed in electrical boxes per NEC 2011. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1218ELE1 | WIRING CLEANUP | 1218 | The wiring at the Park Headquarters Shop/ Garage does not have a dead panel or cover for the electrical panel. This creates a safety issue and is a code violation. This project would provide for a new dead panel, proper labeling and for the cover to be reinstalled over the electrical panel per NEC 2011. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2000
1218SFT2 | EXTERIOR LANDING INSTALLATION | 1218 | The concrete stairs that access the building are deteriorating. Spalling and cracking have occurred. Exposure to the elements is a contributing factor. It appears that the stairs are original to the building. The stairs do not comply with 2012 International Building Code (IBC) Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings and stairs. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 10000
1218ENR1 | LIGHTING UPGRADE | 1218 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6616
1218EXT2 | WINDOW REPLACEMENT | 1218 | The window is original, single pane construction and has a metal frame. This older window is drafty and not energy efficient. This project recommends replacing the window with a dual pane, higher efficiency unit. This estimate is for the replacement of one window. Removal and disposal of the existing window is included in this estimate. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1218HVA1 | ELECTRIC HEATER REPLACEMENT | 1218 | There is an electric heater in the Park Headquarters Shop/ Garage that has reached the end of its expected life. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | PARK HEADQUARTERS SHOP/ GARAGE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 827 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1178ADA4 | ADA SIGNAGE | 1178 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria include: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 750
1221EXT1 | EXTERIOR FINISHES | 1221 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking, sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS STORAGE SHED | 9943 | CNR | Parks |  | Spring Valley | 1998 | 1078 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2156
2262EXT2 | EXTERIOR/ INTERIOR FINISHES | 2262 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | NEW WELL/ PUMP HOUSE | 9943 | CNR | Parks |  | Spring Valley | 1998 | 60 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 1200
0523EXT1 | EXTERIOR FINISHES | 0523 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2160
0513INT2 | INTERIOR FINISHES | 0513 | It is recommended to repair and seal the interior concrete block walls at least once in 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | COMFORT STATION #3 | 9943 | CNR | Parks |  | Spring Valley | 2000 | 299 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2990
0523EXT2 | WINDOW REPLACEMENT | 0523 | The windows are older, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 windows. Removal and disposal of the existing windows is included in this estimate. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 3000
0523ENR1 | EXTERIOR LIGHTING REPLACEMENT | 0523 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, utilizing the existing wiring. | PARK OFFICE | 9943 | CNR | Parks |  | Spring Valley | 1940 | 216 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 800
0525PLM2 | WATER HEATER REPLACEMENT | 0525 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater, seismic straps, braided steel hose, expansion tank, ball valves and a pan be installed. Removal and disposal of the existing equipment is included in this estimate. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0525HVA1 | HEATER REPLACEMENT | 0525 | The building is heated by three wall mounted propane-fired and electric heating units. They have reached the end of their useful life. This project provides for disposal of the existing units and replacement with new propane-fired and electric units, and includes connections to utilities. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 4500
0525PLM1 | FUEL GAS SEDIMENT TRAP INSTALLATION | 0525 | The gas line serving the appliances in the residence does not have sediment traps. Per International Fuel Gas Code (IFGC) 2012, Section 408, where a sediment trap is not incorporated as part of the appliance, a sediment trap shall be installed downstream of the appliance shutoff valve as close to the inlet of the appliance as practical. The sediment trap shall be either; a tee fitting, having a capped nipple, of any length, installed vertically in the bottommost opening of the tee, or other device approved as an effective sediment trap. This project would provide for all labor and materials to have sediment traps installed near two gas heaters. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1176SFT1 | EXTERIOR LANDING INSTALLATION | 1176 | Section 1008.1, of the 2012 International Building Code (IBC), describes requirements for doors and landings; floors or landings shall be at the same elevation on each side of the door; exterior landings shall not exceed a 2% slope and shall have a length measured in the direction of travel of not less than 44 inches. There is no compliant landing located at the outside of the door of the building. This is out of compliance and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1177EXT2 | ROOF REPLACEMENT | 1177 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4560
1220EXT1 | EXTERIOR FINISHES | 1220 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS SUPPLY ROOM | 9943 | CNR | Parks |  | Spring Valley | 1940 | 333 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3330
1178ADA3 | ADA ACCESSIBLE PATH OF TRAVEL | 1178 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to Comfort Station #2 are necessary to comply with ADA accessibility requirements. This project would provide for the removal and replacement of the concrete van accessible ADA parking and loading space and the concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1178ADA2 | ADA SIDEWALK REPLACEMENT | 1178 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The concrete sidewalk around the building does not meet ADA requirements and is in need of replacement. Settling, spalling and cracking have created a non-ADA compliant path of travel to the restrooms. This project would provide for the removal and replacement of the concrete sidewalk. 500 SF of 4" thick P.C. concrete sidewalk was used for this estimate. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 7500
1175EXT1 | HISTORIC BUILDING MAINTENANCE | 1175 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MILLET RANCH CHICKEN COOP | 9943 | CNR | Parks |  | Spring Valley | 1930 | 208 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3120
1176INT1 | INTERIOR FINISHES | 1176 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1840
1176EXT1 | EXTERIOR FINISHES | 1176 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood finishes, re-pointing the stone where needed and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1840
1177ADA1 | ADA PARKING UPGRADE | 1177 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The ADA parking space next to the building is deteriorating and no longer meets the requirements of ADA. The concrete for the parking space, adjacent passenger loading zone and path of travel to the building is spalling and should be removed and replaced. The parking space and path of travel will also require updated signage and striping. 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1177HVA1 | ELECTRIC HEATER REPLACEMENT | 1177 | There are two electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 334 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1178PLM1 | FUEL GAS SEDIMENT TRAP INSTALLATION | 1178 | The gas line serving the appliances in the Comfort Station #2 does not have sediment traps. Per International Fuel Gas Code (IFGC) 2012, Section 408, "where a sediment trap is not incorporated as part of the appliance, a sediment trap shall be installed downstream of the appliance shutoff valve as close to the inlet of the appliance as practical. The sediment trap shall be either; a tee fitting, having a capped nipple, of any length, installed vertically in the bottommost opening of the tee, or other device approved as an effective sediment trap." This project would provide for all labor and materials to have sediment traps installed near all gas appliances. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1178EXT3 | ROOF REPLACEMENT | 1178 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old underlayment and roof. | COMFORT STATION #2 | 9943 | CNR | Parks |  | Spring Valley | 1975 | 380 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4560
1176ELE1 | GENERATOR REPLACEMENT | 1176 | There is a propane-fired generator on site that has reached the end of its expected life and was not working at the time of the survey. It does not have automatic switch gear and the room that it is stored in does not have proper ventilation. The generator provides backup power for the buildings. It is recommended that a new 12 kW propane-fired generator be installed. This estimate includes removal and disposal of the old generator. | PARK HEADQUARTERS GENERATOR BUILDING | 9943 | CNR | Parks |  | Spring Valley | 1979 | 184 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
3674EXT1 | HISTORIC BUILDING MAINTENANCE | 3674 | The underground structure is over 100 years old and is at rick of caving in. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for replacing any deteriorated wood poles or beams, replacing any stones that have become dislodged and patching the roof assembly to prevent water intrusion. This project would create a 5% slope away from the structure. Additional drainage swales shall be installed, as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAMMOND CABIN OUTBUILDING 2 | 9943 | CNR | Parks |  | Spring Valley | 1870 | 256 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
3673EXT1 | HISTORIC BUILDING MAINTENANCE | 3673 | The underground structure is over 100 years old and is at rick of caving in. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for replacing any deteriorated wood poles or beams, replacing any stones that have become dislodged and patching the roof assembly to prevent water intrusion. This project would create a 5% slope away from the structure. Additional drainage swales shall be installed, as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAMMOND CABIN OUTBUILDING 1 | 9943 | CNR | Parks |  | Spring Valley | 1870 | 300 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0522EXT2 | HISTORIC BUILDING MAINTENANCE | 0522 | The wood structure is over 77 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing, fixtures and windows, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MILLET RANCH LEAN-TO BARN | 9943 | CNR | Parks |  | Spring Valley | 1940 | 736 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11040
0524EXT3 | EXTERIOR LANDING INSTALLATION | 0524 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | OLD WELL/ PUMP HOUSE - CAMPGROUND | 9943 | CNR | Parks |  | Spring Valley | 1970 | 96 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0525EXT2 | EXTERIOR FINISHES | 0525 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RANGER RESIDENCE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 2280 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 22800
2922EXT2 | HISTORIC BUILDING MAINTENANCE | 2922 | The wood structure is over 76 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, caulking the flashing and fixtures, replacing metal roof panels as needed, replacing wood siding as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK HEADQUARTERS OUTHOUSE | 9943 | CNR | Parks |  | Spring Valley | 1941 | 25 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 375
9943ADA1 | CONCRETE STAIR REPLACEMENT | 9943 | There are two sets of stairs at the site constructed of landscaping blocks which do not meet construction, safety, or accessibility requirements, according to the 2012 International Building Code (IBC) Chapter 1009. One set of stairs near the restroom has four risers and the other rises up the face of the earthen dam with approximately 16 risers. This project recommends the installation of concrete landings, stairs and risers, with guard rails and handrails having proper height, spacing, and extensions according to the code requirements. Because of the critical construction dimensions and potential liability to the state, a licensed professional should be contracted to design the new stairs. IBC 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SPRING VALLEY STATE PARK SITE | 9943 | CNR | Parks |  | Spring Valley |  |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 25000
9944SIT3 | CRACK FILL & SEAL ASPHALT PAVING | 9944 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and sealing of the pavement site wide including the access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt was used to generate this estimate. It is recommended for this project to coincide with the ADA Parking Space project. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 250000
2935EXT2 | EXTERIOR FINISHES | 2935 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE KIOSK | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 32 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 175
2933EXT2 | EXTERIOR FINISHES | 2933 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FEE KIOSK | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 18 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 175
2929EXT120 | EXTERIOR FINISHES | 2929 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GARDEN SHED | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 120 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 1200
2252EXT3 | EXTERIOR FINISHES | 2252 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 15850
2930SFT2 | SAFETY CABINETS | 2930 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet Occupational Safety and Health Administration (OSHA) standards or International Fire Code (IFC) for hazardous materials containment. This project would provide for a self-closing hazardous storage container in the building and installing placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 5000
0552ADA1 | ADA PARKING UPGRADE | 0552 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There is a designated ADA parking space which does not meet the intent of the code. This project provides funding to bring the existing ADA parking space up to code including a concrete parking stall and loading zone, updated signage, striping and any other necessary upgrades. International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 6400
3716INT1 | INTERIOR FINISHES | 3716 | It is recommended to repair and seal the interior concrete block walls at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to sealing, all surfaces should be repaired and prepped. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1080
3716EXT0 | EXTERIOR FINISHES | 3716 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 1080
3715INT2 | INTERIOR FINISHES | 3715 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ENTRANCE FEE STATION | 9944 | CNR | Parks |  | Kershaw-Ryan | 2010 | 420 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 2500
3685EXT1 | EXTERIOR FINISHES | 3685 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the doors, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ELGIN GENERATOR BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 64 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 120
3716HVA1 | ELECTRIC HEATER REPLACEMENT | 3716 | There is an electric heater in the building that has reached the end of its expected life. This project recommends replacing the electric heater. The estimate includes removal and disposal of the existing equipment. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9944EXT2 | EXTERIOR FINISHES | 9944 | There are 17 wood and steel shade ramadas in different locations throughout the site which are either 144 s.f., 108 s.f. or 612 s.f. for a total of 2,880 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project is scheduled on a cyclical basis to maintain the integrity of the structures. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 5760
3716ENR1 | LIGHTING UPGRADE | 3716 | The interior light in the building has an old light fixture and is not energy efficient. This project would provide for the replacement of the interior light fixture and bulb with a new light fixture and LED bulb. An occupancy sensor will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 120 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350
3686EXT1 | EXTERIOR FINISHES | 3686 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | ELGIN OUTHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1924 | 25 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 300
3686INT1 | INTERIOR FINISHES | 3686 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. Due to the historical nature of the building, this project is subject to review and approval from the State Historical Preservation Office. | ELGIN OUTHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1924 | 25 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 300
0552PLM3 | WATER HEATER REPLACEMENT | 0552 | There is a 12 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0552INT2 | DOOR HARDWARE REPLACEMENT | 0552 | The exterior metal doors are in good shape, but staff has had continuous problems with the hardware. The handles and locks are damaged from age and general wear and tear and have reached the end of their useful life. This project would provide for the replacement of the hardware on seven doors. Removal and disposal of the existing hardware is included in this estimate. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
3686EXT2 | EXTERIOR DOOR REPLACEMENT | 3686 | The exterior door was missing at the time of the survey. This project would provide for the replacement and installation of a new metal door, frame and hardware. Removal and disposal of the existing door frame and painting of the new door is included in this estimate. | ELGIN OUTHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1924 | 25 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 2000
3715EXT0 | EXTERIOR FINISHES | 3715 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ENTRANCE FEE STATION | 9944 | CNR | Parks |  | Kershaw-Ryan | 2010 | 420 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 2500
2252HVA1 | HVAC EQUIPMENT REPLACEMENT | 2252 | The building is heated by a propane-fired heater and cooled with an air conditioner (split system). It is original to the building and is reaching the end of its useful life. This project provides for the disposal of the existing split system and the replacement with a new split system, and includes all connections to the utilities. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9944SIT2 | TREE REMOVAL | 9944 | There are five large cottonwood trees that pose a hazard to several buildings on the site. The trees drop large branches on the buildings as well as leaves and sap which contribute to the deterioration of the exterior of the building. The trees are dying and pose a threat to fall on the buildings. The trees should be removed before damage occurs. This project would provide funding to remove the trees and debris. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6500
2537EXT4 | CONCRETE FOUNDATION | 2537 | The addition to the backside of the Elgin Schoolhouse has wood to earth contact. This can lead to wood rot and insect infestation. Per 2012 International Building Code (IBC) Section 2304 wood siding, clearance between wood siding and earth on the exterior of the building shall not be less than 6 inches; wood shall be protected from decay and termites. This project will remove the addition on the backside of the Elgin Schoolhouse. A concrete foundation will be poured and the addition will be installed on top of the new concrete foundation. | ELGIN SCHOOLHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1921 | 1500 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 50000
0527ADA1 | ADA UPGRADES | 0527 | The Americans with Disabilities Act (ADA) provides for accessibility to Ramada #1 – Lower and services for people with physical limitations. There is a designated ADA parking space which does not meet the intent of the code. This project provides funding to bring the existing ADA parking space up to code including a concrete parking stall and loading zone, updated signage, striping and an ADA accessible pathway, picnic table and barbeque. International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. | GROUP USE RAMADA - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 612 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 30000
2537EXT3 | HISTORIC BUILDING MAINTENANCE | 2537 | The Elgin Schoolhouse is over 95 years old and there are numerous areas where the wood siding is missing and not painted or sealed properly. This is an exhibit for the park and requires maintenance and signage. This project would provide for the cleaning, repair and re-siding where needed and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ELGIN SCHOOLHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1921 | 1500 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0529INT1 | INTERIOR FINISHES | 0529 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BRICK PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2008 | 100 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3685SFT1 | BATTERY STORAGE IMPROVEMENTS | 3685 | Section 608 of the 2012 International Fire Code (IFC) explains the requirements for stationary storage of battery systems. This project will provide funding to properly store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirements of Section 608 of the 2012 IFC. | ELGIN GENERATOR BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2009 | 64 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 25000
0553EXT1 | HISTORIC BUILDING MAINTENANCE | 0553 | The structure is made of unreinforced stone masonry. It is over 82 years old and there are numerous areas where the mortar is failing, missing and not sealed properly. This is also an exhibit for the park and requires maintenance and requires signage. This project would provide for the cleaning, repair and re-pointing of the stone work and maintaining the exhibit. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CCC RESTROOM | 9944 | CNR | Parks |  | Kershaw-Ryan | 1934 | 78 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
2930EXT3 | OVERHEAD DOOR REPLACEMENT | 2930 | There is an overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2252PLM2 | WATER HEATER REPLACEMENT | 2252 | There is a 40 gallon propane fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2200
2931HVA1 | HEATER REPLACEMENT | 2931 | The building is heated by two wall mounted propane-fired heating units. One of the two heaters is original to the building and is reaching the end of its useful life. This project provides for the disposal of the existing unit and the replacement with a new propane-fired unit and includes all connections to utilities. | GREENHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 495 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2252INT3 | KITCHEN REMODEL | 2252 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid range, high quality components. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2252INT2 | CARPET REPLACEMENT | 2252 | The carpet in the building is showing signs of extreme wear and should be scheduled for replacement. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next 2-3 years. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8820
2930ENR2 | LIGHTING UPGRADE | 2930 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2840
2934EXT1 | EXTERIOR FINISHES | 2934 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #2 - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 2003 | 1024 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
0553EXT2 | HISTORIC STRUCTURE REPORT | 0553 | The building was constructed in 1934. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. | CCC RESTROOM | 9944 | CNR | Parks |  | Kershaw-Ryan | 1934 | 78 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 8000
2930EXT1 | EXTERIOR FINISHES | 2930 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 710
0552ENR1 | LIGHTING UPGRADE | 0552 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade the fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3616
2252EXT2 | HANDRAIL & CONCRETE LANDING INSTALLATION | 2252 | The entry deck and stairs/ landing do not meet current code. This project would provide for a guardrail around the deck, guardrail and handrail at the stairs and a 4" thick concrete landing at the bottom of the stairs. The 2012 International Building Code (IBC) Chapter 10, Section's 1009.4, 1012 and 1013 were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
2934INT1 | INTERIOR FINISHES | 2934 | It is recommended to repair and seal the interior concrete block walls in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #2 - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 2003 | 1024 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
0552INT1 | INTERIOR FINISHES | 0552 | It is recommended that the interior walls and ceilings be painted or sealed at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4520
0552EXT1 | EXTERIOR FINISHES | 0552 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | COMFORT STATION #1 - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 452 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 4520
2252INT1 | INTERIOR FINISHES | 2252 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK RESIDENCE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 1585 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15850
2537EXT2 | HISTORIC STRUCTURES REPORT | 2537 | The building was constructed in 1921 and is currently operating as a living museum. It may be eligible to be on the National Register of Historic Places. A historic structure report would provide documentary, graphic, and physical information about a property's history and existing condition. It also provides guidelines for maintenance of the building. This project recommends obtaining the report in accordance with the U.S. Department of Interior Recommended Guidelines in Preservation Brief 43. This property may be eligible for federal grants or special funding if this project is implemented. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | ELGIN SCHOOLHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1921 | 1500 | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 15000
2928INT1 | INTERIOR FINISHES | 2928 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE OFFICE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 200 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2930INT1 | INTERIOR FINISHES | 2930 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 355 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3550
2931EXT1 | EXTERIOR FINISHES | 2931 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior building envelope including repairs to the exterior membrane and caulking around the flashing, fixtures, and other penetrations to maintain the building in good weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | GREENHOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 495 | 2016-04-12 | Two to Four Years | Necessary - Not Yet Critical | 2 | 990
2932EXT1 | EXTERIOR FINISHES | 2932 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK RESIDENCE GARAGE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2006 | 290 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 580
0549EXT1 | EXTERIOR FINISHES | 0549 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior of the structure, other than the roof, including sealing, painting or other applied finishes, and caulking around, flashing, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GROUP USE RAMADA - UPPER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 612 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 6120
0529EXT1 | EXTERIOR FINISHES | 0529 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | BRICK PUMP HOUSE | 9944 | CNR | Parks |  | Kershaw-Ryan | 2008 | 100 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 1000
0527EXT1 | EXTERIOR FINISHES | 0527 | It is important to maintain the finish, weather resistance and appearance of the structure. This project recommends work to protect the exterior of the structure, other than the roof, including sealing, painting or other applied finishes, and caulking around, flashing, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | GROUP USE RAMADA - LOWER | 9944 | CNR | Parks |  | Kershaw-Ryan | 1996 | 612 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 6120
2928EXT1 | EXTERIOR FINISHES | 2928 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4-5 years and it is also recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | PARK MAINTENANCE OFFICE | 9944 | CNR | Parks |  | Kershaw-Ryan | 1998 | 200 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 2000
3702EXT1 | EXTERIOR FINISHES | 3702 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2014 | 900 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 9000
3702INT1 | INTERIOR FINISHES | 3702 | It is recommended to paint the interior walls and ceilings at least once in the next 9-10 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE BUILDING | 9944 | CNR | Parks |  | Kershaw-Ryan | 2014 | 900 | 2016-04-12 | Four to Ten Years | Long-Term Needs | 3 | 9000
9944ADA1 | ADA UPGRADES | 9944 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The upper area of the park including the Ramada #1 - Upper, wading pool and children's playground should be accessible to comply with ADA regulations. A hard-surfaced parking area with an adjacent passenger loading zone should be installed near Ramada #1 - Upper, including compliant signage and striping. A compliant path of travel should be provided from the ADA parking space to the ramada, wading pool and playground. The path will likely include several accessible ramps. IBC 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 260000
9944ADA3 | INSTALL HANDRAILS | 9944 | The existing stone and concrete stairs which connect the access road to Ramada #1 - Upper are missing handrails. The 2012 International Building Code (IBC) Chapter 1009.15 states that stairways shall have handrails on each side. This project would provide for 1-1/2 inch diameter steel handrails, one on each side of the stairway to meet the 2012 IBC code requirements. Painting of the handrails is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/16/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/12/2016. | KERSHAW-RYAN STATE PARK SITE | 9944 | CNR | Parks |  | Kershaw-Ryan |  |  | 2016-04-12 | Immediate to Two Years | Currently Critical | 1 | 10000
0508EXT2 | WINDOW REPLACEMENT | 0508 | The windows are original, double pane construction with metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. Removal and disposal of the existing windows is included in this estimate. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3750EXT1 | EXTERIOR FINISHES | 3750 | It is important to maintain the finish, weather resistance and appearance of the ramada. This project would provide funding to protect the exterior of the ramada excluding the roof. Included in the cost is power washing and staining the wood. It is recommended that the ramada be stained in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK OFFICE SHADE STRUCTURE | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 232 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 464
3729EXT1 | EXTERIOR/ INTERIOR FINISHES | 3729 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RV ADA COMFORT STATION #1 | 9945 | CNR | Parks |  | Echo Canyon | 2014 | 432 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 8640
3728EXT1 | EXTERIOR FINISHES | 3728 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RESIDENCE METAL SHED #2 | 9945 | CNR | Parks |  | Echo Canyon | 0 | 450 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 900
3727EXT1 | EXTERIOR FINISHES | 3727 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PARK RESIDENCE METAL SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 90 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 180
3727SFT1 | SAFETY CABINETS | 3727 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet Occupational Safety and Health Administration (OSHA) standards or International Fire Code (IFC) for hazardous materials containment. This project would provide for a self-closing hazardous storage container in the building and the installation of placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | PARK RESIDENCE METAL SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 90 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3082EXT2 | ROOF REPLACEMENT | 3082 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes the installation of a new roof and the removal and disposal of the old roofing. | PARK OFFICE STORAGE SHED #2 | 9945 | CNR | Parks |  | Echo Canyon | 2004 | 288 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3456
3081EXT2 | ROOF REPLACEMENT | 3081 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes the installation of a new roof and the removal and disposal of the old roofing. | PARK OFFICE STORAGE SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 2008 | 288 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 3456
1065EXT2 | CONCRETE PATCH/ ROOFING | 1065 | It is important to maintain the water proofing and structural integrity of the concrete roof deck on the building. This project would provide funding to repair the spalling concrete using an epoxy patch (to repair and seal) and then painting with an epoxy-based paint on the concrete roof decking. Included in the cost is the preparation of the concrete roof decking by cleaning, sanding, and removing all paint, loose concrete and aggregate from the roof decking. Per 2012 International Energy Conservation Code (IECC), the minimum insulation in a zone 5 entirely above the deck per Table C402.2 is R- 25. After the concrete roof decking is completely repaired, an R-25 insulation is to be fastened to the concrete roof decking, and a fully adhered single ply membrane should be installed over the insulation. The current roof decking was installed in 1970 and it is recommended that the work be performed in the next year. | PARK WELL HOUSE | 9945 | CNR | Parks |  | Echo Canyon | 1970 | 48 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 5280
0509ELE2 | WIRING CLEANUP | 0509 | The wiring inside the Comfort Station #3 - Boat Ramp is disorganized and not in proper electrical boxes, particularly the old main service wires. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per National Electrical Code (NEC) 2011. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0509PLM1 | WATER HEATER REPLACEMENT | 0509 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is 8-10 years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in the estimate. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 2500
9945ADA7 | ADA SIGNAGE | 9945 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage at the Park Office does not comply with these criteria. This project would provide funding for the purchase and installation of ADA signage, including directional signage from parking to accessible building entrances. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0508ADA3 | ADA UPGRADES | 0508 | Section 4.13.9 of the Americans with Disabilities Act Accessibility Guidelines (ADAAG) states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 500
9945ADA5 | ADA PARKING SPACE | 9945 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. At the Park Office a concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete, van accessible, ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0507PLM1 | WATER HEATER REPLACEMENT | 0507 | There is a 74 gallon propane water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was installed in 2004. It is recommended that a new propane water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and a pan be installed. The removal and disposal of the existing equipment is included in this estimate. | PARK RESIDENCE | 9945 | CNR | Parks |  | Echo Canyon | 1991 | 1580 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0508ADA2 | ADA PARKING SPACE | 0508 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete, van accessible, ADA parking and loading space and a walkway. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
9945ADA6 | ADA ACCESSIBLE PATH OF TRAVEL | 9945 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Park Office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete, van accessible, ADA parking and loading space, and a concrete ADA walkway to the existing sidewalk. This will require re-grading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180, and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the ADA parking and ADA signage projects. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1064EXT2 | EXTERIOR FINISHES | 1064 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 4330
1063EXT2 | EXTERIOR FINISHES | 1063 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 4370
0509ADA2 | ADA SIGNAGE | 0509 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
1064ADA1 | ADA PARKING AND PATH OF TRAVEL | 1064 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
1064ADA2 | ADA RESTROOM UPGRADE | 1064 | The Men's and Women's restrooms do not comply with the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding to remodel one Men's and one Women's accessible restroom in the building. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 40000
1064ADA3 | ADA SIGNAGE | 1064 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
1065EXT1 | EXTERIOR/ INTERIOR FINISHES | 1065 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost is repairing cracked concrete, painting the precast concrete and caulking of any exterior penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended for this work to be performed in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK WELL HOUSE | 9945 | CNR | Parks |  | Echo Canyon | 1970 | 48 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
1101EXT1 | EXTERIOR FINISHES | 1101 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE STORAGE SHED #3 | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 198 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 396
3081EXT1 | EXTERIOR FINISHES | 3081 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE STORAGE SHED #1 | 9945 | CNR | Parks |  | Echo Canyon | 2008 | 288 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
3082EXT1 | EXTERIOR FINISHES | 3082 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE STORAGE SHED #2 | 9945 | CNR | Parks |  | Echo Canyon | 2004 | 288 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2880
0509EXT1 | EXTERIOR FINISHES | 0509 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0508ADA1 | ADA DOOR & THRESHOLD REPLACEMENT | 0508 | The existing exterior entrance door and threshold to the Park Office is not accessible. This project would provide for a new accessible door and threshold assembly including removal of the existing door assembly and installation of the new accessible door assembly. ADA compliant signage is also included in this project. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. This project or a portion there of was previously recommended in the FCA report dated 09/27/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/29/2016. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0509ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0509 | There is a water fountain mounted on the exterior of this building. The 2012 International Building Code (IBC) Section 1109.5 states where a water fountain is provided, at least half should be accessible for people who use a wheelchair. This project would provide funding for the purchase and installation of a ADA new accessible fixed high/ low drinking fountain. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 4000
0509ENR1 | PHOTOVOLTAIC SYSTEM INSTALLATION | 0509 | There is a propane-fired furnace and a propane-fired water heater in the building that are not connected to power. The existing photovoltaic system only has enough power for the lighting and it is recommended to install a second photovoltaic system to provide additional power. This project would provide for the purchase and installation of a photovoltaic system including solar panels, deep cycle solar batteries and all associated electrical boxes and hardware to connect it to the furnace and water heater. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0510EXT1 | EXTERIOR FINISHES | 0510 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 930
0510INT1 | INTERIOR FINISHES | 0510 | It is recommended that the Fiberglass Reinforced Panels be power washed and re-caulked as needed. This project should be done at least once in the next 2-3 years and scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 930
0510ADA1 | ADA SIGNAGE | 0510 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
0510ADA2 | FISH CLEANING STATION REPLACEMENT | 0510 | The Fish Cleaning Station is original to the building, has reached the end of its expected life and does not meet the Americans with Disabilities Act (ADA) requirements. A complete replacement of the fish cleaning equipment is necessary. This project would provide for removal and disposal of the existing equipment and the replacement with a new accessible fish cleaning station equipped with a grinder and sprayer. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | FISH CLEANING STATION - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 93 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 10000
9945EXT1 | EXTERIOR FINISHES | 9945 | There are 63 wood and steel shade ramadas in different locations throughout the site which are either 144 s.f., 224 s.f., 234 s.f., 256 s.f., or 493 s.f. for a total of 14,010 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for the painting of the structures. It is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71924
0509INT1 | INTERIOR FINISHES | 0509 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #3 - BOAT RAMP | 9945 | CNR | Parks |  | Echo Canyon | 1994 | 250 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1063INT1 | INTERIOR FINISHES | 1063 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4370
0508INT1 | INTERIOR FINISHES | 0508 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion there of was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1470
1063ADA3 | ADA SIGNAGE | 1063 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009, Nevada Revised Statutes (NRS) 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 2500
1064INT1 | INTERIOR FINISHES | 1064 | It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #1 - NORTH CAMPGROUND | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 433 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4330
1063ADA2 | ADA RESTROOM UPGRADE | 1063 | The Men's and Women's restrooms do not comply with the Americans with Disabilities Act (ADA) requirements. A complete retrofit is necessary. This project would provide funding remodel one Men's and one Women's accessible restroom in the building. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. Nevada Revised Statutes (NRS) 338.180, International Building Code (IBC) 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 40000
9945ADA3 | ADA HANDRAIL INSTALLATION | 9945 | The Americans with Disabilities Act (ADA) ramp leading up to the amphitheater is missing handrails. This project recommends the installation of handrails on both sides of the ramp and compliant returns and supports. Nevada Revised Statutes (NRS) 338.180, 2012 International Building Code (IBC) Chapter 10, Section 1012, ICC/ANSI A117.1 - 2009, and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ECHO CANYON STATE PARK SITE | 9945 | CNR | Parks |  | Echo Canyon | 1970 |  | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 15000
1068EXT1 | REBUILD STRUCTURE | 1068 | The ramada is structurally failing and should be scheduled for replacement. This project would provide for demolishing the existing structure and rebuilding a new one. The new structure will have new concrete footings, steel framing and a metal standing seam roof. The design plans and permitting fees are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | RAMADA - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 493 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1063ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 1063 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restrooms are necessary to comply with ADA accessibility requirements. This project would provide for a concrete, van accessible, ADA parking and loading space, and a concrete ADA walkway to the existing sidewalk. This will require re-grading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 International Building Code (IBC), ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | COMFORT STATION #2 - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 437 | 2016-04-13 | Immediate to Two Years | Currently Critical | 1 | 30000
0507EXT1 | EXTERIOR FINISHES | 0507 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RESIDENCE | 9945 | CNR | Parks |  | Echo Canyon | 1991 | 1580 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 15800
0508EXT1 | EXTERIOR FINISHES | 0508 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding and painting the wood trim and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion there of was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK OFFICE | 9945 | CNR | Parks |  | Echo Canyon | 1986 | 147 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1470
0507INT1 | INTERIOR FINISHES | 0507 | It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | PARK RESIDENCE | 9945 | CNR | Parks |  | Echo Canyon | 1991 | 1580 | 2016-04-13 | Four to Ten Years | Long-Term Needs | 3 | 15800
1067EXT1 | REBUILD STRUCTURE | 1067 | The ramada is structurally failing and should be scheduled for replacement. This project would provide for demolishing the existing structure and rebuilding a new one. The new structure will have new concrete footings, steel framing and a metal standing seam roof. The design plans and permitting fees are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | ADA RAMADA - GROUP AREA | 9945 | CNR | Parks |  | Echo Canyon | 1990 | 493 | 2016-04-13 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
3020EXT1 | EXTERIOR/ INTERIOR FINISHES | 3020 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior and interior of the building. Included in the cost is sanding and sealing the wood framing. It is recommended that the wood framing be sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | LAKEVIEW CAMPGROUND YURT | 9946 | CNR | Parks |  | Cave Lake | 2003 | 160 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 320
2257EXT1 | EXTERIOR/ INTERIOR FINISHES | 2257 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #1 - BOAT RAMP | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
2257ADA1 | ADA PARKING SPACE | 2257 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the restroom. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #1 - BOAT RAMP | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
1284INT1 | INTERIOR FINISHES | 1284 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13600
1284ADA1 | ADA RESTROOM UPGRADE | 1284 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
1284ENR1 | LIGHTING UPGRADE | 1284 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10880
1284SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1284 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 1360
1284SFT2 | FIRE ALARM SYSTEM INSTALLATION | 1284 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 IFC. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 5440
2258ADA1 | ADA PARKING SPACE | 2258 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #2 - GROUP USE AREA | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
2258EXT1 | EXTERIOR/ INTERIOR FINISHES | 2258 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #2 - GROUP USE AREA | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
2259ADA1 | ADA PARKING SPACE | 2259 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the restroom. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #3 - OVERLOOK TRAILHEAD | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
2259EXT1 | EXTERIOR/ INTERIOR FINISHES | 2259 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CXT RESTROOM #3 - OVERLOOK TRAILHEAD | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
1295EXT1 | EXTERIOR FINISHES | 1295 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
3020SFT1 | EXTERIOR HANDRAIL REPLACEMENT | 3020 | The exterior stairs and deck have handrails and a guardrail that do not meet building code requirements for safety. The gripping surfaces are incorrect, they are not continuous from the top to bottom landings and the deck is lacking a guardrail. This project recommends the installation of guardrails and handrails in accordance with the 2012 IBC Section 1012 and 1013. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | LAKEVIEW CAMPGROUND YURT | 9946 | CNR | Parks |  | Cave Lake | 2003 | 160 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 1000
1284SIT1 | CONCRETE APRON REPLACEMENT | 1284 | The exterior concrete apron at the shop area has extensive cracking and spalling and is due for replacement. This project would provide for the installation of a new 200 square foot, 4" thick concrete slab-on-grade apron at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
3021ADA1 | ADA PARKING SPACE | 3021 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the information booth. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. | CAVE LAKE INFORMATION BOOTH | 9946 | CNR | Parks |  | Cave Lake | 1991 | 96 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
3021INT1 | INTERIOR FINISHES | 3021 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE INFORMATION BOOTH | 9946 | CNR | Parks |  | Cave Lake | 1991 | 96 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3021EXT1 | EXTERIOR FINISHES | 3021 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAVE LAKE INFORMATION BOOTH | 9946 | CNR | Parks |  | Cave Lake | 1991 | 96 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
3022EXT1 | EXTERIOR FINISHES | 3022 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | ELK FLAT INFORMATION KIOSK | 9946 | CNR | Parks |  | Cave Lake | 2003 | 15 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
1284PLM1 | WATER HEATER REPLACEMENT | 1284 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1295ENR1 | GENERATOR REPLACEMENT | 1295 | There is a propane-fired generator on site that has reached the end of its expected life and is no longer operating. The generator provides backup power when the photovoltaic system cannot keep up with demand. It is recommended that a new 12 kW propane-fired generator be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
1280EXT1 | EXTERIOR FINISHES | 1280 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1294SFT1 | SMOKE DETECTOR UPGRADE | 1294 | IRC 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012 require that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 1000
1280INT3 | JANITORS CLOSET REPAIRS | 1280 | The mop sink is mounted adjacent to OSB and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1280HVA1 | HEATER REPLACEMENT | 1280 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1280SFT1 | FIRE EXTINGUISHER INSTALLATION | 1280 | The building does not have a portable fire extinguisher available. International Fire Code Section 906 requires that portable fire extinguishers shall be installed in B occupancies. They shall be provided for employee use and selected and distributed based on the classes of anticipated workplace fires and on the size and degree of hazard which would affect their use. This project would provide funding for the purchase and installation of 1 fire extinguisher, cabinet, and the hardware necessary to install it. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 500
1295SFT1 | SMOKE DETECTOR UPGRADE | 1295 | IRC 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2500
3019EXT1 | EXTERIOR FINISHES | 3019 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | FISH CLEANING STATION | 9946 | CNR | Parks |  | Cave Lake | 2003 | 100 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1295ENR2 | WINDOW REPLACEMENT | 1295 | The windows are original, dual pane construction in a metal frame. These older windows have damaged seals, are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1284EXT1 | EXTERIOR FINISHES | 1284 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding and sealing, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be stained and painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13600
1288ENR1 | HEATER REPLACEMENT | 1288 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new energy efficient propane-fired unit including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1288INT1 | INTERIOR FINISHES | 1288 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3300
1288EXT1 | EXTERIOR FINISHES | 1288 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project should coincide with the siding replacement project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3300
1289INT2 | SHOWER REPAIRS | 1289 | There are two shower rooms in the building that are showing signs of failure in the walls and should be scheduled for repairs. The walls are constructed of gypsum board covered by FRP. The gypsum board is failing in the wet environment and should be replaced with a cementitious backerboard. This project would provide for removing the gypsum board and replacing it with a more appropriate wall board, such as Hardiboard, covered with new FRP. Removal and disposal of the existing materials is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 7500
1289INT1 | INTERIOR FINISHES | 1289 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1289EXT1 | EXTERIOR FINISHES | 1289 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is replacing the wood trim around the building, sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the trim be replaced and the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1293EXT1 | EXTERIOR FINISHES | 1293 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. This project includes the cost for sanding, priming and painting and the caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | EQUIPMENT STORAGE BUILDING | 9946 | CNR | Parks |  | Cave Lake | 1981 | 204 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2040
1294INT1 | INTERIOR FINISHES | 1294 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1288EXT2 | EXTERIOR SIDING REPLACEMENT | 1288 | The restroom has painted T1-11 siding that is in poor condition and due for replacement. It is cracking and buckling from exposure and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new Cementitious T1-11. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1520
1295INT1 | INTERIOR FINISHES | 1295 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10080
1295EXT2 | ROOF REPLACEMENT | 1295 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next two to three years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #2 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 1008 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15120
1294EXT1 | EXTERIOR FINISHES | 1294 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1280INT1 | INTERIOR FINISHES | 1280 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3800
1284SIT2 | SITE BOLLARDS | 1284 | There are two above ground fuel tanks on the site, one for diesel and unleaded gasoline, and the other holds propane for the building. These tanks do not have adequate bollard coverage. Per IFC 2012 Section 312 Vehicle Impact Protection, there needs to be steel posts installed, not less than 4 inches in diameter and filled with concrete. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for eight new bollards to be located in front of the tanks. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1289HVA1 | HEATER REPLACEMENT | 1289 | The building is heated by one wall mounted propane-fired heating unit. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1289SFT1 | BATTERY STORAGE | 1289 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. Batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced and a smoke alarm. This project will provide funding for the requirements of Section 608 of the 2012 IFC proper way to store, charge and/or use batteries indoors. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
1289INT4 | RESTROOM REMODEL | 1289 | The restrooms in the building were in poor condition at the time of the survey. They are original to the building and are due for a complete remodel. This project would provide for a complete remodel of the restroom fixtures, hardware, floor and wall finishes. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
1289EXT4 | EXTERIOR SIDING REPLACEMENT | 1289 | The restroom has painted T1-11 siding that is in poor condition and due for replacement. It is cracking and buckling from exposure and will no longer hold paint. This project recommends removing the T1-11 siding and replacing it with new Cementitious T1-11. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1600
1288ADA1 | ADA SIDEWALK REPLACEMENT | 1288 | The concrete sidewalk around the building is in need of replacement. It is cracked, spalling and in some areas it exceeds a 2% slope. This project would provide for the removal and replacement of the concrete sidewalks. 1500 SF of 4" thick concrete was used for this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 22500
1289EXT3 | EXTERIOR DOOR REPLACEMENT | 1289 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the seven door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
1284HVA1 | HEATER REPLACEMENT | 1284 | The building is heated by two wall mounted propane-fired heating units. They are original to the building and are reaching the end of their useful life. This project provides for the disposal of the existing units and the replacement of new propane-fired units including all connections to the utilities. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1294INT2 | KITCHEN REMODEL | 1294 | The kitchen was is in fair to poor condition at the time of the survey. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid-range, high quality components. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
1284INT3 | JANITORS CLOSET REPAIRS | 1284 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1284SFT3 | SMOKE CARBON MONOXIDE ALARM INSTALLATION | 1284 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. IFC 2012 Section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with these codes. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1284ADA2 | ADA UPGRADES | 1284 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 5000
1284SFT4 | SAFETY CABINETS | 1284 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1288ELE1 | WIRING CLEANUP | 1288 | The wiring is disorganized and not in proper electrical boxes. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | RESTROOM #2 - DAY USE | 9946 | CNR | Parks |  | Cave Lake | 1981 | 330 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1289INT3 | JANITORS CLOSET REPAIRS | 1289 | The mop sink in the plumbing chase is mounted adjacent to studs without a wall backing and is showing signs of water damage. This project would provide for a Cementitious Backer and FRP to be installed on the walls adjacent to the mop sink. The Cementitious Backer and FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1289PLM1 | WATER HEATER REPLACEMENT | 1289 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RESTROOM #3 - ELK FLAT | 9946 | CNR | Parks |  | Cave Lake | 1991 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1294HVA1 | HEATER REPLACEMENT | 1294 | The building is heated by one propane-fired furnace. It is original to the building and is reaching the end of its useful life. This project provides for disposal of the existing furnace and the replacement with a new propane-fired furnace to include the connections to the existing utilities and cleaning the ductwork. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1294PLM1 | WATER HEATER REPLACEMENT | 1294 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
1294EXT2 | ROOF REPLACEMENT | 1294 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. | RESIDENCE #1 - LAKEVIEW | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1200 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
2257PLM1 | SEPTIC SYSTEM REPLACEMENT | 2257 | The septic system serving the restroom is failing. This project recommends replacing the septic tank. The estimate includes abandoning and filling the old septic tank and the installation of a new tank and leach field. This estimate is for an engineered system which will conform to all required environmental rules and regulations including NDEP. | CXT RESTROOM #1 - BOAT RAMP | 9946 | CNR | Parks |  | Cave Lake | 2002 | 112 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
3022EXT2 | ROOF REPLACEMENT | 3022 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roof. | ELK FLAT INFORMATION KIOSK | 9946 | CNR | Parks |  | Cave Lake | 2003 | 15 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
1280ELE1 | WIRING CLEANUP | 1280 | The wiring is disorganized and not in proper electrical boxes, particularly the old main service wires. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1280PLM1 | WATER HEATER REPLACEMENT | 1280 | There is an on-demand propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | RESTROOM #1 - LAKEVIEW CAMPGROUND | 9946 | CNR | Parks |  | Cave Lake | 1981 | 380 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1284SFT5 | FLUE CLEANING | 1284 | At the time of the survey the chimney flue had a buildup of creosote deposits and other debris. Creosote buildup in chimneys can lead to chimney fires or flue blockages. Flue blockage, which may be caused by creosote or other debris, such as animal nesting, can cause dangerous fumes to be forced into the building. It is recommended that the chimney flue be swept to clean and maintain the flue system. The Chimney Safety Institute of America recommends that open masonry fireplaces be cleaned at 1/4" of sooty buildup, and sooner if there is any glaze present in the system. Per NFPA 211 it is recommended that this should be performed once a year. | CAVE LAKE OFFICE/ SHOP | 9946 | CNR | Parks |  | Cave Lake | 1981 | 1360 | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 2000
1293EXT2 | GARAGE DOOR REPLACEMENT | 1293 | The garage door is original to the building and has deteriorated from weather exposure. Because it is constructed of wood it is harder to maintain. It is recommended for a new door to be installed. | EQUIPMENT STORAGE BUILDING | 9946 | CNR | Parks |  | Cave Lake | 1981 | 204 | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9946SIT2 | CRACK FILL & SEAL ASPHALT PAVING | 9946 | It is important to maintain the asphalt concrete paving on the site. This project would provide for: minor crack filling; slurry sealing of the paving site wide, including parking areas; the turnout at the information kiosk; the boat ramp access, the maintenance yard and striping. All other paving is maintained by NDOT. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62500
9946ENR1 | PHOTOVOLTAIC EQUIPMENT REPLACEMENT | 9946 | The existing photovoltaic equipment site wide is over 25 years old. This original equipment has a design life of 7 years. The batteries no longer hold a full charge and replacement parts are no longer available. This project will replace the photovoltaic equipment site wide including, but not limited to: the solar panels; tracking systems; control panels; inverters and the batteries. The removal and the disposal of the existing equipment are included in this estimate. This project will provide for new photovoltaic equipment for the Cave Lake Office/ Shop, the two residences, three restrooms and the Fish Cleaning Station. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 260000
9946SIT3 | BOAT DOCK REPAIRS | 9946 | The boat dock has an area covered by concrete pavers which is settling and due for repairs. The settled area causes a tripping hazard and will continue to settle due to ponding water. This project would provide for the removal of the existing pavers, adding fill, compacting and installing new pavers. This project should be implemented concurrently with the ADA UPGRADES - BOAT DOCK project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6250
9946ADA3 | ADA UPGRADES - LAKEVIEW CAMPGROUND | 9946 | The Lakeview Campground currently has one accessible space that is well graded, but is not in compliance with ADA regulations. Upgrades to the campsite should include 20'-0" wide concrete drive aisles for RV/ tent trailer sites and accessible amenities on an accessible route including grills, picnic tables, fire rings and water & electric utilities. This project provides for upgrading the existing accessible campsite to a fully compliant accessible campsite. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG – 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 8750
9946ADA4 | ADA UPGRADES - DAY USE | 9946 | The ADA provides for accessibility to sites and services for people with physical limitations. A compliant path of travel from the accessible parking space to the restroom and picnic area and an accessible picnic table are necessary to comply with ADA accessibility requirements. This project provides funding for a compliant path of travel and an accessible picnic table. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 10000
9946ADA5 | ADA UPGRADES - GROUP USE | 9946 | The ADA provides for accessibility to sites and services for people with physical limitations. The Group Use area does not have an accessible path of travel to the restroom, picnic area or presentation area. This project provides funding to install a compliant path of travel from the accessible parking space to these three areas as well as upgrading the picnic table to an accessible table. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 20000
9946SFT1 | STAIR REPLACEMENT - GROUP USE | 9946 | There is a flight of stairs in the group use area that provides access to the shoreline. The stairs are made of wood that are set in the dirt and they do not have the proper handrails per IBC. This project would provide for replacing the existing stairs with concrete steps and compliant handrails in accordance with IBC Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 15000
9946ADA1 | ADA UPGRADES - BOAT DOCK | 9946 | The ADA provides for accessibility to sites and services for people with physical limitations. The existing ADA parking space at the boat dock does not meet the ADA requirements. The boat dock has a picnic area that should be ADA accessible. This project provides funding to bring the existing ADA parking space up to code including the removal of the asphalt and replacement with P.C. concrete, updated signage, re-striping, re-grading and any other necessary upgrades. The project funding will also provide for an accessible path of travel from the parking space and an accessible picnic table at the picnic area. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and ADAAG - 2010 were referenced for this project. This project should be implemented concurrently with the BOAT DOCK REPAIRS project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 05/23/2017. | CAVE LAKE STATE PARK SITE | 9946 | CNR | Parks |  | Cave Lake |  |  | 2017-05-23 | Immediate to Two Years | Currently Critical | 1 | 25000
1039ADA1 | ADA RESTROOM UPGRADE | 1039 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 40000
1040ENR1 | LIGHTING UPGRADE | 1040 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35200
1037EXT1 | EXTERIOR FINISHES | 1037 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4-5 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CAMPGROUND STORAGE | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 117 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1170
1044SIT1 | CONCRETE SLAB-ON-GRADE INSTALLATION | 1044 | Group Ramada #2 has a dirt floor area underneath the structure. This project would provide for the installation of a concrete slab-on-grade, 3-1/2 inches thick, underneath the structure. Included in this estimate is a 3-1/2 inches thick concrete walkway from the parking area to the Ramada. 800 square feet of concrete was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | GROUP RAMADA #2 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6400
1038INT1 | INTERIOR FINISHES | 1038 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MILLER'S POINT COMFORT STATION #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 120 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1038EXT1 | EXTERIOR FINISHES | 1038 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MILLER'S POINT COMFORT STATION #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 120 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
1039HVA1 | ELECTRIC HEATER REPLACEMENT | 1039 | There are two electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4400
1039ADA3 | ADA SIDEWALK REPAIR | 1039 | The ADA provides for accessibility to sites and services for people with physical limitations. The concrete sidewalk around the building does not meet ADA requirements and is in need of replacement. Settling, spalling and cracking have created a non-ADA compliant path of travel to the restrooms. This project would provide for the removal and replacement of the concrete sidewalk. 500 SF of 4" thick P.C. concrete sidewalk was used for this estimate. IBC 2012, ICC/ANSI A117.1- 2009 and ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 7500
1040SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1040 | The building is B occupancy per the 2012 IBC. Pursuant to the NSFM Regulation NAC 477.915 (c) which states, every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project also includes an allowance for 100 lineal feet of 4" water line, excavation and backfill, all fittings and an above ground backflow prevention device. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61600
1039ADA2 | ADA SIGNAGE | 1039 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 900
1039INT1 | INTERIOR FINISHES | 1039 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3080
1039EXT1 | EXTERIOR FINISHES | 1039 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2- 3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3080
1040ADA3 | ADA PARKING SPACE | 1040 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area and passenger loading area are necessary to comply with ADA requirements. This project would provide for a concrete van accessible ADA parking and loading space and walkway to the existing sidewalk. This will require regrading, installing P.C. concrete, striping, signage and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 30000
1036STR1 | STRUCTURAL RETROFIT | 1036 | The timber framing supporting the roof is beginning to fail. The timbers have dried out, cracked, and broken in some areas. The roof material is already falling through in some areas. This project would provide for removing and replacing the timber construction. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #1 - CCC | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 180 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 3600
1037INT1 | INTERIOR FINISHES | 1037 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CAMPGROUND STORAGE | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 117 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1170
1059EXT2 | HANDRAIL & CONCRETE LANDING INSTALLATION | 1059 | The entry deck and stairs/ landing do not meet current code. This project would provide for a guardrail around the deck, guardrail and handrail at the stairs and a 4" thick concrete landing at the bottom of the stairs. The 2012 IBC Chapter 10, Section's 1009.4, 1012 and 1013 were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | PARK RESIDENCE | 9947 | CNR | Parks |  | Cathedral Gorge | 1990 | 910 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0273HVA1 | ELECTRIC HEATER REPLACEMENT | 0273 | There are six electric heaters in the building that have reached the end of their expected life. This project recommends replacing the electric heaters. The estimate includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1040EXT2 | OVERHEAD DOOR REPLACEMENT | 1040 | There are two 10'x12' overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0273EXT1 | EXTERIOR FINISHES | 0273 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0273PLM1 | WATER HEATER REPLACEMENT | 0273 | The average life span of a water heater is eight to ten years. The two existing 10 gallon propane fired water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of two new 10 gallon propane fired water heaters. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0273SFT1 | EXIT SIGN UPGRADE | 0273 | The existing exit signs in this building are older types and should be replaced with new self-illuminated or LED style signs with battery-backed internal systems. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 900
9947SIT1 | SLURRY SEAL ASPHALT PAVING | 9947 | It is important to maintain the asphalt cement paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 172,500 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CATHEDRAL GORGE STATE PARK SITE | 9947 | CNR | Parks |  | Cathedral Gorge |  |  | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 129375
0273ADA3 | ADA DOOR HARDWARE | 0273 | The two exterior entrance doors are on an accessible path of travel, but the door hardware and threshold are not compliant. This project would provide for ADA compliant door hardware and threshold on the exterior door. ADA complaint signage is also included in this project. ADAAG Guidelines - 2010 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2800
9947EXT1 | EXTERIOR FINISHES, SHADE RAMADAS | 9947 | There are 28 steel shade ramadas in different locations throughout the site which are 151 s.f. each for a total of 4,228 square feet. It is important to maintain the finish, weather resistance and appearance of the structures. This project would provide for painting of the structures and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structures. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CATHEDRAL GORGE STATE PARK SITE | 9947 | CNR | Parks |  | Cathedral Gorge |  |  | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 8456
0273SIT1 | CONCRETE REPLACEMENT | 0273 | The concrete patio at the entrance to the building does not drain properly and is showing signs of failure. It is important to maintain positive drainage away from the building to protect it from moisture penetration. The existing concrete is also settling and cracking and should be scheduled for replacement. This project would provide for replacing approximately 1,500 square feet of concrete including removal and disposal of the existing concrete. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0273ADA2 | ADA SIGNAGE | 0273 | The building is lacking ADA signage. ADA regulations pertaining to building access, route of travel and restrooms have established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. ADAAG Guidelines - 2010 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2000
1039INT2 | JANITORS CLOSET REPAIRS | 1039 | The mop sink in the Janitors Closet has several cracks in the concrete and is leaking. This could lead to mold growth if not addressed. This project would provide for a new fiberglass mop sink and FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
1043ADA1 | GROUP USE AREA IMPROVEMENTS | 1043 | The group use area is not ADA compliant. This area should be scheduled for improvements. Currently, the picnic tables under the Group Ramada #1 are not ADA complaint. 5% of the picnic tables are required to be in compliance per IBC 2012 and ICC ANSI-A117.1-2009. This project would provide for the purchase and installation of 1 new ADA accessible picnic table. | GROUP RAMADA #1 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1000
1053EXT2 | HISTORIC BUILDING MAINTENANCE | 1053 | The wood structure is over 82 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, replacing wood roof shingles as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MILLER'S POINT CCC RAMADA | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 306 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4590
1040HVA1 | HVAC EQUIPMENT REPLACEMENT | 1040 | The HVAC systems are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. The R-22 refrigerant in the cooling systems are no longer EPA complaint and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC systems and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC systems and all required connections to utilities. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
1040SFT2 | EXIT SIGN AND EGRESS LIGHTING | 1040 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
1040SFT3 | SAFETY CABINETS | 1040 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide for two self-closing hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 10000
1040SFT4 | BATTERY STORAGE | 1040 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2012 IFC. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 25000
1040PLM1 | WATER HEATER REPLACEMENT | 1040 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2200
1039ENR1 | LIGHTING UPGRADE | 1039 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2464
1039EXT2 | ROOF REPLACEMENT | 1039 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | COMFORT STATION #4 - CAMPGROUND | 9947 | CNR | Parks |  | Cathedral Gorge | 1971 | 308 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4520
1042EXT2 | HISTORIC BUILDING MAINTENANCE | 1042 | The wood structure is over 82 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, replacing wood roof shingles as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CCC RAMADA | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 595 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8925
1036EXT2 | HISTORIC BUILDING MAINTENANCE | 1036 | The wood structure is over 82 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance time to display the artifacts and maintain the signage. This project would provide for sealing the wood, replacing wood roof shingles as needed and maintaining the exhibit in a state of arrested decay. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION #1 - CCC | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 180 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8925
0273HVA2 | HVAC EQUIPMENT REPLACEMENT | 0273 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA complaint and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0273HVA3 | AIR CONDITIONER INSTALLATION | 0273 | The theater room is not sufficiently cooled by the existing HVAC system. It is recommended to install an air conditioning system in the theater room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0273ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0273 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2000
0273ADA4 | ADA ACCESSIBLE COUNTER | 0273 | The plastic laminate countertop in the gift shop is not ADA compliant. This project would provide funding for the removal of the existing countertop and installation of a new plastic laminate countertop. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 12750
0273SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0273 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 9000
0273HVA4 | EXHAUST FAN REPLACEMENT | 0273 | Many of the exhaust fans in the restrooms and shower areas were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | REGIONAL INFORMATION CENTER | 9947 | CNR | Parks |  | Cathedral Gorge | 1996 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
1040EXT3 | WINDOW REPLACEMENT | 1040 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1060SIT1 | SITE BOLLARDS | 1060 | The Park Residence utilizes a propane tank for the home. The above ground propane tank requires bollards for protection from vehicle impact per IFC 2012. This project would provide for the purchase and installation of 6 - 8" concrete filled steel bollards to protect the propane tank. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2941ENR1 | LIGHTING UPGRADE | 2941 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | RESIDENCE SHED #5 | 9947 | CNR | Parks |  | Cathedral Gorge | 2004 | 280 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3360
2939ADA1 | ADA RESTROOM UPGRADE | 2939 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 15000
2939ENV1 | DUST COLLECTION SYSTEM REPLACEMENT | 2939 | The building has a woodshop which has an inoperative dust collection system. The existing exhaust fan is undersized for the equipment being used. This project recommends the replacement of the dust collection system with a higher capacity system, including the fan, motor and ducting to each piece of equipment. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 20000
2939EXT2 | EXTERIOR DOOR REPLACEMENT | 2939 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the south double door assembly and the north single door assembly with new metal doors, frames and hardware. The removal and disposal of the existing doors is included in this estimate. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2939SIT1 | SITE DRAINAGE UPGRADES | 2939 | The grade does not slope away effectively from the buildings. This allows water to pool against the foundation. In the winter months, the water freezes against the foundation, and over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading that the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2936PLM1 | WATER HEATER REPLACEMENT | 2936 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. The removal and disposal of the existing equipment is included in this estimate. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2936ENR1 | LIGHTING UPGRADE | 2936 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8192
1060EXT2 | ROOF REPLACEMENT | 1060 | The standing seam metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13650
2936INT2 | JANITORS CLOSET REPAIRS | 2936 | The mop sink in the plumbing chase is mounted adjacent to CMU walls and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1040ADA4 | BREAK ROOM REMODEL | 1040 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes the removal and the disposal of the existing materials. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 15000
1060INT1 | FLOORING REPLACEMENT | 1060 | The linoleum and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for the removal and the disposal of the existing flooring and the installation of new linoleum with a 6"cove base and a heavy duty commercial grade carpet. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7280
9947EXT3 | EXTERIOR HANDRAIL REPLACEMENT | 9947 | At the Miller Point Overlook, there are no sidewalks or handrails. This is creating a safety hazard due to erosion. This project recommends for the installation of erosion control, new handrails, sidewalks, ramps and for the proper returns and supports to be installed. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CATHEDRAL GORGE STATE PARK SITE | 9947 | CNR | Parks |  | Cathedral Gorge |  |  | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500000
1060SIT2 | SITE DRAINAGE UPGRADES | 1060 | The grade does not slope away effectively from the buildings. This allows water to pool against the skirting. In the winter months, as the water freezes against the skirting, and over time, this can cause damage. It is recommended per IBC 1804.3 Site Grading that the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2939EXT1 | EXTERIOR FINISHES | 2939 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1059EXT1 | EXTERIOR FINISHES | 1059 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing, painting, staining or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | PARK RESIDENCE | 9947 | CNR | Parks |  | Cathedral Gorge | 1990 | 910 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9100
1059INT1 | INTERIOR FINISHES | 1059 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 4-5 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | PARK RESIDENCE | 9947 | CNR | Parks |  | Cathedral Gorge | 1990 | 910 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 9910
1057EXT1 | DEMOLISH BUILDING | 1057 | The metal storage shed is in extremely poor condition and the roof is damaged. This project would provide for the demolition of the structure including debris removal. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | METAL STORAGE SHED #4 | 9947 | CNR | Parks |  | Cathedral Gorge | 1980 | 261 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1040ADA1 | ADA RESTROOM UPGRADE | 1040 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 40000
1040INT1 | INTERIOR FINISHES | 1040 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 44000
1040EXT1 | EXTERIOR FINISHES | 1040 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | MAINTENANCE OFFICE/ SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 1976 | 4400 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 44000
1043EXT1 | EXTERIOR FINISHES | 1043 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting or staining of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | GROUP RAMADA #1 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6800
1054EXT1 | EXTERIOR FINISHES | 1054 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing and caulking around, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | METAL STORAGE SHED #1 | 9947 | CNR | Parks |  | Cathedral Gorge | 1982 | 266 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2660
1055EXT1 | EXTERIOR FINISHES | 1055 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD STORAGE SHED #2 | 9947 | CNR | Parks |  | Cathedral Gorge | 1983 | 102 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5100
1056EXT1 | EXTERIOR FINISHES | 1056 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. Due to the current condition of the exterior, it is recommended that this project be implemented immediately and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD STORAGE SHED #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1964 | 147 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1470
1056EXT2 | ROOF REPLACEMENT | 1056 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayment. This estimate includes removal and disposal of the old roofing. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD STORAGE SHED #3 | 9947 | CNR | Parks |  | Cathedral Gorge | 1964 | 147 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2205
1044EXT1 | EXTERIOR FINISHES | 1044 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting or staining of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | GROUP RAMADA #2 | 9947 | CNR | Parks |  | Cathedral Gorge | 1962 | 680 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6800
2256EXT1 | EXTERIOR/ INTERIOR FINISHES | 2256 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended to seal and caulk the building in the next 2-3 years. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CCC DAY USE CXT COMFORT STATION | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 100 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2939ENR1 | LIGHTING UPGRADE | 2939 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
2936INT1 | INTERIOR FINISHES | 2936 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
1060EXT1 | EXTERIOR FINISHES | 1060 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | CCC WATER TOWER | 9947 | CNR | Parks |  | Cathedral Gorge | 1934 | 59 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2939INT1 | INTERIOR FINISHES | 2939 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and every 5-6 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | WOOD SHOP | 9947 | CNR | Parks |  | Cathedral Gorge | 2002 | 1200 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2941EXT1 | EXTERIOR FINISHES | 2941 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | RESIDENCE SHED #5 | 9947 | CNR | Parks |  | Cathedral Gorge | 2004 | 280 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2936EXT1 | EXTERIOR FINISHES | 2936 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | COMFORT STATION #5 - GROUP USE | 9947 | CNR | Parks |  | Cathedral Gorge | 2003 | 1024 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10240
2940EXT2 | ROOF REPLACEMENT | 2940 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a standing seam metal roofing system. This estimate includes the removal and the disposal of the old roof. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 6300
2940EXT3 | GARAGE DOOR REPLACEMENT | 2940 | The garage door is constructed of metal and is original to the building. It has deteriorated from weather exposure over time. It is recommended that a new garage door be installed. This estimate includes the removal and the disposal of the existing garage door. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2940SFT1 | EXTERIOR LANDING INSTALLATION | 2940 | Section R311.4.3 of the 2012 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. There are two doors that do not comply with this code and pose a safety hazard. This project would provide for the installation of compliant landings for each door. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2940EXT1 | EXTERIOR FINISHES | 2940 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof. This shall include sealing or other applied finishes, caulking around flashing, fixtures, and other penetrations to keep the building in a weather tight condition. It is recommended that this project be implemented in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/17/2008. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | NDOW STORAGE SHED | 9947 | Wildlife |  |  | Cathedral Gorge | 2004 | 420 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
0460EXT4 | WINDOW REPLACEMENT | 0460 | The window is original, single pane construction in metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the window with a dual pane, higher efficiency unit. This estimate is for the replacement of 1 unit. Removal and disposal of the existing window is included in this estimate. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
0465SIT1 | SITE DRAINAGE UPGRADES | 0465 | The grade does not slope away effectively from the building. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | BDSP PUMP HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1970 | 42 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0465EXT2 | ROOF REPLACEMENT | 0465 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roof. | BDSP PUMP HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1970 | 42 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 630
0460SFT1 | EXTERIOR LANDING INSTALLATION | 0460 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door; the exterior landing shall not exceed a 2% slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0466EXT2 | EXTERIOR FINISHES | 0466 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP SHADE RAMADA - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 310 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 3100
0460EXT3 | ROOF REPLACEMENT | 0460 | The asphalt roof on the building was in poor condition and had active leaks at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system. This will allow for the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
0506EXT2 | DEMOLISH STRUCTURE | 0506 | The building is an old storage shed that is no longer in use and is severely damaged. It is recommended that this structure be demolished and that the pit below to be filled-in, per the guidelines of the Nevada State Division of Environmental Protection and any local requirements. | BDSP STORAGE SHED | 9948 | CNR | Parks |  | Beaver Dam | 1995 | 192 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 500
2254EXT2 | EXTERIOR/ INTERIOR FINISHES | 2254 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP CXT TOILET #2 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1900
0997ELE1 | WIRING CLEANUP | 0997 | The wiring in the residence is disorganized and not in proper electrical boxes and cover plates. This creates a safety issue. This project would provide for electrical wiring to be placed in the proper boxes and cover plates to be installed per NEC 2011. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0997SFT2 | FLUE DISTANCES | 0997 | There is a water heater flue in the building that does not comply with UMC 2012 chapter 8, chimneys and vents. The flue is close to combustibles and does not have the proper clearances per UMC 2012. This is a fire hazard. It is recommended that the flue in the building meet the proper clearances per UMC 2012 and the manufacture’s specifications. The flue should be installed by a licensed contractor. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 2000
0997PLM1 | WATER HEATER REPLACEMENT | 0997 | There is a 40 gallon propane-fired water heater in the building. The average lifespan of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement immediately. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1750
0997ENV1 | PEST CONTROL | 0997 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2254ADA1 | ADA ACCESSIBLE PATH OF TRAVEL | 2254 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BDSP CXT TOILET #2 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 30000
2255SIT1 | PARKING LOT STRIPING | 2255 | It is important to maintain the striping on the pavement at the site. This project would provide for the necessary striping and painting of the curbs and parking spaces. An ADA parking and loading space emblem will be painted on the concrete that is designated for ADA parking. This project should be scheduled on a 2 year cyclical basis to maintain the integrity of the striping, painting and ADA designation. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BDSP ADA CXT TOILET #3 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2255EXT2 | EXTERIOR/ INTERIOR FINISHES | 2255 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP ADA CXT TOILET #3 - LOOP B | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1900
2253EXT2 | EXTERIOR/ INTERIOR FINISHES | 2253 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. Epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 4-5 years and for this project to be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP ADA CXT TOILET #1 - LOOP A | 9948 | CNR | Parks |  | Beaver Dam | 2002 | 95 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 1900
0997ENR2 | LIGHTING UPGRADE | 0997 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4704
0459EXT1 | COMFORT STATION REPLACEMENT | 0459 | The Out House was built in 1964 and has not been in use for over 12 years. The building is dilapidated and deteriorating and has reached the end of its useful life. It has also been identified by State Health as problematic due to the infiltration of human waste into the local sub soils and ultimately, the local water table. This project would provide funding for the demolition of the building and replacement with a new CXT unit. The estimate includes hazardous waste remediation in compliance with all local, state and federal health codes. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP OUT HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 140 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0997SFT1 | SMOKE CARBON MONOXIDE ALARM | 0997 | IRC 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012 requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 500
3085EXT1 | EXTERIOR FINISHES | 3085 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP SPRING HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1996 | 72 | 2017-04-05 | Four to Ten Years | Long-Term Needs | 3 | 360
9948ADA1 | ADA PARKING SPACE AND PATH OF TRAVEL | 9948 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BEAVER DAM STATE PARK SITE | 9948 | CNR | Parks |  | Beaver Dam |  |  | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0997ENR1 | WINDOW REPLACEMENT | 0997 | Some of the windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9948SFT1 | BRIDGE GUARDRAIL REPLACEMENT | 9948 | The park has an interpretive trail that crosses over the creek by a bridge. The guardrail for the bridge does not meet current code. Section 1013.3 of the 2012 IBC states that open guardrails shall have balusters or ornamental patterns such that a 4-inch-diameter (102 mm) sphere cannot pass through any opening up to a height of 34 inches (864 mm). This project would provide for the installation of a compliant guardrail for the bridge from a height of 34 inches (864 mm) to 42 inches (1067 mm) above the adjacent walking surfaces. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BEAVER DAM STATE PARK SITE | 9948 | CNR | Parks |  | Beaver Dam |  |  | 2017-04-05 | Immediate to Two Years | Currently Critical | 1 | 1000
0460EXT1 | EXTERIOR FINISHES | 0460 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the concrete masonry unit walls, painting the wood siding and eaves and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed, painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
0460EXT2 | EXTERIOR DOOR REPLACEMENT | 0460 | The exterior metal door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP GENERATOR BUILDING | 9948 | CNR | Parks |  | Beaver Dam | 1980 | 64 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0997CUL1 | KITCHEN REMODEL | 0997 | At the time of the survey the kitchen was in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, countertops, fixtures and equipment with mid-range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
0465EXT1 | EXTERIOR FINISHES | 0465 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the wood framing and eaves and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PUMP HOUSE | 9948 | CNR | Parks |  | Beaver Dam | 1970 | 42 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 420
0997EXT1 | EXTERIOR FINISHES | 0997 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
0997INT1 | INTERIOR FINISHES | 0997 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | BDSP PARK RESIDENCE | 9948 | CNR | Parks |  | Beaver Dam | 1964 | 588 | 2017-04-05 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
0863EXT2 | ROOF REPLACEMENT | 0863 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes the removal and the disposal of the old roof. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36000
0863ENR3 | LIGHTING UPGRADE | 0863 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19200
0863EXT4 | OVERHEAD DOOR REPLACEMENT | 0863 | There is a 10'x12' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0863ENV1 | BREAK ROOM REMODEL | 0863 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and counter tops are delaminating and failing. This project recommends the replacement of the existing kitchen counters, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. This estimate includes disposal of the existing materials. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
0863PLM1 | WATER HEATER REPLACEMENT | 0863 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended to replace water heater with an on-demand propane-fired water heater. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0863INT2 | INTERIOR FINISHES | 0863 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0863ENR2 | HVAC EQUIPMENT REPLACEMENT | 0863 | The existing HVAC equipment consists of isolated evaporative coolers and space heaters. They do not condition the spaces adequately, are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of a gas-fired packaged unit and ducting to upgrade the existing system. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0863SFT4 | EXTERIOR LANDING UPGRADE | 0863 | There are two out-swinging exterior doors which swing out over a step and do not have a landing that comply with IBC 2012. IBC Section 1008 requires that landings not be more than 1/2" below the threshold. This project would provide for the installation of two compliant landings for the doors. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 10000
0863EXT1 | EXTERIOR FINISHES | 0863 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
0863SFT2 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0863 | This building is B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 33600
0863ENR1 | WINDOW REPLACEMENT | 0863 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0863ADA1 | ADA RESTROOM UPGRADE | 0863 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
0863ADA2 | ADA SIGNAGE | 0863 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 2500
0863ADA3 | ADA PARKING AND PATH OF TRAVEL | 0863 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP NDF OFFICE | 9949 | CNR | Forestry |  | Pioche | 1987 | 2400 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
2209SFT1 | SAFETY CABINETS | 2209 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 5000
1364EXT3 | EXTERIOR SIDING REPLACEMENT | 1364 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. This estimate is based on 700 linear feet of 4' wide panels at $17.00 per linear foot. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11900
1366SFT1 | EXTERIOR LANDING INSTALLATION | 1366 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing that complies with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | WALK-IN COOLER STORAGE | 9949 | Correct | PCC |  | Pioche | 1980 | 480 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
1366EXT2 | EXTERIOR FINISHES | 1366 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WALK-IN COOLER STORAGE | 9949 | Correct | PCC |  | Pioche | 1980 | 480 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 4800
2209ELE1 | WIRING CLEANUP | 2209 | The wiring in the building is disorganized and not in proper electrical boxes. This creates a safety issue when making repairs or upgrades. This project would provide for cleanup and labeling of the wiring. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2210INT3 | FLOORING REPLACEMENT | 2210 | The floor coverings throughout this building are in generally poor condition and have reached the end of their serviceable lives. At the present time, most of the floor surfaces have been removed in the cafeteria and culinary area. This presents health and sanitation issues. The remaining floor covering has 12" VCT floor covering. This project would provide funding to replace the entire floor with non-slip sheet vinyl, and includes removing and installing the Culinary preparation and cooking equipment, tables and chairs. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 159021
2209ENR1 | LIGHTING UPGRADE | 2209 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 512
1364EXT4 | EXTERIOR DOOR REPLACEMENT | 1364 | The existing exterior metal doors and frames are original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of two new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1355EXT2 | ROOF REPLACEMENT | 1355 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes the removal and the disposal of the old roof. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10800
2210CUL1 | CULINARY EQUIPMENT REPLACEMENT | 2210 | The kitchen cooking equipment is original to the building and has reached the end of its useful life. It is recommended that the equipment be scheduled for replacement in the next 2-3 years, including ovens and hoods, grills, sinks and dishwashers. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
2210HVA5 | HVAC EQUIPMENT REPLACEMENT | 2210 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA complaint and it's production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2209SFT2 | PROPANE TANK RELOCATION | 2209 | There are above ground propane storage tanks stored next to the building. According to Table 3504.2.1 of the 2012 International Fire Code, flammable gases must be stored at least 5 feet away from a building of non-rated construction. This project would provide for relocating the propane storage tanks to comply with the code. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3500
1364SFT5 | EXTERIOR LANDING INSTALLATION | 1364 | There are two out-swinging exterior doors on the building, which swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1, which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
1364SFT6 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 1364 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 7000
1364ENR2 | LIGHTING UPGRADE | 1364 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1364INT5 | DRYER REPLACEMENT | 1364 | The commercial tumbler dryer in the laundry area is original to the building and is troublesome and problematic to operate. Considering the age of the machine and the evolving needs of the facility it is recommended to replace it. This project provides for the removal and disposal of the existing tumbler dryer and would replace it with a new unit. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1355ENR1 | LIGHTING UPGRADE | 1355 | The existing lighting fixtures are the older High Pressure Sodium, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5760
1355SFT1 | SAFETY CABINETS | 1355 | The building contains many different paints, stains, and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 5000
9949PLM1 | SEWER SYSTEM REPLACEMENT | 9949 | The sanitary wastewater system and the lift station are showing signs of deterioration and the system is not working to its full potential. The sewer and leach field lines are original to the site and are in poor condition. Deposits within the pipes are causing them to be restricted, which is slowing the flow of water. The passage of time and constant heavy use are contributing factors to problems that arise. This project would provide for the complete replacement of the sanitary sewer system and the lift station. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 2500000
2210ADA5 | ADA TABLE UPGRADE | 2210 | Per the USAB Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 4 of the fixed seats, which will allow access for four wheel chairs. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 4000
1364INT4 | WASHING MACHINE REPLACEMENT | 1364 | The two existing commercial washing machines appear to have reached the end of their useful life. They show signs of age, and are constantly breaking down. This project would provide funding for the purchase and installation of two new 60lb. commercial washing machine units. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
2211INT3 | INTERIOR FINISHES | 2211 | The interior finishes are in fair condition. Some walls are covered by a fabric wall covering and some have been painted. It is recommended that the painted walls and ceilings be re-painted at least once in the next 4-5 years. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
9949ENR1 | EXTERIOR LIGHTING REPLACEMENT | 9949 | The 13 perimeter light poles that surround the site have a total of 52 light fixtures. These light fixtures are metal halide and are not energy efficient. This project would provide for the replacement of the exterior light fixtures with new LED light fixtures and will utilize the existing wiring. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19500
2212EXT2 | EXTERIOR FINISHES | 2212 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
2212INT3 | INTERIOR FINISHES | 2212 | The interior finishes are in fair condition. Some walls are covered by a fabric wall covering and some have been painted. It is recommended that the painted walls and ceilings be re-painted at least once in the next 4-5 years. This project should be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
2212EXT3 | ROOF REPLACEMENT | 2212 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14700
2212HVA1 | HEATER REPLACEMENT | 2212 | The heating system was installed in 1995. It consists of propane gas-fired furnaces. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of new heating systems and cleaning of the existing duct work and grilles. The new systems shall be designed to significantly reduce electrical and propane usage in order to comply with the 2012 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes the removal and disposal of the existing heating units and all required connections to the utilities. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2212HVA2 | EVAPORATIVE COOLER REPLACEMENT | 2212 | There are two evaporative coolers mounted on the roof of the housing unit. They are severely scaled and have reached the end of their serviceable life. This project would provide for two new evaporative coolers to be installed, and will include the removal and disposal of the old evaporative coolers and the utility connections to the new units. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2212EXT4 | WOOD SKIRTING REPLACEMENT | 2212 | The skirting on the modular building is made of T1-11 and was in poor condition at the time of the survey. IBC 2012, Section 2304.11.2.6, wood siding clearance between wood siding and earth on the exterior of a building shall not be less than 6 inches (152 mm) or less than 2 inches (51mm) vertical from concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood. This project would provide for the removal of the T1-11 skirting and the installation of new vinyl skirting. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2212ENR2 | LIGHTING UPGRADE | 2212 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7840
2212ELE1 | WIRING CLEANUP | 2212 | The wiring in the housing unit is disorganized and not in proper electrical boxes. This creates a safety issue. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9949SIT2 | SITE DRAINAGE IMPROVEMENTS | 9949 | The grade does not slope away effectively from the buildings. This allows water to pool against the foundation. In the winter months, the water freezes against the foundation, and over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading that the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 4-10 years. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 5000
2211EXT2 | EXTERIOR FINISHES | 2211 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 9800
2210ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2210 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2211EXT3 | ROOF REPLACEMENT | 2211 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14700
2211HVA1 | HEATER REPLACEMENT | 2211 | The heating system was installed in 1995. It consists of propane gas-fired furnaces. The system is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new heating system and the cleaning of the existing duct work and grilles. The new system shall be designed to significantly reduce electrical and propane usage in order to comply with the 2012 IECC and ASHRAE 90.1 and to reduce utility costs. This project includes the removal and disposal of the existing heating units and all required connections to utilities. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2211HVA2 | EVAPORATIVE COOLER REPLACEMENT | 2211 | There are two evaporative coolers mounted on the roof of the housing unit. They are severely scaled and have reached the end of their serviceable life. This project would provide for two new evaporative coolers to be installed, and includes the removal and disposal of the old evaporative coolers and utility connections to the new units. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2211EXT4 | WOOD SKIRTING REPLACEMENT | 2211 | The skirting on the modular building is made of T1-11 and was in poor condition at the time of the survey. IBC 2012, Section 2304.11.2.6, wood siding clearance between wood siding and earth on the exterior of a building shall not be less than 6 inches (152 mm) or less than 2 inches (51mm) vertical from concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood. This project would provide for the removal of the T1-11 skirting and the installation of new vinyl skirting. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2211ENR2 | LIGHTING UPGRADE | 2211 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7840
2211ELE1 | WIRING CLEANUP | 2211 | The wiring in the housing unit is disorganized and not in proper electrical boxes. This creates a safety issue. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2211PLM1 | WATER HEATER REPLACEMENT | 2211 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
2211SFT5 | FLUE REPAIRS | 2211 | The flue vent in the building does not comply with UMC 2012 chapter 8, chimneys and vents. The flue vent was installed with an improper flue and per section 804 direct vent terminations vent terminals for direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vent is to close to combustibles, does not have the proper clearances and has a potential to leak CO. It is recommended that the furnace flue vent be replaced immediately. Replacements shall meet the manufacture’s specifications and UMC 2012. The flue vents should be installed by a licensed contractor. This project would provide funds to replace of the flue vent in the building. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 2000
2210HVA3 | BOILER REPLACEMENT | 2210 | The hot water boilers, controls and mixing valves servicing the building are original dating back to 1995. The life expectancy of these units is 20 to 25 years with proper maintenance and with a water treatment program in place. Replacement parts for performing routine and emergency maintenance are hard to find for this old equipment. This project would provide for the removal and the disposal of the existing boilers, controls and mixing valves and will replace with all new equipment. This estimate includes all required connections to utilities and equipment. The estimate is based on 505 MBH output hot water boilers. The existing chemical water treatment system will need to be tested and adjusted once equipment is operational. $2,000 is included in this estimate for testing of the chemical water treatment system. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 100000
2210HVA4 | AIR CONDITIONER INSTALLATION | 2210 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner and includes all required connections to existing utilities. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2212PLM1 | WATER HEATER REPLACEMENT | 2212 | There is a 30 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, the water heater and the floor below the water heater are showing signs of wear and deterioration. It is recommended that the floor be replaced and a new propane-fired water heater be installed immediately. Removal and disposal of the existing equipment is included in this estimate. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 1750
2211SFT1 | EXTERIOR LANDING UPGRADES | 2211 | Chapter 10 of the 2012 IBC describes the requirements for doors including floor elevations, landings and handrails. The floor or landing shall be at the same elevation on each side of the door. The exterior landing shall not exceed a 2-percent slope and a length measured in the direction of travel of not less than 44 inches. Stairways shall have handrails on each side of the stairs. The landing and stairway at both exterior doors do not comply with this code and pose a safety hazard. This project would provide for the installation of two compliant landings and handrails for each door. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 10000
1355EXT1 | EXTERIOR FINISHES | 1355 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MAINTENANCE SHOP | 9949 | Correct | PCC |  | Pioche | 1980 | 720 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
1364ADA2 | ADA SIGNAGE | 1364 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project will provide for compliant ADA signage. The 2012 IBC, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 1500
1364EXT2 | OVERHEAD DOOR REPLACEMENT | 1364 | There is a 16'x14' overhead coiling door which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a motorized door. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1364SFT4 | INTERIOR STAIR HANDRAIL REPLACEMENT | 1364 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railing is included in this estimate. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 5000
2210EXT2 | LOADING DOCK REPAIRS | 2210 | The loading dock behind the Culinary area is worn and damaged and in need of replacement. The concrete has heaved and has extensive cracks and the entire structure is pulling away from the building. This project will provide for the removal and the replacement of the concrete and the installation of new hardware for the truck guards. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
2209EXT2 | ROOF REPLACEMENT | 2209 | The asphalt composition shingle roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next year with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Four to Ten Years | Long-Term Needs | 3 | 960
1364INT2 | VCT FLOORING REPLACEMENT | 1364 | The VCT flooring in the chapel, laundry, library and on the stairs is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
1364ENR1 | HEATING EQUIPMENT REPLACEMENT | 1364 | The existing heating system consists of a ceiling mounted propane heater (30,000 - 50,000 BTU). The heaters are inefficient and should be replaced with a propane fired heater 80% AFUE or higher units. This project would provide for disposal of the existing units and replacement with a new propane fired units including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2209EXT1 | EXTERIOR FINISHES | 2209 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | GARDEN SHED | 9949 | Correct | PCC |  | Pioche | 1987 | 64 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
1364INT1 | INTERIOR FINISHES | 1364 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
2212SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2212 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 4900
2210PLM2 | EVAPORATIVE COOLER REPLACEMENT | 2210 | There are 13 evaporative coolers installed on the roof of this building. They are severely scaled and have reached the end of their useful and expected life. They do not have overflow drains and the excess water is damaging roof materials. This project would provide for new evaporative coolers to be installed, including all required connections to utilities. The estimate includes the removal and the disposal of the old coolers. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 52000
2212SFT1 | EXTERIOR LANDING UPGRADES | 2212 | Chapter 10 of the 2012 IBC describes the requirements for doors including floor elevations, landings and handrails. The floor or landing shall be at the same elevation on each side of the door. The exterior landing shall not exceed a 2-percent slope and a length measured in the direction of travel of not less than 44 inches. Stairways shall have handrails on each side of the stairs. The landing and stairway at both exterior doors do not comply with this code and pose a safety hazard. This project would provide for the installation of two compliant landings and handrails for each door. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 10000
2210PLM3 | WATER TREATMENT SYSTEM INSTALLATION | 2210 | The existing plumbing and HVAC systems are not equipped with a water treatment system. Failure to treat the water causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners / treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1364ADA1 | ADA RESTROOM REMODEL | 1364 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 15000
2210INT2 | JANITORS CLOSET REPAIRS | 2210 | The mop sink in one of the Janitors Closets is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1364SFT3 | OCCUPANCY SEPARATION UPGRADE | 1364 | The multipurpose building serves as a H-4 garage on one side (approximately 2600 s.f.) with office space and mezzanine storage above. A gymnasium, chapel, library and laundry is located on the other side. Per table 508.3.3 of the 2012 IBC, a 3 hour occupancy separation is required between the H-4 garage and the A-3 gymnasium. This will require demolition and new construction between the two portions of the building. his project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 25000
1364EXT1 | EXTERIOR FINISHES | 1364 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations and removing and replacing rusted metal panels as needed. It is recommended that the building be caulked, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 70000
2210ADA1 | ADA SIGNAGE | 2210 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3000
9949ADA1 | ADA PARKING AND PATH OF TRAVEL | 9949 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 30000
2210ELE2 | ELECTRICAL UPGRADE | 2210 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. In the commissary and several of the office areas, the receptacles are at their limit. It is recommended that additional capacity be provided in the main core to meet the evolving demands of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 441725
2210EXT3 | ROOF REPLACEMENT | 2210 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes the removal and the disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 265035
1364SFT1 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 1364 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/11/2002 and 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | MULTI-PURPOSE/ SHOP | 9949 | Correct | PCC | Forestry | Pioche | 1987 | 7000 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 14000
2211SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2211 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 4900
9949SEC1 | FENCE UPGRADE | 9949 | The chain link perimeter fence is currently 7 feet high. For security purposes the staff has requested to raise the fence to 12 feet high. This project would provide for adding 5 feet of fencing and razor wire to the existing perimeter fence. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PIOCHE CONSERVATION CAMP SITE | 9949 | Correct | PCC |  | Pioche | 1980 | 0 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
2210ADA3 | ADA RESTROOM UPGRADE | 2210 | The building does not have accessible restrooms. The existing restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | HOUSING ABC/ CULINARY UNIT | 9949 | Correct | PCC |  | Pioche | 1995 | 17669 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 160000
2212SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2212 | This building does not have an automatic fire suppression system and should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 13720
2212SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2212 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3920
2211SFT3 | FIRE ALARM SYSTEM INSTALLATION | 2211 | This building is lacking fire detection and an alarm system. It is recommended that fire detection and an alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 3920
2212ENR1 | WINDOW REPLACEMENT | 2212 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2211ENR1 | WINDOW REPLACEMENT | 2211 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 4 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2211INT2 | RESTROOM REMODEL | 2211 | The restroom in the building is dated and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2211SFT4 | FIRE SUPPRESSION SYSTEM INSTALLATION | 2211 | This building does not have an automatic fire suppression system. It should be retrofitted with fire sprinklers during the next remodel or addition. This project would provide funding for the installation of fire sprinklers including backflow prevention devices. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT D | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Immediate to Two Years | Currently Critical | 1 | 13720
2212INT2 | ADA RESTROOM UPGRADE | 2212 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a unisex accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/02/2017. | PREFERRED HOUSING UNIT E | 9949 | Correct | PCC |  | Pioche | 1995 | 980 | 2017-03-02 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0212ENR1 | EXTERIOR ENERGY RETROFIT | 0212 | The building is constructed of CMU with no insulation. The windows are original to the building, and are of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0199ADA1 | ADA RESTROOM UPGRADE | 0199 | The men's and women's designated ADA restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
9950ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9950 | There are two pole lights in the parking lot that have reached the end of their expected life and are not energy efficient. This project would provide for the installation of 4 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. It may be feasible to use the two existing poles and only change out the heads. The estimate should be adjusted accordingly. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 26000
0199EXT2 | EXTERIOR FINISHES | 0199 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0199ADA2 | ADA ENTRY UPGRADES | 0199 | The ADA provides for accessibility to sites and services for people with physical limitations. At the threshold between the entrance door and the landing there is a large gap. The gap is large enough to compromise the compliance of the path of travel and should be altered. This project would provide for installing an extended threshold to cover the gap and bring the path of travel into compliance with the code. The 2012 IBC, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 500
0199ADA3 | ADA SIGNAGE | 0199 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0199PLM1 | WATER HEATER REPLACEMENT | 0199 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0211SFT4 | SPRINKLER PIPE ENCAPSULATION | 0211 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0199ENR2 | WINDOW REPLACEMENT | 0199 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0211ENR1 | EXTERIOR ENERGY RETROFIT | 0211 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0212SFT4 | SPRINKLER PIPE ENCAPSULATION | 0212 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0212EXT5 | EXTERIOR DOOR REPLACEMENT | 0212 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0212ADA2 | ADA RESTROOM UPGRADE | 0212 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0212ADA3 | ADA SIGNAGE | 0212 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0213SFT4 | SPRINKLER PIPE ENCAPSULATION | 0213 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0213EXT5 | EXTERIOR DOOR REPLACEMENT | 0213 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0213ADA2 | ADA RESTROOM UPGRADE | 0213 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0213ADA3 | ADA SIGNAGE | 0213 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0213ENR1 | EXTERIOR ENERGY RETROFIT | 0213 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0218ENR1 | EXTERIOR ENERGY RETROFIT | 0218 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0211EXT5 | EXTERIOR DOOR REPLACEMENT | 0211 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0292SFT1 | FLUE REPLACEMENT | 0292 | There is a flue vent in the building which does not comply with UMC 2012 chapter 8, chimneys and vents. The flue vent was installed with an improper flue and per section 804 direct vent terminations vent terminals direct vented appliances shall be installed in accordance with the manufacturer’s installation instructions. The flue vent is taped and does not allow for the proper air flow. It is recommended that the flue vent be replaced per UMC and the manufacturer’s instructions. This project would provide funding to replace the flue vent. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0218EXT3 | EXTERIOR FINISHES | 0218 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 41850
0219ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0219 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the stored materials blocking the working space. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 400
0215SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0215 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0216ADA3 | KITCHEN REMODEL | 0216 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility. The cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0216PLM4 | WATER HEATER REPLACEMENT | 0216 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0216EXT2 | EXTERIOR FINISHES | 0216 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0216SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0216 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0217ADA3 | ADA RESTROOM UPGRADE | 0217 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0217ADA2 | KITCHEN REMODEL | 0217 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation are inadequate for the high usage at this facility, but the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0217PLM4 | WATER HEATER REPLACEMENT | 0217 | There is a 50 gallon electric water heater in the building. The average lifespan of a water heater is eight to ten years. This unit was not installed correctly and was missing an element cover at the time of the survey. It is recommended that a new electric water heater, seismic straps, braided steel hoses, expansion tank, ball valve and a pan be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
9950SEC1 | SECURITY SYSTEM INSTALLATION | 9950 | The site does not have a security system. This project recommends motion detection, door switches, access control and related items be installed and interfaced with the fire alarm. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640430
0217SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0217 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0215ADA2 | KITCHEN REMODEL | 0215 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0218SIT1 | SITE DRAINAGE UPGRADES | 0218 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0218HVA3 | EXHAUST FAN REPLACEMENT | 0218 | The existing exhaust fans that serve the bathrooms are original equipment and are not providing adequate ventilation. This project would provide for the removal of the existing exhaust fan assemblies and the purchase and installation of two new exhaust fan assemblies including connections to utilities. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0218ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0218 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0218ELE1 | ELECTRICAL UPGRADE | 0218 | This building was constructed before the high demand for electrical services were needed for security systems, computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. The electrical panels and receptacles are at their limit. There are also problems with rusting conduits particularly underground conduits. As failures have happened, new conduits have been installed on the interior walls and some are not properly connected. It is recommended the entire system be upgraded to meet the evolving needs of the building and provide safe electrical distribution. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 104625
0218HVA2 | AIR CONDITIONER INSTALLATION | 0218 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0219PLM2 | WATER HEATER REPLACEMENT | 0219 | There is a 300 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next year. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0219ADA5 | ADA ACCESSIBLE COUNTER | 0219 | The ADA provides for accessibility to sites and services for people with physical limitations. The entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as a references for this project. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0219SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0219 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 11760
0219ELE3 | PANIC HARDWARE IN ELECTRICAL ROOMS | 0219 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed in 1962. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 1-2 years. The estimate is based on one door that requires panic hardware. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0219ELE2 | ELECTRICAL UPGRADE | 0219 | This building was constructed before the high demand for electrical services were needed. As time has progressed, the building’s electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit and they do not comply with NEC 2011. It is recommended to have the entire system upgraded to meet the current standards. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 294000
0217EXT2 | EXTERIOR FINISHES | 0217 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0212SFT7 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0212 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2943ADA1 | ADA RESTROOM UPGRADE | 2943 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as references for this project. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0199ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0199 | This building contains two water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 8000
0199ENR4 | EXTERIOR LIGHTING REPLACEMENT | 0199 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0211ADA3 | KITCHEN REMODEL | 0211 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0211PLM5 | WATER HEATER REPLACEMENT | 0211 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0211EXT2 | EXTERIOR FINISHES | 0211 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0211SFT7 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0211 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0211ADA2 | ADA RESTROOM UPGRADE | 0211 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0212ADA4 | KITCHEN REMODEL | 0212 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0215EXT2 | EXTERIOR FINISHES | 0215 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0212EXT2 | EXTERIOR FINISHES | 0212 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0215PLM4 | WATER HEATER REPLACEMENT | 0215 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0213ADA4 | KITCHEN REMODEL | 0213 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0213PLM4 | WATER HEATER REPLACEMENT | 0213 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0213EXT2 | EXTERIOR FINISHES | 0213 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0213SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0213 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0214ADA3 | KITCHEN REMODEL | 0214 | The kitchen and associated cabinets in the kitchen area are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
0214PLM4 | WATER HEATER REPLACEMENT | 0214 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0214EXT2 | EXTERIOR FINISHES | 0214 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 4-5 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 45920
0214SFT6 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0214 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
0214ADA2 | ADA RESTROOM UPGRADE | 0214 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0292ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0292 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0212PLM4 | WATER HEATER REPLACEMENT | 0212 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2168INT2 | JANITORS CLOSET REPAIRS | 2168 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2001HVA2 | HVAC EQUIPMENT REPLACEMENT | 2001 | The HVAC roof top units were installed in 1994. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 550000
2001SFT3 | PANIC HARDWARE IN ELECTRICAL ROOMS | 2001 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required at the time the building was built in 1994, but is suggested in this report as an increased safety measure. It is recommended that this project be completed within 1-2 years. The estimate is based on one door that requires panic hardware. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2001EXT4 | EXTERIOR DOOR REPLACEMENT | 2001 | The existing exterior metal doors and frames appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the replacement and installation of eight new metal doors, frames and hardware. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 24000
2001EXT3 | OVERHEAD DOOR REPLACEMENT | 2001 | There is an 8'x8' overhead coiling door on the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling door and replacement with a new manually operated overhead coiling door. Removal and disposal of the existing door is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2001SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2001 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2001ADA3 | BREAK ROOM REMODEL | 2001 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 15000
2001PLM1 | WATER HEATER REPLACEMENT | 2001 | There is a 119 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is missing proper seismic bracing and an expansion tank. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2001SFT1 | EXTERIOR LANDING INSTALLATION | 2001 | There are two out-swinging exterior doors on the building. These doors swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2001SIT1 | SITE DRAINAGE UPGRADES | 2001 | The grade does not slope away effectively from the buildings. Water has pooled against the foundation. In the winter months, as the water freezes against the foundation, over time, this can cause damage to the foundation. It is recommended per IBC 1804.3 Site Grading the ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than one vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. This project would create a 5% slope away from the buildings. Additional drainage swales shall be installed, as needed. It is recommended that the grading be completed within 2-3 years. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2001ADA4 | ADA RESTROOM UPGRADE | 2001 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2166SFT1 | EXTERIOR LANDING INSTALLATION | 2166 | There are two out-swinging exterior doors on the building. These doors swing out over a step that does not have a landing. This does not comply with 2012 IBC Section 1008.1 which requires a proper landing and for the landing to not be more than 1/2" below the threshold. This project would provide for the installation of compliant landings. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2166EXT3 | ROOF REPLACEMENT | 2166 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1994. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2168SFT4 | OSHA COMPLIANT LADDER | 2168 | The ladder in the building was constructed in-house and does not comply with OSHA guidelines. This project recommends an OSHA compliant ladder per OSHA 1926.1053 for the interior of the building. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 800
2168ENR3 | LIGHTING UPGRADE | 2168 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 48000
2168ADA1 | ADA RESTROOM UPGRADE | 2168 | The men's and women's designated ADA restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
2943EXT2 | WINDOW REPLACEMENT | 2943 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 20 units. Removal and disposal of the existing windows is included in this estimate. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 30000
2943SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2943 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 6120
2943ENR2 | LIGHTING UPGRADE | 2943 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 24480
2943HVA1 | HVAC EQUIPMENT REPLACEMENT | 2943 | There are 2 packaged HVAC units that are original to the building and should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Four to Ten Years | Long-Term Needs | 3 | 40000
2943PLM1 | WATER HEATER REPLACEMENT | 2943 | There is a 20 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0220ENR4 | LIGHTING UPGRADE | 0220 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 12624
0215ADA3 | ADA RESTROOM UPGRADE | 0215 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
2166ELE2 | ELECTRICAL PANEL UNUSED OPENINGS | 2166 | The wiring in the electrical panel has missing breakers and needs to have blanks installed at the unused openings. Per NEC 408.7 Unused Openings. Unused openings for circuit breakers and switches shall be closed using identified closures, or other approved means that provide protection substantially equivalent to the wall of the enclosure. Unused openings create a safety issue during repairs or upgrades. This project would provide for blanks to be installed where the missing breakers are located. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250
0220PLM1 | WATER HEATER REPLACEMENT | 0220 | There are 3 on-demand propane-fired water heaters on the roof of the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that 3 new on-demand propane-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
0220HVA1 | HVAC EQUIPMENT REPAIRS | 0220 | There and two HVAC split systems that were installed in 2015. Both of the systems have ductwork, line sets, A/C condenser and heaters installed improperly. This project would provide for the proper installation of both HVAC split systems. This project includes removal and installation of the existing equipment and all required connections to utilities. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2166ELE1 | GFCI OUTLETS | 2166 | The existing receptacle on the outside of the building is a standard duplex receptacle. The 2011 NEC 210.8 requires these locations to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
0220INT3 | JANITORS CLOSET REPAIRS | 0220 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2001HVA3 | AIR CONDITIONER INSTALLATION | 2001 | The server room is not sufficiently cooled by the existing HVAC system. If the room is too warm, the computer equipment will prematurely age and may fail due to overheating. It is recommended to install an air conditioning system in the room to ensure that the temperature is properly regulated. This project would provide for the purchase and installation of an air conditioner including all required connections to existing utilities. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0221ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0221 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0221SFT4 | ANCHOR SHELVES | 0221 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1) All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a license engineer or architect. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0221PLM4 | WATER HEATER REPLACEMENT | 0221 | There are two 120 gallon electric water heaters in the building. The average lifespan of a water heater is eight to ten years. It is recommended that 2 new electric water heaters, seismic straps, braided steel hose, expansion tanks, ball valves and pans be installed within a year. Removal and disposal of the existing equipment is included in this estimate. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
0221INT4 | FLOORING REPLACEMENT | 0221 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 293040
0221ELE1 | WIRING CLEANUP | 0221 | The building has wiring that is disorganized and not in proper electrical boxes, particularly in the near the stage area. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0221ENR2 | LIGHTING UPGRADE | 0221 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 293040
0221CUL2 | CULINARY EQUIPMENT REPLACEMENT | 0221 | The kitchen equipment is original to the building and has reached the end of its useful life. It is recommended that the equipment be scheduled for replacement in the next 2-3 years, including the ovens and hoods, grills, sinks and dishwashers. This project provides for the removal and disposal of the existing equipment and replacement with new equipment. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0221INT3 | JANITORS CLOSET REPAIRS | 0221 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2001SFT4 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2001 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 110000
0292PLM4 | POOL EQUIPMENT REPLACEMENT | 0292 | The existing pool circulation pump, water filter, heater, chemical feeder, clocks and plumbing were in poor condition at the time of the survey. The pool equipment is beyond its useful life expectancy. This project would provide for the purchase and installation of new pool equipment and all required connections to utilities. This project would also provide for a chemical treatment program to include an updated chemical control system, service and employee training to be provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
2001HVA4 | EXHAUST FAN REPLACEMENT | 2001 | Many of the exhaust fans in the restrooms areas were inoperative and/or damaged at the time of the survey. Due to building code requirements, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
2001INT3 | SINK INSTALLATION | 2001 | The classroom that teaches silk screening does not have a sink or an area to clean up after the silk screening activities. This project recommends installing a new sink with plumbing for the use and cleanup of the silk screening functions. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0292EXT4 | EXTERIOR DOOR REPLACEMENT | 0292 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the south double door assembly and the north single door assembly with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0292SFT2 | SAFETY CABINETS | 0292 | The building contains pool chemicals and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0292SFT4 | HAZARDOUS COMMUNICATION PROGRAM | 0292 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness, and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2000
0292PLM3 | WATER HEATER REPLACEMENT | 0292 | There is a 75 gallon propane water heater in the building. The average lifespan of a water heater is eight to ten years. It is recommended that a new propane water heater, seismic straps, braided steel hose, expansion tank, ball valves, new flex gas line and pan be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0292SFT3 | HAZARDOUS MATERIALS STORAGE | 0292 | The building contains hazardous materials (i.e. pool chemicals). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 30000
2001EXT5 | WINDOW REPLACEMENT | 2001 | The windows are original, double pane construction in metal frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
3073EXT1 | EXTERIOR FINISHES | 3073 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GREENHOUSE STORAGE 2 | 9950 | HHS | DCFS | CYC | Caliente | 0 | 80 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
0215INT2 | INTERIOR FINISHES | 0215 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
2943INT1 | INTERIOR FINISHES | 2943 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30600
0219ENV1 | NONABSORBENT FINISHES | 0219 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of FRP or an equal material in all 8 restroom facilities to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 27000
0219SFT3 | FIRE ALARM SYSTEM UPGRADE | 0219 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. The current system is problematic and the duct detectors were rendered inoperative in a previous remodel. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 47040
2168ENR2 | HVAC EQUIPMENT UPGRADE | 2168 | The existing HVAC system consists of ceiling mounted electric heaters and does not have any cooling equipment. The electricity powered heaters are inefficient and should be replaced with propane fired heaters. There is a need for cooling equipment as well to provide a comfortable work environment in the summer. This project would provide for replacing the existing heaters with exterior ground mounted packaged units that provide propane fired heating as well as air conditioning. Propane gas service will be required and is included in the cost. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
3072EXT1 | EXTERIOR FINISHES | 3072 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GREENHOUSE STORAGE 1 | 9950 | HHS | DCFS | CYC | Caliente | 0 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
2168SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2168 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 6000
3074EXT1 | EXTERIOR FINISHES | 3074 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sealing the concrete masonry units, sanding, priming and painting the wood siding and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC WORK CREW STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 256 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2560
0214INT2 | INTERIOR FINISHES | 0214 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
3075EXT1 | EXTERIOR FINISHES | 3075 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC INDUSTRIAL ARTS STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 416 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4160
3075EXT2 | ROOF REPLACEMENT | 3075 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition shingle roof and new underlayment. This estimate includes removal and disposal of the old roof. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC INDUSTRIAL ARTS STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 416 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6240
3076EXT1 | EXTERIOR FINISHES | 3076 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3078EXT1 | EXTERIOR FINISHES | 3078 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3080EXT1 | EXTERIOR FINISHES | 3080 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
2943EXT1 | EXTERIOR FINISHES | 2943 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30600
2943ENR1 | OCCUPANCY SENSOR INSTALLATION | 2943 | There are no occupancy sensors installed in the restrooms to control lighting. It is recommended to install sensors in the Men's and Women's restrooms in order to reduce energy costs. This project provides for purchase and installation of 2 sensors. | CYC RECREATIONAL CENTER | 9950 | HHS | DCFS | CYC | Caliente | 2008 | 3060 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0218INT3 | INTERIOR FINISHES | 0218 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0220ENR3 | WINDOW REPLACEMENT | 0220 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 11 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16500
0220SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0220 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 22092
0199SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0199 | The building is a B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project also includes an allowance for 100 lineal feet of 4" water line, excavation and backfill, all fittings and an above ground backflow prevention device. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25200
9950ADA1 | ADA PATH OF TRAVEL UPGRADES | 9950 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. It is recommended that this project coincide with the paving project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0219ENR2 | EXTERIOR ENERGY RETROFIT | 0219 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 50 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 192600
0221HVA1 | HVAC SYSTEM UPGRADE | 0221 | The HVAC system consists of many roof mounted packaged units, boilers and evaporative coolers. They are not energy efficient and have reached the end of their expected and useful life. The air handlers are troublesome and require constant maintenance to remain in working condition. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles and any new ducting and associated work. The new system should be designed by a mechanical engineer who will determine the most economical and efficient way to upgrade the existing building. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2143624
0219EXT1 | EXTERIOR FINISHES | 0219 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. Also included is repairing and painting the wood fascia as needed. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 117600
0218ENR4 | HVAC EQUIPMENT REPLACEMENT | 0218 | The heat pump units and chiller piping are original to the building. They are located in the ceiling above the circular corridor. They have been problematic, have been leaking and have outdated R-22, which will be obsolete by January 1, 2020. The HVAC equipment should be scheduled for replacement within 2-3 years. This project would provide for the replacement of the equipment and cleaning of the existing duct work and grills. This project includes the removal and disposal of the existing equipment and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 62775
0220INT2 | INTERIOR FINISHES | 0220 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15780
0215SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0215 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4185
2168SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2168 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2009 Section 7 and the 2012 International Fire Code. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 24000
0214SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0214 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4185
0211SFT2 | EXIT SIGN & EGRESS LIGHTING UPGRADE | 0211 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
2168ENR1 | WINDOW REPLACEMENT | 2168 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2001ADA1 | ADA SIGNAGE | 2001 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0221ADA4 | ADA UPGRADES - STAGE | 0221 | The auditorium is lacking an accessible path to the stage. The stage is required to have an accessible path to it per the ADA regulations. This project would provide for an accessible ramp or powered lift to access the stage. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 7500
0219INT3 | INTERIOR FINISHES | 0219 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 117600
0220EXT1 | EXTERIOR FINISHES | 0220 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15780
0199INT1 | INTERIOR FINISHES | 0199 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MENTAL HEALTH BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 1800 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18000
0213INT3 | CABINET REPLACEMENT | 0213 | The sleeping rooms have a built-in desk, dresser and wardrobe closet for the students clothing and personal effects. They are constructed of chipboard and are of poor quality. Many are missing pulls and handles, have broken drawer faces and broken drawer slides. This project recommends replacing the existing units with heavy duty, institutional type desks and storage units constructed of metal or plywood with a washable surface. There are 18 built-in units and 2 portable units in the confinement rooms. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0215SFT4 | EXTERIOR LANDING | 0215 | The exterior landing at the secondary exit door is in need of replacement due to the door swinging out over a 7" step. The 2012 IBC Chapter 10 requires a flat landing no more than 1/2 inch below finish floor where the door swings out over the landing. This project would provide for a new concrete landing to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0218ADA4 | ADA RESTROOM UPGRADE | 0218 | The men's and women's designated ADA restrooms do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of two unisex accessible restrooms. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0212INT3 | CABINET REPLACEMENT | 0212 | The sleeping rooms have a built-in desk, dresser and wardrobe closet for the students clothing and personal effects. They are constructed of particle board and are of poor quality. Many are missing pulls and handles, have broken drawer faces and broken drawer slides. This project recommends replacing the existing units with heavy duty, institutional type desks and storage units constructed of metal or plywood with a washable surface. There are 18 built-in units and 2 portable units in the confinement rooms. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
9950SIT1 | CRACK FILL & SEAL ASPHALT PAVING | 9950 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 125,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156250
0292INT1 | INTERIOR FINISHES | 0292 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0217SFT4 | SPRINKLER PIPE ENCAPSULATION | 0217 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0218SFT3 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0218 | The building is an B occupancy per the 2012 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 or R-2 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. This project also includes an allowance for 100 lineal feet of 4" water line, excavation and backfill, all fittings and an above ground backflow prevention device. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 58590
0214SFT4 | EXTERIOR LANDING | 0214 | The exterior landing at the secondary exit door is in need of replacement due to the door swinging out over a 7" step. The 2012 IBC Chapter 10 requires a flat landing no more than 1/2 inch below finish floor where the door swings out over the landing. This project would provide for a new concrete landing to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0221INT2 | FLOORING REPLACEMENT | 0221 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. The gymnasium and concrete floors are excluded from the square footage. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
0221SFT3 | FIRE ALARM SYSTEM UPGRADE | 0221 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 146520
0221ADA3 | ADA SIGNAGE | 0221 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 8000
0220ADA4 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0220 | This building contains water fountains on each floor that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of four drinking fountains to meet the ADA requirements, two on each floor. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0220ADA3 | ADA SIGNAGE | 0220 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/ pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
0220SFT2 | FIRE ALARM SYSTEM UPGRADE | 0220 | This building is equipped with an automatic fire detection and alarm system that no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 6312
0292EXT2 | EXTERIOR FINISHES | 0292 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0292ADA1 | RESTROOM REMODEL | 0292 | The showers and restroom facilities are damaged from wear and tear, not operational and do not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the restrooms and constructing an accessible shower and restroom. These items may include a new shower stall, sink, toilet, hardware, mirrors, fixtures, flooring and paint. NRS 338.180, IBC 2012, ICC/ANSI A117.1 – 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0220ADA5 | INSTALL LEVER ACTION DOOR HARDWARE | 0220 | The existing door handles are round knob type and are not ADA compliant. This project would provide for the installation of new lever action door hardware on all doors in the facility. This estimate is for 15 units. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5250
0219PLM1 | PLUMBING VALVE REPLACEMENTS | 0219 | The majority of the plumbing isolation valves are gate valves that are original to the building. Most of these valves no longer completely stop water when closed. This project would provide for replacing the valves with new ball valves. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0218ENV1 | NONABSORBENT FINISHES | 0218 | 2012 IBC Section 1210 requires the installation of smooth, hard, nonabsorbent surfaces in the following restroom areas: on floors in toilet and bathing rooms that extend upward onto the walls at least 6 inches, within 2 feet of the sides of urinals and water closets to a height of 4 feet above the floor and in shower compartments to a height not less than 70 inches above the drain inlet. This project recommends the installation of FRP or an equal material to comply with this code section. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
0292ENR1 | LIGHTING UPGRADE | 0292 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC POOL HOUSE AND POOL | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
9950ENV1 | ASBESTOS SURVEY | 9950 | The Caliente Youth Center received a site-wide asbestos survey in 1988. The survey dealt only with friable asbestos issues. The dates and types of construction of the buildings indicate the possibility of other asbestos at the facility. The Asbestos Hazard Emergency Response Act requires that schools and any other facility used for the instruction or housing of students or for the administration of educational or research programs are inspected periodically for Asbestos Containing Materials. This project provides for an asbestos survey to be performed in accordance with the act. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 31500
0214EXT5 | EXTERIOR DOOR REPLACEMENT | 0214 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0214ENR1 | EXTERIOR ENERGY RETROFIT | 0214 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. | CYC HAMILTON DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0217ENR1 | EXTERIOR ENERGY RETROFIT | 0217 | The building is constructed of CMU with no insulation. The windows are original to the building, and are of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75920
3077EXT1 | EXTERIOR FINISHES | 3077 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC HAMILTON STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
0218PLM2 | WATER HEATER REPLACEMENT | 0218 | There is an older booster water heater in the building that appears to be original to the structure. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0216ADA2 | ADA RESTROOM UPGRADE | 0216 | The designated restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for construction of a new accessible restroom. These items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 25000
0221ADA5 | ADA ACCESSIBILITY IMPROVEMENTS | 0221 | The existing building is in need of an ADA accessibility upgrade. This project would provide for new lever action door hardware throughout, modifications to dining and serving tables and counters in the culinary and dining areas and modifications to the existing Men's and Women's restrooms which are used by the public during special events. The locker rooms in the Gym are also included in this estimate. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 100000
0220ADA1 | ADA RESTROOM UPGRADE | 0220 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC EVALUATION/ INFIRMARY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 1578 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0218ADA3 | ADA SIGNAGE | 0218 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC ADMINISTRATION | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
0211SFT6 | EXTERIOR LANDING | 0211 | The exterior landing at the secondary exit door is in need of replacement due to the door swinging out over a 7" step. The 2012 IBC Chapter 10 requires a flat landing no more than 1/2 inch below finish floor where the door swings out over the landing. This project would provide for a new concrete landing to be installed. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 1500
9950SFT2 | COMMUNICATIONS SYSTEM UPGRADE | 9950 | This facility is equipped with a communications system which has reached the end of its expected life. The telephone system has had numerous problems including a repeater that was destroyed in a windstorm in 2004. The emergency phones and intercom system have been inoperative since the early 1990's. The system provides paging and phone communications to classrooms and is an integral component of the notification and safety procedures for the classrooms. It is recommended that the entire communication systems be upgraded site wide. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2143624
0219ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 0219 | This building contains a water fountain. The 2012 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and installation of a new accessible fixed high/ low ADA drinking fountain. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 4000
0219ADA1 | ADA RESTROOM UPGRADE | 0219 | The building does not have an accessible restroom. The existing restroom does not meet the ADA requirements. A complete retrofit is necessary. This project would provide funding for remodeling the Men's and Women's restrooms per ADA regulations. Items may include a new sink, toilet, hardware, mirrors, fixtures, flooring and paint. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 40000
0219ADA4 | ADA SIGNAGE | 0219 | ADA regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with these criteria. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - OLD | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 11760 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 5000
0211INT3 | CABINET REPLACEMENT | 0211 | The sleeping rooms have a built-in desk, dresser and wardrobe closet for the students clothing and personal effects. They are constructed of particle board and are of poor quality. Many are missing pulls and handles, have broken drawer faces and broken drawer slides. This project recommends replacing the existing units with heavy duty, institutional type desks and storage units constructed of metal or plywood with a washable surface. There are 18 built-in units and 2 portable units in the sleeping rooms. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
2001ADA2 | ADA UPGRADES | 2001 | The building does not have a designated accessible office and the door handles are not compliant with the ADA. This project would provide for an accessible office area, path of travel throughout the building and ADA compliant lever action door hardware. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADAAG were used as references for this project. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2001INT2 | INTERIOR FINISHES | 2001 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 220000
0221EXT1 | EXTERIOR FINISHES | 0221 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the stucco and concrete masonry unit walls and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 366300
0221INT1 | INTERIOR FINISHES | 0221 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 366300
3079EXT1 | EXTERIOR FINISHES | 3079 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE STORAGE SHED | 9950 | HHS | DCFS | CYC | Caliente | 2010 | 96 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
0221PLM3 | WATER TREATMENT SYSTEM INSTALLATION | 0221 | The existing water softening/ treatment system in the building only serves the boiler for the Laundry and Culinary. The other boiler and the rest of the HVAC equipment should have a water treatment system as well. Failure to treat the water can cause wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softeners/ treatment systems to serve all of the mechanical and plumbing equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor for the HVAC systems. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0221CUL1 | ICE MACHINE REPLACEMENT | 0221 | There is an ice machine in the dining room. This unit is showing signs of wear including extensive leaks which are ruining the flooring and should be scheduled for replacement in the next 2-3 years. It is recommended that a new ice machine be purchased and installed. Removal and disposal of the existing machine is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MULTI-PURPOSE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1966 | 36630 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0290EXT1 | EXTERIOR FINISHES | 0290 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GARAGE/ STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2001ENR1 | LIGHTING UPGRADE | 2001 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 176000
0514EXT2 | DEMOLISH STRUCTURE | 0514 | The structure is built of steel posts and beams, a wood framed roof structure and a concrete slab-on-grade foundation. All of these structural elements are showing signs of failing and the structure should be removed. This project provides for the demolition of the structure, including the foundation and disposal of the materials. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC RAMADA | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 968 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 2500
2001EXT1 | EXTERIOR FINISHES | 2001 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. Repairs to the damaged EIFS on the south side of the building should be completed as soon as possible to prevent further damage to the structure. It is recommended that the building be painted and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC SCHOOL - NEW | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 22000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 220000
0216ENR1 | EXTERIOR ENERGY RETROFIT | 0216 | The building is constructed of CMU with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. This estimate is based on $10.00 per square foot for the EIFS plus $1,500.00 per window for a total of 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75920
9950PLM1 | REPLACE IRRIGATION WATER MAIN | 9950 | The grounds are irrigated via galvanized piping from the well. The piping is original to the site and is increasingly failing resulting in flooding. The age and type of the pipe makes it difficult to repair or replace. This project recommends replacing the existing water main with a Schedule 40 PVC or similar material, and the installation of a back-flow device to protect the well from cross contamination. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CALIENTE YOUTH CENTER SITE | 9950 | HHS | DCFS | CYC | Caliente | 1962 |  | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
2166EXT1 | EXTERIOR FINISHES | 2166 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is painting the concrete masonry unit walls and caulking of the vents, flashing, fixtures and all other penetrations. It is recommended that the building be painted and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2166INT1 | INTERIOR FINISHES | 2166 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2166EXT2 | EXTERIOR DOOR REPLACEMENT | 2166 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frame and hardware. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GENERATOR BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 1994 | 300 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2168EXT1 | EXTERIOR FINISHES | 2168 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
2168INT1 | INTERIOR FINISHES | 2168 | The interior finishes are in fair condition. About one quarter of the interior has finished gypsum board walls. It is recommended that the interior finished walls be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC MAINTENANCE BUILDING | 9950 | HHS | DCFS | CYC | Caliente | 2000 | 6000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 60000
0290EXT2 | EXTERIOR DOOR REPLACEMENT | 0290 | The exterior metal man door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC GARAGE/ STORAGE | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 2000 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0216INT2 | INTERIOR FINISHES | 0216 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45920
0216EXT5 | EXTERIOR DOOR REPLACEMENT | 0216 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame, hardware and paint. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
0216SFT4 | SPRINKLER PIPE ENCAPSULATION | 0216 | The sprinkler piping is hung from the ceiling of the dormitory and is exposed to the occupants. This creates a safety hazard in two ways. One is that the occupants could damage the piping and cause flooding in the building. The other is that the occupants can tie things around the pipes and cause harm to themselves. This project recommends encapsulating the piping with wallboard and texturing and painting to match the adjacent ceiling finishes. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC KIMBERLY DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Immediate to Two Years | Currently Critical | 1 | 3000
0215ENR3 | EXTERIOR ENERGY RETROFIT | 0215 | The building is constructed of CMU with no insulation. The windows are original to the building, and are of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an EIFS over the CMU and replacing the windows with new dual-pane, safety glazed windows. This estimate includes removal and disposal of the existing windows. The estimate is based on $10.00 per square foot for the EIFS plus $1500.00 per window for 20 windows. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 71850
0215EXT5 | EXTERIOR DOOR REPLACEMENT | 0215 | The exterior wood exit double doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the double door assembly with new metal doors, frames, hardware and paint. Removal and disposal of the existing doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC JARBIDGE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1964 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0213INT2 | INTERIOR FINISHES | 0213 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC CURRIE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0212INT2 | INTERIOR FINISHES | 0212 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC BEOWAWE DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0211INT1 | INTERIOR FINISHES | 0211 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC AURORA DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1962 | 4185 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 41850
0217INT2 | INTERIOR FINISHES | 0217 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 04/09/2002 and 09/21/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 03/01/2017. | CYC LINCOLN DORMITORY | 9950 | HHS | DCFS | CYC | Caliente | 1977 | 4592 | 2017-03-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45920
2208EXT1 | EXTERIOR FINISHES | 2208 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #4 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3520
2203INT1 | INTERIOR FINISHES | 2203 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM TICKET STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2204INT1 | INTERIOR FINISHES | 2204 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2201EXT1 | EXTERIOR FINISHES | 2201 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2202EXT1 | EXTERIOR FINISHES | 2202 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2203EXT1 | EXTERIOR FINISHES | 2203 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM TICKET STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2204EXT1 | EXTERIOR FINISHES | 2204 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 1440
2205EXT1 | EXTERIOR FINISHES | 2205 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #1 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3520
2202INT1 | INTERIOR FINISHES | 2202 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2207EXT1 | EXTERIOR FINISHES | 2207 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #3 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5120
0841EXT3 | EXTERIOR FINISHES | 0841 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. Special attention should be given to the flashing and seams on the south side of the building where large gaps are visible from inside the building. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Replacing all of the weather striping on the overhead coiling doors is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 36800
3039EXT1 | EXTERIOR FINISHES | 3039 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM TRAIN PAVILION | 9951 | CultAffr | M&H | Museums | Boulder City | 2007 | 11102 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 44408
9951SIT5 | CONCRETE PAVILION REPAIRS | 9951 | The exterior concrete sidewalks and platforms in the train pavilion are due for repairs. This project would provide for removing and replacing the expansion joints in the concrete and replacing the broken concrete curbing at the entrance to the parking lot. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
9951SFT1 | EXTERIOR SITE LIGHTING INSTALLATION | 9951 | The site has minimal site lighting in the public parking area and between the buildings which is a security and safety concern. This project will provide funding for the purchase and installation of 12 additional LED fixtures; 30’ light poles and 30" diameter raised concrete bases, electrical trenching, conduit, wiring, and required connections to the existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 112000
2206EXT1 | EXTERIOR FINISHES | 2206 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM SHADE STRUCTURE #2 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5120
2201INT1 | INTERIOR FINISHES | 2201 | The interior finishes are in fair condition. It is recommended that the interior walls and ceiling be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2204HVA1 | HVAC EQUIPMENT REPLACEMENT | 2204 | The building is heated and cooled by a wall-mounted combination unit. The average life span of this type of unit is fifteen years. This unit is original to the building and should be scheduled for replacement in the next 2-4 years. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 2000
2202HVA1 | HVAC EQUIPMENT REPLACEMENT | 2202 | The building is heated and cooled by a wall-mounted combination unit. The average life span of this type of unit is fifteen years. This unit is original to the building and should be scheduled for replacement in the next 5-6 years. This project includes removal and disposal of the existing HVAC unit and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 2000
2201PLM1 | WATER HEATER REPLACEMENT | 2201 | There is a 15 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0841INT1 | INTERIOR FINISHES | 0841 | The interior of the building is unfinished except for the office, the restrooms and portions of the metal shop area which together account for about 1,000 square feet of area. The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0841ADA2 | ADA UPGRADES | 0841 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
0841ENR1 | REPLACE INSULATION | 0841 | The walls and ceiling in the building have a layer of batt insulation installed that is not enclosed by a finish system. The insulation batts are deteriorating and large sections have fallen out of the walls and ceiling. The existing insulation is R-24 in the ceiling and R-15 in the walls. This project recommends replacing all of the insulation with a foil-backed R-30 batt insulation which will increase the energy efficiency of the building. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0841ENR2 | LIGHTING UPGRADE | 0841 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73600
0841HVA1 | RADIANT HEATER REPAIRS | 0841 | The building is heated by eight wall-mounted natural gas fired radiant heaters. Three of the heaters were not operating at the time of the survey and all eight should be scheduled for replacement. This project provides for the disposal of the existing radiant heaters and replacement with eight new gas fired radiant heaters including connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
0841SFT1 | EMERGENCY EYE WASH STATION REFURBISHMENT | 0841 | The emergency eye wash station is original to the building and the domestic water supply piping should be scheduled for replacement. The galvanized pipe is rusting on the inside and contaminating the water rendering the station useless. This project would provide for the removal of the existing piping and installation of new copper domestic water supply. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
0841SFT2 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0841 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 9200
0841SFT3 | FIRE SUPPRESSION SYSTEM MAINTENANCE | 0841 | The fire suppression system is a wet system and the corrosive water is causing damage. With each annual test, the corrosion is accelerated and has recently caused failures in some of the valves and pipes. The system is about 21 years old. It is recommended to perform a five year flush on the system with an inspection of the sprinkler heads at the cost of about $3,500. Should the inspection deem it necessary, a full flush and replacement of the heads would follow at the cost of about $6,500. The five year flush should be scheduled every five years thereafter to maximize the lifecycle of the system. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
9951SIT1 | SLURRY SEAL ASPHALT PAVING | 9951 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 32,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 40000
2201HVA1 | HVAC EQUIPMENT REPLACEMENT | 2201 | The building is heated and cooled by two wall-mounted combination units. The average life span of this type of unit is fifteen years. These units are original to the building and should be scheduled for replacement in the next 2-3 years. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/14/2016. | BOULDER CITY MUSEUM COMFORT STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Four to Ten Years | Long-Term Needs | 3 | 4000
0841EXT4 | OVERHEAD DOOR REPLACEMENT | 0841 | There are four overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
0841SFT4 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0841 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
0841HVA2 | EVAPORATIVE COOLER REPLACEMENT | 0841 | There are two evaporative coolers that at the time of the survey were not working. They are severely scaled and have reached the end of their serviceable life. This project would provide for two new evaporative coolers to be installed, and includes removal and disposal of the old evaporative coolers and utility connections to the new units. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 8000
0841PLM1 | WATER HEATER REPLACEMENT | 0841 | There is a 30 gallon gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0841HVA3 | HVAC EQUIPMENT REPLACEMENT | 0841 | The HVAC split system was installed in 1999. It is not energy efficient and has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC split system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing equipment and all required connections to utilities. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0841ELE2 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0841 | There is an electrical panel in the building which does not have the proper clear floor space surrounding it. The 2012 IFC Section 605.3 states that, a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the miscellaneous items blocking the working space. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 250
0841SFT5 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 0841 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 9000
0841SFT6 | SAFETY CABINETS | 0841 | The building contains many different paints, stains, and other hazardous products located on open shelves. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide a self-closing hazardous storage container in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0841ELE3 | RATED ELECTRICAL ROOM | 0841 | NFPA 13 requires a fire sprinkler in electrical rooms or if the electrical room complies within NFPA Section 5-13.11, which allows an exception to installing fire sprinklers in an electrical room, the electrical room shall meet all of the following requirements: the electrical room is dedicated to electrical equipment only; only dry-type electrical equipment is used; equipment is installed in a 2-hour fire rated enclosure including the floor and deck above and includes protection for penetrations; no combustible storage is permitted to be stored in the electrical room; any openings (doors) in the room must be properly fire rated at 90-minutes and must be self-closing and positive latching; any ventilation ductwork which penetrates the 2-hour barrier must be equipped with the appropriate fire dampers, and all penetrations must be properly fire stopped. This project would provide a 2 hour separation or a fire sprinkler to be installed in the electrical room per NFPA. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0841SFT7 | BACKFLOW PREVENTER REPLACEMENT | 0841 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 5000
0841SFT8 | EXTERIOR LANDING INSTALLATION | 0841 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the doors, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the doors on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of compliant landings for both doors. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0841ENR3 | EXTERIOR LIGHTING REPLACEMENT | 0841 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, failing and not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new LED light fixtures, using existing wiring. | BOULDER CITY MUSEUM MAINTENANCE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 | 9200 | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2202ADA1 | ADA ACCESSIBLE COUNTER | 2202 | The ADA provides for accessibility to sites and services for people with physical limitations. The building is used to sell souvenirs to the general public visiting the museum. The service counter in the building does not meet the current ADA requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
2205ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2205 | The Boulder City Museum is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #1 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
2202SFT1 | EGRESS STORAGE REMOVAL | 2202 | The exit is currently blocked by items that are being stored in this area. The 2012 IBC Chapter 10 Means of Egress explains that exit routes cannot be blocked, reduced or altered. This project would provide for the removal of all items in conflict with this code requirement to ensure that egress and exit routes are not impeded. | BOULDER CITY MUSEUM GIFT SHOP | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
2203ADA1 | ADA ACCESSIBLE COUNTER | 2203 | The ADA provides for accessibility to sites and services for people with physical limitations. The building is used to sell tickets to the general public visiting the museum. The service counter on the front of the building does not meet the current ADA requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM TICKET STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 4000
2203ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2203 | There is an electrical panel in the building which does not have the proper clear floor space surrounding it. The 2012 IFC Section 605.3 states that, A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the tables, microwaves and other items currently blocking the working space. | BOULDER CITY MUSEUM TICKET STATION | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 250
2204SFT2 | EGRESS STORAGE REMOVAL | 2204 | The exit is currently blocked by items that are being stored in this area. The 2012 IBC Chapter 10 Means of Egress explains that exit routes cannot be blocked, reduced or altered. This project would provide for the removal of all items in conflict with this code requirement to ensure that egress and exit routes are not impeded. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
2204ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2204 | There is an electrical panel in the building which does not have the proper clear floor space surrounding it. The 2012 IFC Section 605.3 states that, A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the tables, microwaves and other items currently blocking the working space. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 250
2206ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2206 | The Boulder City Museum is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #2 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
2207ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2207 | The Boulder City Museum is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #3 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 1280 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
2208ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 2208 | The Boulder City Museum Shade Structure #4 is open to the public and does not have designated ADA access to the Shade Structure. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Shade Structure areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM SHADE STRUCTURE #4 | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 880 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
3039ADA1 | ADA ACCESS PROGRAM ACCESSIBILITY | 3039 | The Boulder City Museum is open to the public and does not have designated ADA access to the Train Pavilion. This project would provide for ADA access inside of the public area of this building and additionally for an audio/ visual presentation at the Train Pavilion areas, which may not be ADA accessible. This project includes funds for an audio/ visual consultant to outline and document the Boulder City Railroad Museum operations and to purchase and install required audio/ visual equipment, needed signage, TDD equipment and any minor remodeling of the public area of the building, as required, to accommodate this program. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | BOULDER CITY MUSEUM TRAIN PAVILION | 9951 | CultAffr | M&H | Museums | Boulder City | 2007 | 11102 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 20000
9951SIT6 | RAILROAD TRACK REPLACEMENT RAILROAD TRACK REPLACEMENT | 9951 | The site has 5 miles of railroad tracks that were in poor condition and were not in compliance with Federal standards at the time of the survey. This project would remove and replace the existing railroad tracks and replace them with new tracks that meet or exceed the Federal Railroad design standards. | BOULDER CITY RAILROAD MUSEUM SITE | 9951 | CultAffr | M&H | Museums | Boulder City | 1996 |  | 2016-12-14 | Two to Four Years | Necessary - Not Yet Critical | 2 | 80000
2204SFT1 | STORAGE REMOVAL | 2204 | Items in this building are stored too close to the ceiling. The 2012 IFC Section 315.3.1 states that, Storage shall be maintained 2 feet or more below the ceiling in non sprinklered areas of buildings or a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings. This project would provide for the removal of all items in conflict with code requirements to ensure that the fire suppression system operates correctly. | BOULDER CITY MUSEUM CREW QUARTERS | 9951 | CultAffr | M&H | Museums | Boulder City | 2001 | 144 | 2016-12-14 | Immediate to Two Years | Currently Critical | 1 | 500
2177SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2177 | Tower #4 was constructed in 2002. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2177SFT5 | EGRESS LIGHTING REPLACEMENT | 2177 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes as needed. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2507HVA1 | HVAC EQUIPMENT REPLACEMENT | 2507 | The air handlers, fan coils and related equipment are original to the building, dating back to 2004. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 6-7 years to avoid possible failure and emergency funding for replacement. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 900000
2507ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2507 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 900000
2097ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2097 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 753775
2097HVA3 | HVAC EQUIPMENT REPLACEMENT | 2097 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 452265
2098ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2098 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 85125
2506HVA1 | HVAC EQUIPMENT REPLACEMENT | 2506 | The air handlers, fan coils and related equipment are original to the building, dating back to 2004. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 365500
2178ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2178 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 926025
2099ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2099 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 331025
2099SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2099 | Security/ Administration was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total square footage of 13,241 was used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 125790
2099SEC1 | DOORS CONTROL SYSTEM REPLACEMENT | 2099 | The control panel/ inmate movement and control system in the Security/ Administration is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 423712
2100SFT5 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2100 | Tower #1 was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2176PLM2 | BACKFLOW PREVENTER REPLACEMENT | 2176 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2176SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2176 | Yard Tower was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2101SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2101 | Tower #2 was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2104SFT5 | EGRESS LIGHTING REPLACEMENT | 2104 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2102SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2102 | Tower #3 was constructed in 2000. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2103SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2103 | Tower #5 was constructed in 2002. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2103SFT5 | EGRESS LIGHTING REPLACEMENT | 2103 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2089SFT6 | ROOF HATCH REPLACEMENT | 2089 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2104SEC1 | DOORS, LOCKS AND CONTROLS REPLACEMENT | 2104 | Tower #6 was constructed in 2002. The doors, locks and controls are original to the building and have been problematic due to age. This project would provide for installing new doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2946SFT3 | ROOF HATCH REPLACEMENT | 2946 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2099HVA1 | HVAC EQUIPMENT REPLACEMENT | 2099 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 198615
2091PLM3 | WATER HEATER REPLACEMENT | 2091 | There are five electric on-demand water heaters that are 5-gallon capacity in the building. The average life span of the water heaters is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that 5 new 5-gallon on-demand electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2091SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2091 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 616040
2091SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2091 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2091HVA1 | HOT WATER RE-USE ROOM REMODEL | 2091 | The hot water re-use room was designed to recycle hot final rinse water to be used as a pre-rinse and provide adequate pressure to laundry washers. During the time of the survey, the equipment required high maintenance, parts were obsolete, the holding tanks had failures and the system had been changed over to a cold wash and rinse system for energy savings. The hot water re-use area is due for a remodel to increase capacity and support the cold wash and rinse system. A mechanical engineer is needed to redesign the area and this project would provide for remodeling the existing area. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
2174SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2174 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2091HVA2 | HVAC EQUIPMENT REPLACEMENT | 2091 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1155075
2172SFT6 | ROOF HATCH REPLACEMENT | 2172 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2091INT1 | JANITORS CLOSET REPAIRS | 2091 | The mop sinks in the Janitors Closets are mounted adjacent to CMU walls and are showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2092ADA1 | ADA DOOR HARDWARE REPLACEMENT | 2092 | The 2010 ADA Standards for Accessible Design states that the force to activate operable parts shall be 5 pounds maximum. It is recommended that 5 pounds or less closers be installed on the men’s and woman’s ADA restroom doors. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and Sections 309.4 and 404.2.7 of the 2010 ADA Standards for Accessible Design were used as references for this project. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2091EXT3 | ROOF REPLACEMENT | 2091 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1155075
2091ADA1 | ADA TABLE UPGRADE | 2091 | Per the United States Access Board Section 226.1 where dining surfaces are provided for the consumption of food or drink, at least 5 percent of the seating spaces and standing spaces at the dining surfaces shall comply with 902. ICC ANSI-A117.1-2009 Section 902 which says, if fixed seating is provided, a loose seat or open space for a wheelchair location must be available at those accessible tables. This project would provide funding to remove 4 of the fixed seats, which will allow access for seven wheel chairs. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 7000
2090INT2 | FLOORING REPLACEMENT | 2090 | The VCT flooring in the Infirmary/ Intake is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 296874
2090INT3 | WASHING MACHINE REPLACEMENT | 2090 | One of the existing commercial washing machines appears to be a year 2000 model and has reached the end of its useful life. It is showing signs of age, and is constantly breaking down. This project would provide funding for the purchase and installation of one new 60lb. commercial washing machine. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2090INT4 | DRYER REPLACEMENT | 2090 | The commercial tumbler dryer in the laundry area is original to the building and is troublesome and problematic to operate. Considering the age of the machine and the evolving needs of the facility it is recommended to be replaced. This project provides for the removal and disposal of the existing tumbler dryer and replacement with a new unit. A total of 1 dryer was used for this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2090ADA1 | ADA SHOWER UPGRADE | 2090 | This project would provide for nine ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of nine stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 225000
2091SFT4 | PANIC HARDWARE IN ELECTRICAL ROOMS | 2091 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed in 2000. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 1-2 years. The estimate is based on one door that requires panic hardware. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2090ADA3 | ADA EMPLOYEE LOUNGE UPGRADES | 2090 | In order to comply with current ADA requirements, modification will be necessary for the employee lounge and the sinks. It is recommended to upgrade some of the features of the rooms for compliance with accessibility standards for employees. This project would provide funding for construction of an accessible sink and faucet, an accessible space at one of the dining tables and an accessible path of travel throughout the room. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2087SFT6 | ROOF HATCH REPLACEMENT | 2087 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2086SFT6 | ROOF HATCH REPLACEMENT | 2086 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2175SFT5 | ROOF HATCH REPLACEMENT | 2175 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2174SFT5 | ROOF HATCH REPLACEMENT | 2174 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2173SFT6 | ROOF HATCH REPLACEMENT | 2173 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2945SFT3 | ROOF HATCH REPLACEMENT | 2945 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2092ELE1 | GFCI OUTLETS | 2092 | The existing receptacle in the mechanical room is a standard duplex receptacle. The 2011 NEC 210.8 require this location to have GFCI protection. This project would provide for removing the standard receptacle and installing a GFCI receptacle. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
2090EXT2 | ROOF REPLACEMENT | 2090 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time-frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 395832
2092INT3 | FLOORING REPLACEMENT | 2092 | The VCT and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 269216
2090ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2090 | This building contains several water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 8000
2096ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2096 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4800
2090SEC1 | DOOR CONTROLS SYSTEM REPLACEMENT | 2090 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2948SFT3 | ROOF HATCH REPLACEMENT | 2948 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2092SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2092 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 269216
2088SFT6 | ROOF HATCH REPLACEMENT | 2088 | The roof hatches are original to the building and have reached the end of their useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for the removal and the disposal of the existing roof hatches and for the purchase and installation of new roof hatches. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2947SFT3 | ROOF HATCH REPLACEMENT | 2947 | The roof hatch is original to the building and has reached the end of its useful life. The compression spring operators do not function properly, the latches and handles are worn and the seals and flashing have deteriorated. A faulty roof hatch is a safety hazard to anyone accessing the roof. This project would provide for removal and disposal of the existing roof hatch and purchase and installation of a new roof hatch. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2094EXT2 | ROOF REPLACEMENT | 2094 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 167625
2093EXT3 | ROOF REPLACEMENT | 2093 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 134100
2087HVA2 | HVAC EQUIPMENT REPLACEMENT | 2087 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2087SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2087 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2087SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2087 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2087SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2087 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2087SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2087 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2087ADA4 | ADA SHOWER UPGRADE | 2087 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2087PLM1 | WATER HEATER REPLACEMENT | 2087 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2094PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 2094 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2094PLM2 | WATER HEATER REPLACEMENT | 2094 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2094HVA1 | VARIABLE FREQUENCY DRIVE REPLACEMENT | 2094 | The Variable Frequency Drives throughout the building have been disabled. Staff reports that the VFD's are problematic and have been by-passed from the HVAC system. This project would provide for purchase and installation of new VFD's. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2094SFT1 | EGRESS LIGHTING UPGRADE | 2094 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5588
2094SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2094 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2091ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2091 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1925125
2087HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2087 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2087ADA2 | TDD INSTALLATION | 2087 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2088ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2088 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2088HVA2 | HVAC EQUIPMENT REPLACEMENT | 2088 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2088SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2088 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2088SEC3 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2088 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2088SEC4 | DOOR CONTROLS SYSTEM REPLACEMENT | 2088 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2087ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2087 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2088ADA4 | ADA SHOWER UPGRADE | 2088 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2093INT2 | JANITORS CLOSET REPAIRS | 2093 | The walls adjacent to and above the janitor's closet mop sink did not have a water resistant finish. This project recommends the installation of fiberglass reinforced panels on the walls adjacent to the mop sink to a height of 54" above the finish floor. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2087SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2087 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2087HVA1 | EXHAUST FAN INSTALLATION | 2087 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2087ENR1 | LIGHTING UPGRADE | 2087 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2087SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2087 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2087INT3 | JANITORS CLOSET REPAIRS | 2087 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2087ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2087 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2088HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2088 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2093HVA1 | HVAC EQUIPMENT REPLACEMENT | 2093 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 167910
2094ENR1 | LIGHTING UPGRADE | 2094 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 89400
2091PLM4 | WATER TREATMENT SYSTEM REPLACEMENT | 2091 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the water softening/ treatment system causes additional wear and tear on the domestic water supply lines, water heaters and plumbing fixtures. This project would provide for the installation of a PRV (to be installed prior to the water softener/ treatment system) and the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program to include an updated chemical control system, service and employee training to be provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 fee is suggested. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2092HVA1 | HVAC EQUIPMENT REPLACEMENT | 2092 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504780
2092ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2092 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 841300
2093INT3 | FLOORING REPLACEMENT | 2093 | The VCT in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base in the next 2-3 years. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
2090SFT2 | ANCHOR SHELVES | 2090 | OSHA recommends that the bottom of all columns be furnished with column base plates, and be anchored to the floor with anchor bolts capable of resisting the forces caused by the loads on the shelving unit. Per OSHA standard 1926.250(a)(1) All materials stored in tiers shall be stacked, racked, blocked, interlocked, or otherwise secured to prevent sliding, falling or collapse. This project would provide for a licensed contractor to install anchor bolts and properly secure the shelving units to the floor and to the other shelves. This project should be overseen by a licensed engineer or architect. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2093SEC1 | DOOR CONTROLS SYSTEM REPLACEMENT | 2093 | The control panel/ inmate movement and control system in the building is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2091CUL1 | DISHWASHER REPLACEMENT | 2091 | The commercial dishwashers in the kitchen appear to be original to the building and are troublesome and problematic to operate. Considering the age of the dishwashers and the evolving needs of the facility they are recommended to be replaced. This project provides for removal and disposal of the two existing dishwashers and replacement with two new units. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
2094SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2094 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 89400
2094INT3 | FLOORING REPLACEMENT | 2094 | The VCT (vinyl composite tile) and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100575
2094ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2094 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 279375
2094HVA2 | HVAC EQUIPMENT REPLACEMENT | 2094 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 167625
2095SEC1 | DOOR CONTROLS SYSTEM REPLACEMENT | 2095 | The control panel/ inmate movement and control system in the Gatehouse is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2095ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2095 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 154125
2093ELE1 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2093 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 279850
2092PLM1 | WATER HEATER REPLACEMENT | 2092 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2093PLM1 | WATER TREATMENT SYSTEM REPLACEMENT | 2093 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
3775SFT1 | EXTERIOR LANDING INSTALLATION | 3775 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2093ADA1 | ADA TABLE UPGRADE | 2093 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2093ADA2 | ADA ACCESSIBLE COUNTER | 2093 | The ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2093ADA3 | ADA RESTROOM FIXTURES | 2093 | The fixtures in the ADA restrooms are worn and damaged from many years of use including the water closets, urinals, lavatories, faucets, shower heads and handles. Many fixtures are or have been leaking and have caused extensive scaling and staining to the fixtures themselves. It is recommended that all fixtures be replaced with new ADA compliant units. This project includes removal and disposal of the existing fixtures and installation of new fixtures. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2091INT3 | FLOORING REPLACEMENT | 2091 | The tile in the building is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new culinary grade tile in the next 4-5 years. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 693045
2093PLM2 | WATER HEATER REPLACEMENT | 2093 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2095HVA1 | HVAC EQUIPMENT REPLACEMENT | 2095 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends replacement of the air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 92475
2092SFT1 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2092 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2092INT2 | JANITORS CLOSET REPAIRS | 2092 | The walls adjacent to and above the janitor's closet mop sink did not have a water resistant finish. This project recommends the installation of FRP on the walls adjacent to the mop sink to a height of 54" above the finish floor. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2092PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2092 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2089INT5 | SHOWER UPGRADE | 2089 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing unit. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2090SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2090 | Infirmary/ Intake was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 100 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800000
2946PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2946 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
2093ADA4 | ADA UPGRADES | 2093 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. It is recommended that applicable signage be installed where required. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 600
2175ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2175 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2947PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2947 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2174INT3 | JANITORS CLOSET REPAIRS | 2174 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2174SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2174 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2174ENR1 | LIGHTING UPGRADE | 2174 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2174HVA1 | EXHAUST FAN INSTALLATION | 2174 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2174SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2174 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2174ADA2 | TDD INSTALLATION | 2174 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2174ADA1 | ADA TABLE UPGRADE | 2174 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2174INT2 | SHOWER UPGRADE | 2174 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2175ADA4 | ADA SHOWER UPGRADE | 2175 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2175HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2175 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2175SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2175 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438241.25
2175SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2175 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2174PLM1 | WATER HEATER REPLACEMENT | 2174 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2175ENR1 | LIGHTING UPGRADE | 2175 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2172SFT2 | SPRINKLER HEAD REPLACEMENT | 2172 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2175SFT2 | SPRINKLER HEAD REPLACEMENT | 2175 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2174SFT1 | SPRINKLER HEAD REPLACEMENT | 2174 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2087ADA1 | ADA TABLE UPGRADE | 2087 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2175ADA2 | TDD INSTALLATION | 2175 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2175SFT4 | ELECTRICAL OUTLET & CABLE UPGRADES | 2175 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2175HVA1 | EXHAUST FAN INSTALLATION | 2175 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2175HVA2 | HVAC EQUIPMENT REPLACEMENT | 2175 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2175SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2175 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2175INT3 | JANITORS CLOSET REPAIRS | 2175 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2175ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2175 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2175PLM1 | WATER HEATER REPLACEMENT | 2175 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2175SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2175 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2174SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2174 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2175SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2175 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2505INT1 | INTERIOR FINISHES | 2505 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | STORAGE BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 144 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
3775EXT2 | EXTERIOR FINISHES | 3775 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3775INT1 | INTERIOR FINISHES | 3775 | It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3775ELE1 | PANIC HARDWARE IN ELECTRICAL ROOMS | 3775 | The Pump House with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 2-3 years. The estimate is based on one door that requires panic hardware. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3774EXT1 | EXTERIOR FINISHES | 3774 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HAZMAT BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 64 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
3774INT1 | INTERIOR FINISHES | 3774 | It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | HAZMAT BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 64 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 640
3223EXT1 | EXTERIOR FINISHES | 3223 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | HDSP WATER TANK #1 | 9952 | Correct | HDSP |  | Indian Springs | 1978 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29520
3223INT1 | INTERIOR FINISHES | 3223 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | HDSP WATER TANK #1 | 9952 | Correct | HDSP |  | Indian Springs | 1978 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29520
3223EXT2 | GUARDRAIL INSTALLATION | 3223 | The water tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | HDSP WATER TANK #1 | 9952 | Correct | HDSP |  | Indian Springs | 1978 | 2952 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
3224EXT1 | EXTERIOR FINISHES | 3224 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | HDSP WATER TANK #2 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 29520
3224INT1 | INTERIOR FINISHES | 3224 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | HDSP WATER TANK #2 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 2952 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3224EXT2 | GUARDRAIL INSTALLATION | 3224 | The water tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | HDSP WATER TANK #2 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 2952 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
3225EXT1 | EXTERIOR FINISHES | 3225 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 2-3 years and is recommended on a cyclical basis based on environmental conditions. | HDSP WATER TANK #3 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 1859 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18590
3225INT1 | INTERIOR FINISHES | 3225 | It is important to maintain water quality, quantity and the interior finish of the water tank. This project would include hiring certified divers or draining the tank to inspect and clean the interior walls, and to weld, sandblast and perform repairs and add protective coatings, if needed. It is important to follow all ANSI, NSF and AWWA approved ways to disinfect and repair water tanks. The standard recommendation is to conduct a comprehensive inspection inside the water tank every 5 years, except for newly constructed tanks. Newly constructed water tanks should be inspected within 10 years of service and every 5 years thereafter. | HDSP WATER TANK #3 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 1859 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2174ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2174 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2088INT2 | SHOWER UPGRADE | 2088 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
2174ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2174 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2174HVA2 | HVAC EQUIPMENT REPLACEMENT | 2174 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2174SFT4 | ELECTRICAL OUTLET & CABLE UPGRADES | 2174 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2948SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2948 | Housing Unit 11 was constructed in 2009. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
2947SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2947 | Housing Unit 10 was constructed in 2009. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
3225EXT2 | GUARDRAIL INSTALLATION | 3225 | The water tank is used to store water for fire protection. It is an AWWA D100 tank. 360° guardrails should be installed per NFPA 22 standards which designate the requirements for water tanks used for private fire protection. This project would provide for the purchase and installation of new guardrails to be located at the top of the water tank. | HDSP WATER TANK #3 | 9952 | Correct | HDSP |  | Indian Springs | 1998 | 1859 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
2945SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2945 | Housing Unit 9 was constructed in 2008. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
2505EXT1 | EXTERIOR FINISHES | 2505 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 144 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1440
2172INT2 | SHOWER UPGRADE | 2172 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2172INT1 | INTERIOR FINISHES | 2172 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2173SFT5 | SPRINKLER HEAD REPLACEMENT | 2173 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2175ADA5 | ADA TABLE UPGRADE | 2175 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2948HVA2 | EXHAUST FAN INSTALLATION | 2948 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2088SFT2 | SPRINKLER HEAD REPLACEMENT | 2088 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2946SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2946 | Housing Unit 12 was constructed in 2008. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. A total of 168 doors were used for this estimate. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 421875
3775EXT1 | CONCRETE APRON INSTALLATION | 3775 | There are two rollup doors that don’t have concrete aprons on the outside of the building. This project would provide for the installation of two new 120 square foot 4" thick concrete slab-on-grade aprons. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2175PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2175 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2175PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2175 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2175PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2175 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2945PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2945 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2945PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2945 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2945PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2945 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
2946PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2946 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2946PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2946 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2093SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2093 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2947PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2947 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2088SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2088 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2947PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2947 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
2948PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2948 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504000
2089SFT2 | SPRINKLER HEAD REPLACEMENT | 2089 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2090PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2090 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2090SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2090 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 263888
2090SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2090 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2090INT5 | JANITORS CLOSET REPAIRS | 2090 | The mop sinks in the Janitor Closets are mounted adjacent to CMU walls and are showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2090PLM3 | WATER HEATER REPLACEMENT | 2090 | There is a 40 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2090ADA4 | ADA ACCESSIBLE COUNTER | 2090 | The ADA provides for accessibility to sites and services for people with physical limitations. The nurse’s station at the entrance of the building has a service counter which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2948PLM4 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2948 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 15000
2090ELE4 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 2090 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 824650
2948PLM5 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2948 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 50000
3776EXT1 | CONCRETE APRON INSTALLATION | 3776 | There are two rollup doors that don’t have concrete aprons on the outside of the building. This project would provide for the installation of two new 120 square foot 4" thick concrete slab-on-grade aprons. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
3776SFT1 | EXTERIOR LANDING INSTALLATION | 3776 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
3776EXT2 | EXTERIOR FINISHES | 3776 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3776INT1 | INTERIOR FINISHES | 3776 | It is recommended to repair and seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8400
3776ELE1 | PANIC HARDWARE IN ELECTRICAL ROOMS | 3776 | The Pump House with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within 2-3 years. The estimate is based on one door that requires panic hardware. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2174PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2174 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2090ELE2 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 2090 | There are electrical panels in the building which do not have proper clear floor space around them. The 2012 IFC Section 605.3 states that, A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the items currently blocking the working space. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 250
2947ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2947 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2174PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2174 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2086PLM3 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2086 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2086PLM2 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2086 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3774EXT2 | ROOF REPLACEMENT | 3774 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HAZMAT BUILDING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 64 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
3775EXT3 | ROOF REPLACEMENT | 3775 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PUMP HOUSE #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12600
2087PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2087 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2948ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2948 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2087PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2087 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2946ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2946 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2945ELE2 | DOOR CONTROLS SYSTEM REPLACEMENT | 2945 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1438241.25
2089EXT2 | ROOF REPLACEMENT | 2089 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2175EXT2 | ROOF REPLACEMENT | 2175 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2087SFT2 | SPRINKLER HEAD REPLACEMENT | 2087 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2090HVA2 | HVAC EQUIPMENT REPLACEMENT | 2090 | The air handler fan coils and related equipment are original to the building (2000). The equipment has consistent problems and has reached its expected life span. This project recommends replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 494790
3776EXT3 | ROOF REPLACEMENT | 3776 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PUMP HOUSE #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 840 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12600
2089PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2089 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2088EXT2 | ROOF REPLACEMENT | 2088 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2173PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2173 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2173PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2173 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2173PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2173 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2172PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2172 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2086PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2086 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2172PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2172 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 588000
2174PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2174 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2089PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2089 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2089PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2089 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2088PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2088 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2088PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2088 | The showers do not have water control systems in place. It is recommended to install new water control systems within the next 2-3 years. Installing water control systems will reduce the water usage in the building. This project includes the installation of new water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2088PLM2 | CELL WATER CONTROL SYSTEMS REPLACEMENT | 2088 | This building is equipped with cell water control systems that are outdated and should be scheduled for replacement. Problems exist with the current water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. It is recommended to replace the water control systems. This project includes the replacement of the water controllers, piping, valves, access panels and all connections to the existing utilities. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 504000
2087PLM4 | COMPUTER WATER CONTROL SYSTEM REPLACEMENT | 2087 | This building is equipped with a computer water control system that is outdated and should be scheduled for replacement. Problems exist with the current computer water control system. It is increasingly difficult to find software updates and experienced repairmen to service the equipment. This project recommends the installation of a new computer water control system for the building. This system will monitor and control the water for all fixtures throughout the building. New electronic sensors will be installed on each water control system. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
2172PLM3 | SHOWER WATER CONTROL SYSTEMS REPLACEMENT | 2172 | This building is equipped with shower water control systems that are outdated and should be scheduled for replacement. Problems exist with the current shower water control systems. It is increasingly difficult to find replacement parts and experienced repairmen to service the equipment. This project includes the replacement of the shower water controllers, piping, valves, access panels, shower heads and all connections to the existing utilities. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2101SFT4 | EGRESS LIGHTING REPLACEMENT | 2101 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2101SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2101 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2101ENR3 | LIGHTING UPGRADE | 2101 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2101INT2 | FLOORING REPLACEMENT | 2101 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2101SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2101 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2101SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2101 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2103ENR1 | LIGHTING UPGRADE | 2103 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2101EXT2 | WINDOW REPLACEMENT | 2101 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2102SFT4 | EGRESS LIGHTING REPLACEMENT | 2102 | There are older emergency egress lighting units in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and to also provide additional lights on the main exit routes and in individual rooms as needed. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2101HVA1 | HVAC EQUIPMENT REPLACEMENT | 2101 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2101EXT3 | SLIDING GLASS DOOR REPLACEMENT | 2101 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2100SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2100 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2945PLM1 | FLOOR DRAIN REPAIR | 2945 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2945EXT1 | EXTERIOR FINISHES | 2945 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2946SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2946 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2101PLM1 | WATER HEATER REPLACEMENT | 2101 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2102ENR3 | LIGHTING UPGRADE | 2102 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2100SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2100 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2103SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2103 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2103SFT4 | BACKFLOW PREVENTER REPLACEMENT | 2103 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2103PLM1 | WATER HEATER REPLACEMENT | 2103 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2103EXT2 | WINDOW REPLACEMENT | 2103 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 33600
2103HVA1 | HVAC EQUIPMENT REPLACEMENT | 2103 | The HVAC unit was installed in 2002 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 11375
2102EXT3 | SLIDING GLASS DOOR REPLACEMENT | 2102 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2102SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2102 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2102HVA1 | HVAC EQUIPMENT REPLACEMENT | 2102 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2102INT2 | FLOORING REPLACEMENT | 2102 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2102SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2102 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2102SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2102 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2102PLM1 | WATER HEATER REPLACEMENT | 2102 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2102EXT2 | WINDOW REPLACEMENT | 2102 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2088PLM1 | WATER HEATER REPLACEMENT | 2088 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2103EXT3 | ROOF REPLACEMENT | 2103 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5460
2948SFT1 | SPRINKLER HEAD REPLACEMENT | 2948 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2093SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2093 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 89400
2947EXT1 | EXTERIOR FINISHES | 2947 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2948SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2948 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2948ENR1 | LIGHTING UPGRADE | 2948 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2948SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2948 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2948ADA2 | TDD INSTALLATION | 2948 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2947SFT1 | SPRINKLER HEAD REPLACEMENT | 2947 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2948ADA1 | ADA TABLE UPGRADE | 2948 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2947ADA1 | ADA TABLE UPGRADE | 2947 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2945INT1 | INTERIOR FINISHES | 2945 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
9952ELE2 | ELECTRICAL EQUIPMENT SURVEY | 9952 | The electrical systems are original to the site and should be evaluated to reduce possibility of a fire hazard, equipment down time or energy loss. There seems to be loose connections and electrical deficiencies and repairs needed. It is recommended to perform an infrared and ultrasonic inspection on all electrical site-wide and sample the oil in all oil filled transformers. This project would provide for an electrical engineer to conduct analysis of the current electrical and to recommend a preventative maintenance plan and necessary repairs. Other projects may arise from this survey. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 95000
9952PLM2 | WELL UPGRADE | 9952 | The construction of Well #6 was accomplished with CIP project (13-C04). This project would include construction of a well house with associated equipment and connection to the existing water distribution system at High Desert State Prison. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 240480
2100ENR3 | LIGHTING UPGRADE | 2100 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2100INT2 | FLOORING REPLACEMENT | 2100 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2100SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2100 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2948INT1 | INTERIOR FINISHES | 2948 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2946SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2946 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2103SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2103 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2946HVA1 | EXHAUST FAN INSTALLATION | 2946 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2946ADA2 | TDD INSTALLATION | 2946 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2946INT1 | INTERIOR FINISHES | 2946 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2946ADA1 | ADA TABLE UPGRADE | 2946 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2946SFT1 | SPRINKLER HEAD REPLACEMENT | 2946 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2947PLM1 | FLOOR DRAIN REPAIR | 2947 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2946EXT1 | EXTERIOR FINISHES | 2946 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2946ENR1 | LIGHTING UPGRADE | 2946 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2947SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2947 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2947ENR1 | LIGHTING UPGRADE | 2947 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2947HVA1 | EXHAUST FAN INSTALLATION | 2947 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2947SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2947 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2947ADA2 | TDD INSTALLATION | 2947 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2947INT1 | INTERIOR FINISHES | 2947 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #10 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2946PLM1 | FLOOR DRAIN REPAIR | 2946 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #12 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 52096 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2506SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2506 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2506ENR1 | LIGHTING UPGRADE | 2506 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 116960
2506SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2506 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 116960
2506EXT1 | EXTERIOR FINISHES | 2506 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 146200
2506EXT3 | ROOF REPLACEMENT | 2506 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 7-8 years to be consistent with the roofing program and the end of the warranty period. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 175440
2506INT1 | INTERIOR FINISHES | 2506 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 146200
2103INT2 | FLOORING REPLACEMENT | 2103 | The VCT flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2506EXT4 | WINDOW REPLACEMENT | 2506 | The existing windows in this building are of double pane wire mesh construction. Some are broken and all are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 219300
2507ADA2 | ADA UPGRADES | 2507 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2178EXT2 | ROOF REPLACEMENT | 2178 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 444492
2178ENR1 | LIGHTING UPGRADE | 2178 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 296328
2178ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2178 | This building contains two water fountains that are not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 8000
2178HVA2 | HVAC EQUIPMENT REPLACEMENT | 2178 | The existing HVAC system consists of ceiling mounted hydronic heaters, 8 packaged heat pumps, 10 swamp coolers and an Evapco cooling tower. The HVAC system was installed in 2002. The HVAC system is not energy efficient and has reached the end of its expected and useful life. This project would provide for installation of new HVAC equipment. The new systems shall be designed to significantly reduce utility usage in order to comply with the 2012 IECC and ASHRAE 90.1. This project includes removal and disposal of the existing HVAC system and all required connections to utilities. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 926025
2178SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2178 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 296328
2178HVA3 | EXHAUST FAN REPLACEMENT | 2178 | The exhaust fans in the restrooms serving the Warehouse/ Motor Pool building were inoperative and/or damaged at the time of the survey. Due to building code requirements and excessive humidity concerns, this project would provide funding for the purchase and installation of high volume commercial exhaust fans. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2506INT2 | JANITORS CLOSET REPAIRS | 2506 | The mop sink in the Janitors Closet has several cracks in the concrete and is leaking. This could lead to mold growth if not addressed. This project would provide for a new fiberglass mop sink and FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2800
2945SFT1 | SPRINKLER HEAD REPLACEMENT | 2945 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 16800
2945ADA2 | TDD INSTALLATION | 2945 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2945SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2945 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 258045
2945HVA1 | EXHAUST FAN INSTALLATION | 2945 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2945ENR1 | LIGHTING UPGRADE | 2945 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 412872
2945SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2945 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2507EXT1 | EXTERIOR FINISHES | 2507 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete walls, painting the doors and trim and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2506PLM1 | WATER HEATER REPLACEMENT | 2506 | There is a 66 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1750
2945ADA1 | ADA TABLE UPGRADE | 2945 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #9 | 9952 | Correct | HDSP |  | Indian Springs | 2008 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2507SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2507 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2507INT1 | INTERIOR FINISHES | 2507 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600000
2507SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2507 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 480000
2507ADA1 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2507 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 12000
2507PLM0 | WATER HEATER REPLACEMENT | 2507 | There are six 30 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
2507ENR1 | LIGHTING UPGRADE | 2507 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480000
2178INT2 | JANITORS CLOSET REPAIRS | 2178 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the CMU walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2507EXT2 | ROOF REPLACEMENT | 2507 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 6-7 years to be consistent with the roofing program and the end of the warranty period. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 720000
2104SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2104 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2178PLM1 | WATER HEATER REPLACEMENT | 2178 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 8-9 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1500
2176EXT2 | WINDOW REPLACEMENT | 2176 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2176SFT4 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2176 | The building does not currently have exit signs and emergency egress lighting is insufficient. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 455
2176HVA1 | HVAC EQUIPMENT REPLACEMENT | 2176 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2176EXT3 | SLIDING GLASS DOOR REPLACEMENT | 2176 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2104SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2104 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2176SFT2 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2176 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2104INT2 | FLOORING REPLACEMENT | 2104 | The VCT flooring in the building is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2176INT2 | FLOORING REPLACEMENT | 2176 | The VCT flooring in the tower is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2104SFT4 | BACKFLOW PREVENTER REPLACEMENT | 2104 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2104PLM1 | WATER HEATER REPLACEMENT | 2104 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2104EXT2 | WINDOW REPLACEMENT | 2104 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 33600
2104HVA1 | HVAC EQUIPMENT REPLACEMENT | 2104 | The HVAC unit was installed in 2002 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 11375
2104EXT3 | ROOF REPLACEMENT | 2104 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5460
2103ENV1 | PEST CONTROL | 2103 | There are numerous bird and rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the pigeon and rodent droppings by a licensed pest control business. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2104ENR1 | LIGHTING UPGRADE | 2104 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2177SFT4 | BACKFLOW PREVENTER REPLACEMENT | 2177 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
9952ELE1 | HIGH MAST LAMP REPLACEMENT | 9952 | There are 45 high mast security light poles throughout the facility that have 10 security lamps each. Many of the lamps were burned out at the time of this survey and should be scheduled for replacement. This project would provide for the purchase and installation of 450 LEDs and retrofit the fixtures for the high mast security light poles. The cost includes the removal and the disposal of the existing lamps and fixtures. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 225000
2178ELE1 | GFCI OUTLETS | 2178 | The existing receptacles next to the drinking fountain and eye wash station are standard duplex receptacles. The 2011 NEC Code 210.8 require these locations to have GFCI protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
2178SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2178 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2177ENV2 | PEST CONTROL | 2177 | There are numerous bird and rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the pigeon and rodent droppings by a licensed pest control business. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2177SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2177 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2177ENR1 | LIGHTING UPGRADE | 2177 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2176PLM1 | WATER HEATER REPLACEMENT | 2176 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2177SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2177 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2178PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2178 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2177PLM1 | WATER HEATER REPLACEMENT | 2177 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2177EXT2 | WINDOW REPLACEMENT | 2177 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 33600
2177HVA1 | HVAC EQUIPMENT REPLACEMENT | 2177 | The HVAC unit was installed in 2002 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 11375
2176ENV1 | PEST CONTROL | 2176 | There are numerous bird and rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the pigeon and rodent droppings by a licensed pest control business. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2176SFT1 | FIRE ALARM SYSTEM REPLACEMENT | 2176 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3640
2176ENR3 | LIGHTING UPGRADE | 2176 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3640
2177INT2 | FLOORING REPLACEMENT | 2177 | The VCT flooring in Tower #4 is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4095
2173SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2173 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2948PLM1 | FLOOR DRAIN REPAIR | 2948 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2173INT3 | JANITORS CLOSET REPAIRS | 2173 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2173ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2173 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2173PLM1 | WATER HEATER REPLACEMENT | 2173 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2173SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2173 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2173ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2173 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2173ENR1 | LIGHTING UPGRADE | 2173 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2173SFT4 | ELECTRICAL OUTLET & CABLE UPGRADES | 2173 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2173HVA1 | EXHAUST FAN INSTALLATION | 2173 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2173SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2173 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438241.25
2173HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2173 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2173ADA4 | ADA SHOWER UPGRADE | 2173 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2172ADA1 | ADA TABLE UPGRADE | 2172 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2172ADA2 | TDD INSTALLATION | 2172 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2172SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2172 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2172HVA1 | EXHAUST FAN INSTALLATION | 2172 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2173HVA2 | HVAC EQUIPMENT REPLACEMENT | 2173 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2175INT2 | SHOWER UPGRADE | 2175 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2086ENR1 | LIGHTING UPGRADE | 2086 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2086HVA3 | EXHAUST FAN INSTALLATION | 2086 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2086SEC2 | COMMUNICATIONS SYSTEM UPGRADE | 2086 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2086ADA3 | TDD INSTALLATION | 2086 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2086ADA4 | ADA TABLE UPGRADE | 2086 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2086SFT5 | SPRINKLER HEAD REPLACEMENT | 2086 | The existing fire suppression sprinkler heads are an older style and are susceptible to damage and misuse by the inmates. Inmates have tied strings to the sprinkler heads and have broken them in the past. This project recommends that all of the fire sprinkler heads in all cells be removed and replaced with a new state of the art tamper-resistant sprinkler heads. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 40000
2173SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2173 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2087EXT2 | ROOF REPLACEMENT | 2087 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2172INT3 | JANITORS CLOSET REPAIRS | 2172 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2174SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2174 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1438241.25
2174HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2174 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2174ADA4 | ADA SHOWER UPGRADE | 2174 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2173INT2 | SHOWER UPGRADE | 2173 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2173ADA1 | ADA TABLE UPGRADE | 2173 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2173ADA2 | TDD INSTALLATION | 2173 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2173SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2173 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2087INT2 | SHOWER UPGRADE | 2087 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2089ADA4 | ADA SHOWER UPGRADE | 2089 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2089PLM1 | WATER HEATER REPLACEMENT | 2089 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2089SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2089 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2089ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2089 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2089HVA2 | HVAC EQUIPMENT REPLACEMENT | 2089 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2089SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2089 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2089SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2089 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2172ENR1 | LIGHTING UPGRADE | 2172 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2089HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2089 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2089SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2089 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2088ADA1 | ADA TABLE UPGRADE | 2088 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2088ADA2 | TDD INSTALLATION | 2088 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2088SEC2 | COMMUNICATIONS SYSTEM UPGRADE | 2088 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2088HVA1 | EXHAUST FAN INSTALLATION | 2088 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2088ENR1 | LIGHTING UPGRADE | 2088 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2088SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2088 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2088INT3 | JANITORS CLOSET REPAIRS | 2088 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2089SEC3 | DOOR CONTROLS SYSTEM REPLACEMENT | 2089 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2172HVA3 | EVAPORATIVE COOLER REPLACEMENT | 2172 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2086ADA2 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2086 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
9952SEC1 | SECURITY SYSTEM INSTALLATION | 9952 | The building does not have a security system. This project recommends installing video monitoring and recording equipment in every common inmate area and visitor area throughout the High Desert State Prison. This project would also include camera installation in all housing units. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2417400
2172ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2172 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2172PLM1 | WATER HEATER REPLACEMENT | 2172 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2172SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2172 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2172ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2172 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2172HVA2 | HVAC EQUIPMENT REPLACEMENT | 2172 | The air handlers, fan coils and related equipment are original to the building, dating back to 2002. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 4-5 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2089ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2089 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2172SEC2 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2172 | The Housing Unit was constructed in 2002. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2089INT3 | JANITORS CLOSET REPAIRS | 2089 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2172ADA4 | ADA SHOWER UPGRADE | 2172 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2089ADA1 | ADA TABLE UPGRADE | 2089 | Per the United States Access Board and ICC ANSI-A117.1-2009, at least 5 percent of the seating spaces shall be, if fixed seating is provided, a loose seat or open space for a wheelchair. This project would provide funding to remove 3 of the fixed seats, which will allow access for wheel chairs. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2089ADA2 | TDD INSTALLATION | 2089 | The Housing Unit is not equipped with a TDD. In order to comply with ADA requirements it is recommended to install a TDD system in the Housing Unit. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 60000
2089SEC1 | COMMUNICATIONS SYSTEM UPGRADE | 2089 | This building is equipped with a communications system that at the time of the survey was not working properly. The communications system provides paging, phone communications and communication to inmates. The communications system is an integral component of the notification and safety procedures for the inmates and staff. The system is problematic and replacement parts are no longer available. It is recommended that the communications system be upgraded. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 222500
2089HVA1 | EXHAUST FAN INSTALLATION | 2089 | The mechanical room within the housing unit has plumbing fixtures and drains. Due to moisture in this room, the humidity is very high and there is an increase probability for indoor air quality concern. This project would provide for the purchase and installation of a new commercial grade exhaust fan and the assemblies and will include the connections to utilities. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2089ENR1 | LIGHTING UPGRADE | 2089 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 356000
2172SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2172 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2172SFT5 | ELECTRICAL OUTLET & CABLE UPGRADES | 2172 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2098ADA1 | BREAK ROOM REMODEL | 2098 | The kitchenette and associated cabinets in the employee break room are original to the building. The quality of construction and installation were inadequate for the high usage at this facility, and the cabinets and countertops are delaminating and failing. This project recommends the replacement of the existing kitchen countertops, cabinets, and associated equipment with heavy duty, quality components. The cabinets should be finished inside and outside with a melamine or similar finish which encapsulates the door, frame, and shelving. The countertops should be constructed of a highly durable product, such as stainless steel, over a moisture resistant underlayment to minimize swelling and damage from water exposure. ADA compliance according to NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and the most current version of the ADA Standards for Accessible Design should be incorporated into the design such as providing an accessible sink. This estimate includes removal and disposal of the existing materials. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 15000
2097INT2 | JANITORS CLOSET REPAIRS | 2097 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2097PLM3 | WATER HEATER REPLACEMENT | 2097 | There is a 30 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2097ENR1 | LIGHTING UPGRADE | 2097 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 241208
2097SFT2 | PANIC HARDWARE IN ELECTRICAL ROOMS | 2097 | The electrical room with the uninterruptable power supply contains equipment that meets or exceeds 1,200 amps. It is recommended per the 2012 IBC 1008.1.10 that panic and fire exit hardware be installed. This equipment was not required when the building was constructed in 2000. When a remodel occurs, it is suggested to comply with current code. It is recommended that this project be completed within the next year. The estimate is based on one door that requires panic hardware. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2086INT3 | JANITORS CLOSET REPAIRS | 2086 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2097HVA1 | VARIABLE FREQUENCY DRIVE REPLACEMENT | 2097 | The Variable Frequency Drives (VLT 6000) for the hot water drives have been disabled. Staff reports that the hot water VFD's have been problematic and have purposely been by-passed from the HVAC system. This project would provide for purchase and installation of the VFD's for the hot water drives. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 35000
2086SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2086 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2097PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2097 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2096ADA2 | ADA UPGRADES | 2096 | Section 4.13.9 of the ADAAG states that handles, pulls, latches, locks and other operating devices on accessible doors shall have a shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist to operate. Lever-operated mechanisms, push-type mechanisms, and U-shaped handles are acceptable designs. It is recommended that proper lever hardware be installed in this building to meet these requirements. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2098SFT4 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2098 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2098SFT3 | BACKFLOW PREVENTER REPLACEMENT | 2098 | There is a backflow preventer for the fire suppression system in the building. It is leaking and should be scheduled for replacement. At the time of the survey the staff indicated they have rebuilt the backflow preventer several times, however it continues to leak. This project would provide for replacing the backflow preventer by a licensed fire suppression contractor. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2098SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2098 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 27240
2097ENR2 | ENERGY MANAGEMENT SYSTEM INSTALLATION | 2097 | The Snider energy management system is original to the building and should be scheduled for replacement. Replacement parts for performing routine and emergency maintenance are not made any more. The system has had numerous failures and the staff no longer has some monitoring capabilities. In a facility of this type, it is imperative that the conditioned spaces are properly controlled at all times. This project would provide for the removal and disposal of the existing energy management system and replacement with new equipment including all required connections to utilities and equipment. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
2098HVA1 | HVAC EQUIPMENT REPLACEMENT | 2098 | The air handlers, fan coils and related HVAC equipment are original to the building, dating back to 2000. At the time of the survey the HVAC equipment was not working and the staff had indicated that it was very problematic and they had abandon the system and installed a mini split for the office location within the building. The equipment has reached its expected life span. This project recommends replacement of all the air handlers, fan coils, ventilation and related HVAC equipment and exhaust fans. It is recommended that this project be implemented in the next year. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 46600
2097SFT1 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2097 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2098ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2098 | The 30 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2098PLM1 | WATER HEATER REPLACEMENT | 2098 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1500
2098EXT3 | ROOF REPLACEMENT | 2098 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 51075
2099PLM1 | WATER HEATER REPLACEMENT | 2099 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 4-5 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 1500
2099SFT3 | FIRE SUPPRESSION OBSTRUCTION INVESTIGATION | 2099 | This building has an automatic fire suppression system. Per NFPA 25 Obstruction Investigation and Prevention an inspection of piping and branch line conditions shall be conducted every 5 years by opening a flushing connection at the end of one main and by removing a sprinkler toward the end of one branch line for the purpose of inspecting for the presence of foreign organic and inorganic material. It is recommended that this project be completed within the next year and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 9000
2099INT2 | JANITORS CLOSET REPAIRS | 2099 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide FRP to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2099SFT2 | FIRE ALARM SYSTEM REPLACEMENT | 2099 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 105928
2099ENR1 | LIGHTING UPGRADE | 2099 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 105928
2099ELE1 | ELECTRICAL TRANSFORMER REPLACEMENT | 2099 | The 45 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2100EXT1 | SLIDING GLASS DOOR REPLACEMENT | 2100 | The sliding glass door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2500
2100HVA1 | HVAC EQUIPMENT REPLACEMENT | 2100 | The HVAC unit was installed in 2000 and is not energy efficient. It has reached the end of its expected and useful life. This project would provide for the installation of a new HVAC unit and cleaning of the existing duct work and grilles. This project includes the removal and the disposal of the existing equipment and all required connections to the utilities. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11375
2100SFT4 | EGRESS LIGHTING REPLACEMENT | 2100 | The building does not currently have exit signs and emergency egress lighting is insufficient. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1000
2100EXT2 | WINDOW REPLACEMENT | 2100 | The existing windows in this building are of single pane wire mesh construction. They are not energy efficient. This project would provide for the removal and replacement of the windows with new dual pane security rated windows. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 19200
2098PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2098 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 25000
2095EXT3 | ROOF REPLACEMENT | 2095 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 73980
2086ELE2 | ELECTRICAL TRANSFORMER REPLACEMENT | 2086 | The 50 kVA electrical transformer that provides services to the building was damaged at the time of inspection and does not function properly. This project recommends replacing the electrical transformer. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2086HVA2 | HVAC EQUIPMENT REPLACEMENT | 2086 | The air handlers, fan coils and related equipment are original to the building, dating back to 2000. The equipment has consistent problems and has reached its expected life span. This project recommends the replacement of all air handlers, fan coils, ventilation equipment and exhaust fans. It is recommended that this project be implemented in the next 2-3 years to avoid possible failure and emergency funding for replacement. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2086SFT2 | ELECTRICAL OUTLET & CABLE UPGRADES | 2086 | At the time of the survey the building had residential and commercial cover plates over the electrical outlets and coaxial wires. This poses a safety hazard allowing inmates to remove them and use them as weapons. This could be a safety hazard to inmates and guards. This project would provide for the installation of new security grade cover plates throughout the entire housing unit. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 74592
2097HVA2 | BOILER BURNER REPLACEMENT | 2097 | The burners on the boilers were not working correctly at the time of the survey. This project recommends replacing all 6 boiler burners with energy-efficient boiler burners. This project would provide for the labor and materials to install 6 new boiler burners. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 670000.02
2086SEC1 | CELL DOORS, LOCKS AND CONTROLS REPLACEMENT | 2086 | The Housing Unit was constructed in 2000. The cell doors, locks and controls are original to the building and have been problematic due to inmate abuse and age. This project would provide for installing new cell doors, locks and controls. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 421875
2086HVA1 | EVAPORATIVE COOLER REPLACEMENT | 2086 | There is a guard stationed on the roof to look out onto the yard. They have one overhead swamp cooler to keep them cool in the warmer months. At the time of the survey the swamp cooler was not working. It is severely scaled and has reached the end of its useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2086ELE1 | DOOR CONTROL SYSTEM REPLACEMENT | 2086 | The control panel/ inmate movement and control system in the housing unit is not working properly. The cell door indicator lights on the control panel are falsely representing the actual status of the cell doors. The officer sometimes cannot tell if the cell door is open or closed. This project would replace the existing secured door control system with a programmable logic controlled system using touch screens for actuation and door status. This project would replace the existing door control system and the outdated wiring. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1438241.25
2086SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2086 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 356000
2095PLM1 | WATER HEATER REPLACEMENT | 2095 | There are two 119 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, the units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2095PLM2 | WATER TREATMENT SYSTEM REPLACEMENT | 2095 | The existing water softening/ treatment systems in the building are currently not operational. They are original to the building and approaching the end of their lifecycles. Failure of the equipment causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the replacement of the existing water softeners/ treatment systems with new equipment. This project would also provide for a chemical treatment program including an updated chemicals control system, service and employee training provided by a qualified water treatment vendor. The annual maintenance fee charged by the water treatment vendor would be determined after an investigation of the water system is complete. These annual costs are not included in this project cost. For budgeting purposes, a $12,000 maintenance fee is suggested. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2095INT2 | JANITORS CLOSET REPAIRS | 2095 | The mop sink in the Janitors Closet is mounted adjacent to CMU and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the CMU walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2095INT3 | FLOORING REPLACEMENT | 2095 | The VCT flooring in the gymnasium is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55485
2086ADA1 | ADA SHOWER UPGRADE | 2086 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of three stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 75000
2086INT2 | SHOWER UPGRADE | 2086 | There are twelve shower stalls in the building that are showing signs of failure and should be scheduled for repair or replacement. This project would provide for twelve stainless steel shower cabinets to be installed to provide shower facilities for the housing units. Removal and disposal of the existing materials is included in the estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 300000
2097EXT2 | ROOF REPLACEMENT | 2097 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 452265
2095SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2095 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1536
2097SFT4 | FIRE ALARM SYSTEM REPLACEMENT | 2097 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 241208
2096HVA1 | HEAT PUMP REPLACEMENT | 2096 | The heat pumps in the building should be scheduled for replacement. They are not energy efficient and have reached the end of their expected and useful life. This project would provide for installation of new heat pump units and the cleaning of the existing ducting and grilles. This project includes removal and disposal of the existing heat pump units and all required connections to utilities. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 2880
2096EXT2 | EXTERIOR DOOR REPLACEMENT | 2096 | The existing exterior metal doors and frames appear to be original to the building. They are damaged and showing signs of wear and deterioration from constant use. This project would provide for the removal and replacement of two new metal door assemblies including frames, locks, hardware and painting. Removal and disposal of the existing doors and painting of the new doors is included in this estimate. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
2096SFT1 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 2096 | The building does not have emergency lighting or exit signs. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC 2012 Chapter 10 was referenced for this project. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 960
2096SFT2 | EGRESS DOOR UPGRADE | 2096 | The egress door located on south east side of the building was welded shut from the inside. IBC 2012 Section 1003.6 Obstructions shall not be placed in the required width of a means of egress. This project would provide for the removal of the welded angle iron and would cut any welds holding the door shut. This project should coincide with an Exterior Door Replacement project. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2000
2096ENR1 | LIGHTING UPGRADE | 2096 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1536
2095ENR1 | LIGHTING UPGRADE | 2095 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1536
2086EXT3 | ROOF REPLACEMENT | 2086 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 667500
2095ADA1 | ADA SHOWER UPGRADE | 2095 | This project would provide for three ADA compliant stainless steel shower cabinets to be installed to provide shower facilities for the disabled. Included in this estimate is the installation of two stainless steel ADA compliant shower cabinet units complete with accessible plumbing fixtures, seats, etc. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 50000
2095ADA2 | ADA ACCESSIBLE COUNTER | 2095 | The ADA provides for accessibility to sites and services for people with physical limitations. The lobby at the entrance of the building has a service counter for the public to approach which does not meet current requirements. Section 904.4 of the ADA Standards for Accessible Design states that a portion of the counter surface that is 36" long minimum and 36" high maximum above the finish floor shall be provided. This project will provide an accessible counter space in accordance with this requirement. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2095ADA3 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 2095 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 4000
2100PLM1 | WATER HEATER REPLACEMENT | 2100 | There is an on-demand electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new on-demand electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2086PLM1 | WATER HEATER REPLACEMENT | 2086 | There are two 18 gallon electric water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new electric water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2096SFT3 | FIRE ALARM SYSTEM REPLACEMENT | 2096 | This building is equipped with an outdated automatic fire detection and alarm system. Parts cannot be obtained and due to this, the system no longer complies with current requirements. It is recommended that the system be upgraded to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure. When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 1536
2948EXT1 | EXTERIOR FINISHES | 2948 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT #11 | 9952 | Correct | HDSP |  | Indian Springs | 2009 | 51609 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 516090
2097PLM1 | EXPANSION TANKS | 2097 | The expansion tanks in the Central Plant Boiler Room are undersized for the system which has ruptured the bladders and blown out pump seals. They were not operational at the time of survey. The system was designed to have an acceptance volume/gallon of 3,964. The existing tanks are Wassels model number NLA7500 which has an acceptance volume/gallon number 1980. This project would provide for two expansion tanks, Wassels model number NLA-15000. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350000
2172STR1 | WALKWAY RAILING | 2172 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2089EXT0 | EXTERIOR FINISHES | 2089 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for caulking all control joints and penetrations on a cyclical basis. The metal doors and window frames should also be sanded and painted a on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2089INT1 | INTERIOR FINISHES | 2089 | The interior finishes are in fair condition. It is recommended that the interior walls and floors be painted or sealed at least once in the next four to six years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2089STR1 | WALKWAY RAILING | 2089 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2088EXT1 | EXTERIOR FINISHES | 2088 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for caulking all control joints and penetrations on a cyclical basis. The metal doors and window frames should also be sanded and painted a on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2088INT1 | INTERIOR FINISHES | 2088 | The interior finishes are in fair condition. It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2088STR1 | WALKWAY RAILING | 2088 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #4 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 2500
2092LGT1 | ROOF REPLACEMENT | 2092 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 504870
2092INT1 | INTERIOR FINISHES | 2092 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 336520
2092EXT1 | EXTERIOR FINISHES | 2092 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PROGRAM SERVICES/ EDUCATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 33652 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 336520
2087EXT1 | EXTERIOR FINISHES | 2087 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide for caulking all control joints and penetrations on a cyclical basis. The metal doors and window frames should also be sanded and painted a on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2100EXT0 | EXTERIOR FINISHES | 2100 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2097EXT0 | EXTERIOR FINISHES | 2097 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 301510
2091SFT1 | CATWALKS | 2091 | The mechanical room has equipment located about 20 feet above the finish floor that need to be monitored or serviced on a regular basis. Currently the maintenance staff is using ladders or climbing on the equipment. This project would provide for the installation of 100 feet long, 2 foot wide of catwalk with guard rails and one set of stairs. All required structural supports are included in this project. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 130500
2097INT3 | INTERIOR FINISHES | 2097 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | MAINTENANCE/ CENTRAL PLANT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 30151 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 301510
2091PLM2 | GREASE WASTE INTERCEPTOR | 2091 | The automatic grease waste separator system for the Kitchen is failing to perform as intended. The system is constantly getting clogged with plastic kitchen utensils and other items disposed of by the inmates. The system has clogged and overflowed onto the floor creating a safety and health hazard. This project would provide for bypassing this equipment and having the waste go directly into the grease interceptor located below grade outside. The facility maintenance staff would have a third party vendor provide pumping services per a routine preventive maintenance schedule based on usage developed by staff to meet the demands of the system. The project cost represents an estimated yearly amount required for this service. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2091STR1 | STEAM PIPE BRACING/ SUPPORT | 2091 | During the visit to the bulk storage/ distribution area of this building, the high pressure steam pipes suspended from the ceiling were moving and shaking violently. It appears that there were surges of pressure in the steam lines that were causing a hammer-locking type condition. The pipes have vibrated badly enough that pieces of the FRP pipe insulation and the metal protective sleeves have fallen from the ceiling mounted pipes. This is a safety concern that needs to be addressed immediately. According to the original drawings, these high pressure steam pipes have 150 psig and there are special system design and inspection/ maintenance parameters and procedures that are required. This project would provide for a licensed Mechanical Engineer who specializes in steam boiler design to investigate this condition and provided a report on the conditions that are causing the condition mentioned above. Future projects would be based on this report. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 5000
2103EXT1 | EXTERIOR FINISHES | 2103 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked joints in the concrete panels, form much of the exterior surface of this building, and are uniformly deteriorated. The caulking should be removed and the joints should be re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2091PLM1 | SUMP PUMP | 2091 | The sump pump in the mechanical room portion of the building is constantly failing. The ½ H.P. pump cannot handle all of the potential water that may flow into the pit. This project recommends the installation of 1H.P. sump pump to replace the existing pump. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11500
2091ELE1 | ELECTRICAL UPGRADE | 2091 | The electrical system within the building needs to have repairs made and an inspection on the main electrical distribution panel. Light switches are broken, electrical covers missing, and parts are missing out of the electrical distribution panel. The maintenance staff said the electrical distribution panel is at or over its rating capacity. This project recommends hiring a professional licensed electrician to make repairs and determine if the main electrical distribution panel is at or over its rated capacity. Future projects would be based on the information provided. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2087STR1 | WALKWAY RAILING | 2087 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2172EXT1 | EXTERIOR FINISHES | 2172 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2087INT1 | INTERIOR FINISHES | 2087 | The interior finishes are in fair condition. It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2175EXT1 | EXTERIOR FINISHES | 2175 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 445000
2176EXT1 | EXTERIOR FINISHES | 2176 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2103INT1 | INTERIOR FINISHES | 2103 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2176INT1 | INTERIOR FINISHES | 2176 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2176ENR1 | INSULATE BUILDING | 2176 | The tower walls are structural steel with metal siding. The condenser for the cooling system is located inside on the middle level of the tower. During the summer months, the metal siding radiates heat and causes the cooling unit to trip off due to extreme temperatures. This project would provide for 4" thick foil faced rigid insulation to be installed on the inside of the guard tower to help minimize the heat gain on the interior of the guard tower. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
2102EXT1 | EXTERIOR FINISHES | 2102 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2102INT1 | INTERIOR FINISHES | 2102 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2101EXT1 | EXTERIOR FINISHES | 2101 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is power washing, priming, painting the metal panels and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended to paint the building in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2101INT1 | INTERIOR FINISHES | 2101 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2100INT1 | INTERIOR FINISHES | 2100 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2099EXT1 | EXTERIOR FINISHES | 2099 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132410
2175INT1 | INTERIOR FINISHES | 2175 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2091INT2 | INTERIOR FINISHES | 2091 | The Inmate Services/Culinary/Dining building has painted CMU walls. All flooring is sealed concrete and non-slip tile. It is recommended that the interior walls be painted and/or sealed at least once in the next 2-4 years. This also includes the sealing of the floor and floor tile maintenance in the kitchen and bakery area. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 770050
2172EXT2 | ROOF REPLACEMENT | 2172 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #8 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2174STR1 | WALKWAY RAILING | 2174 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2507SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 2507 | There is no emergency egress lighting in the warehouse sections. This project would provide for the purchase and installation of emergency egress lighting in each section. Connections to utilities are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | PRISON INDUSTRIES | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 60000 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 30000
2506SFT1 | EMERGENCY EGRESS LIGHTING INSTALLATION | 2506 | There is no emergency egress lighting in the band room or in the barber/ storage room areas. This project would provide for the purchase and installation of 2 emergency egress lights in these two rooms. Connections to existing utilities is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GYMNASIUM | 9952 | Correct | HDSP |  | Indian Springs | 2004 | 14620 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 900
2174INT1 | INTERIOR FINISHES | 2174 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2174EXT1 | EXTERIOR FINISHES | 2174 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2174EXT2 | ROOF REPLACEMENT | 2174 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2173STR1 | WALKWAY RAILING | 2173 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2173INT1 | INTERIOR FINISHES | 2173 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2173EXT1 | EXTERIOR FINISHES | 2173 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2173EXT2 | ROOF REPLACEMENT | 2173 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2002. It is recommended that this building be re-roofed in the next 4-5 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #7 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 667500
2175STR1 | WALKWAY RAILING | 2175 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #5 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2091EXT4 | EXTERIOR FINISHES | 2091 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INMATE SERVICES/ CULINARY/ DINING | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 77005 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 770050
2086STR1 | WALKWAY RAILING | 2086 | The perimeter roof walkway guardrail is failing. The railing is loose or not attached and is posing a potential safety problem. This project recommends an assessment be performed by a Structural Engineer to determine the cause and provide a design solution. Future projects will be based on the design solution recommendation. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 3000
2086EXT2 | EXTERIOR FINISHES | 2086 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
9952ENV1 | PIGEON ABATEMENT | 9952 | The site and buildings have been inhabited by pigeons. The birds introduce a potential risk of disease, cause maintenance problems with the mechanical systems and cost labor time for general clean-up. This project provides for removal and disposal of pigeon debris, eggs and carcasses from the site and buildings by a licensed pest control business. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
2177INT1 | INTERIOR FINISHES | 2177 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2178EXT1 | EXTERIOR FINISHES | 2178 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 270410
2090EXT1 | EXTERIOR FINISHES | 2090 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 329860
2178SFT2 | LOADING DOCK | 2178 | The Warehouse/ Motor Pool has a loading dock. The loading dock is used by large trucks and tractor trailers to back in for loading and unloading supplies needed for the High Desert State Prison. There are no wheel blocks installed to prevent the movement of trucks or trailers loading or unloading, per OSHA 1910.178(m)(7) requirements. The forklifts are battery operated. Per OSHA 1910.178(g)(2), the charging area for the forklifts do not provide an area for; flushing and neutralizing spilled electrolytes; for fire protection; for protecting charging apparatus; from damage by trucks, and for adequate ventilation for dispersal of fumes for gassing batteries. This project addresses the installation of blocks for the loading ramp, installation of two bollards to protect the battery charging/ flushing area in case of spills and provide adequate ventilation for dispersal of fumes for gassing batteries. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Immediate to Two Years | Currently Critical | 1 | 10000
2104EXT1 | EXTERIOR FINISHES | 2104 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked joints in the concrete panels, form much of the exterior surface of this building, and are uniformly deteriorated. The caulking should be removed and the joints should be re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2094INT1 | INTERIOR FINISHES | 2094 | It is recommended that the interior walls be painted at least once in the next 2-3 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111750
9952SIT1 | SLURRY SEAL ASPHALT PAVING | 9952 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 504,110 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HIGH DESERT STATE PRISON SITE | 9952 | Correct | HDSP |  | Indian Springs | 2000 |  | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 603138
2100ENR2 | CONDENSER DUCTING | 2100 | The condensing unit located in the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2101ENR2 | CONDENSER DUCTING | 2101 | The condensing unit located in the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #2 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2102ENR2 | CONDENSER DUCTING | 2102 | The condensing unit located in the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #3 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2176ENR2 | CONDENSER DUCTING | 2176 | The condensing unit located on the middle level of the tower is missing the duct from the outside air intake louver to the condensing unit. This may be a cause for the overheating of the unit. This project would provide for replacing this missing duct and associated connections. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | YARD TOWER | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2178INT1 | INTERIOR FINISHES | 2178 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | WAREHOUSE/ MOTOR POOL | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 37041 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 370410
2099LGT1 | ROOF REPLACEMENT | 2099 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2000. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 198615
2093EXT1 | EXTERIOR FINISHES | 2093 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111940
2177EXT1 | EXTERIOR FINISHES | 2177 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked joints in the concrete panels form much of the exterior surface of this building, and are uniformly deteriorated. The caulking should be removed and the joints should be re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #4 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Four to Ten Years | Long-Term Needs | 3 | 4550
2090INT1 | INTERIOR FINISHES | 2090 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 329860
2096EXT1 | EXTERIOR FINISHES | 2096 | It is important to maintain the finish, weather resistance and appearance of the building. The metal exterior, doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2104INT1 | INTERIOR FINISHES | 2104 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | TOWER #6 | 9952 | Correct | HDSP |  | Indian Springs | 2002 | 455 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4550
2096INT1 | INTERIOR FINISHES | 2096 | It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SALLYPORT | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 192 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
2093INT1 | INTERIOR FINISHES | 2093 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | VISITATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11194 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111940
2098INT1 | INTERIOR FINISHES | 2098 | It is recommended that the interior walls and floors be painted or sealed at least once in the next 2-3 years. Prior to painting or sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34050
2098EXT2 | EXTERIOR FINISHES | 2098 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ARMORY/ EMERGENCY RESPONSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 3405 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34050
2086INT1 | INTERIOR FINISHES | 2086 | This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | HOUSING UNIT #1 | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 44500 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 445000
2094EXT1 | EXTERIOR FINISHES | 2094 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 11175 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 111750
2090HVA1 | VENTILATION | 2090 | At the time of the survey, the mechanical room was extremely warm. It did not appear to have air conditioning or ventilation. This is causing the motors to become hot and will cause premature failure. This project recommends adding a ventilation system for proper temperature control of the mechanical room. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | INFIRMARY/ INTAKE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 32986 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2095INT1 | INTERIOR FINISHES | 2095 | It is recommended to repair, paint or seal the interior concrete block walls at least once in the 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61650
2095EXT0 | EXTERIOR FINISHES | 2095 | It is important to maintain the finish, weather resistance and appearance of the building. The caulked control joints in the CMU of the exterior surface of this building are uniformly deteriorated and should be removed and the joints re-caulked. The metal doors and window frames should be sanded and painted on a cyclical basis. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | GATEHOUSE | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 6165 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 61650
2099INT1 | INTERIOR FINISHES | 2099 | It is recommended to paint the interior walls and ceilings at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/17/2005. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/01/2016. | SECURITY/ ADMINISTRATION | 9952 | Correct | HDSP |  | Indian Springs | 2000 | 13241 | 2016-11-01 | Two to Four Years | Necessary - Not Yet Critical | 2 | 132410
0643INT2 | VCT FLOORING REPLACEMENT | 0643 | The VCT flooring in the Bunkhouse is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. 250 square feet of floor area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2250
2331EXT1 | EXTERIOR/ INTERIOR FINISHES | 2331 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2332ADA1 | ADA SIGNAGE | 2332 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
0643PLM1 | WATER HEATER REPLACEMENT | 0643 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0643INT4 | KITCHEN REMODEL | 0643 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and have approached the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
0645EXT1 | EXTERIOR FINISHES | 0645 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations and removing the dirt and rocks around the perimeter of the building. The dirt and rocks are reacting with the metal panels and causing premature deterioration of the metal. It is recommended that the work is done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
2332EXT1 | EXTERIOR/ INTERIOR FINISHES | 2332 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
0643ADA1 | ADA RESTROOM REMODEL | 0643 | The restroom in the Office is original to the building, not ADA compliant and in overall poor condition. This project would provide for a complete remodel including a wider door, new sink, toilet, plumbing jacket, shower, grab bars, floor and wall finishes and all hardware required to be ADA compliant. Minor remodeling of the space may be required. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 20010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0643SFT2 | EXIT SIGN AND EGRESS LIGHTING INSTALLATION | 0643 | The building does not have emergency lighting and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 1250
2333EXT1 | EXTERIOR FINISHES | 2333 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | RAMADA #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 140 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2334EXT1 | EXTERIOR FINISHES | 2334 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | RAMADA #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 140 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2335EXT1 | EXTERIOR FINISHES | 2335 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | RAMADA #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 140 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 560
2330ADA1 | ADA SIGNAGE | 2330 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
0644EXT1 | EXTERIOR FINISHES | 0644 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is cleaning the vinyl siding and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be cleaned and caulked in the next 5-7 years and that this project is scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 1000
2327EXT1 | EXTERIOR/ INTERIOR FINISHES | 2327 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #3 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2329EXT1 | EXTERIOR/ INTERIOR FINISHES | 2329 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #5 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2329ADA1 | ADA SIGNAGE | 2329 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #5 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2328EXT1 | EXTERIOR/ INTERIOR FINISHES | 2328 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #4 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
2331ADA1 | ADA SIGNAGE | 2331 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2327ADA1 | ADA SIGNAGE | 2327 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #3 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2330EXT1 | EXTERIOR/ INTERIOR FINISHES | 2330 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | BLM RESTROOM #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
2326ADA1 | ADA SIGNAGE | 2326 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #2 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2326EXT1 | EXTERIOR/ INTERIOR FINISHES | 2326 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #2 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0942EXT1 | EXTERIOR FINISHES | 0942 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SEED SILO | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1120
0643EXT1 | EXTERIOR FINISHES | 0643 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations and removing the dirt and rocks around the perimeter of the building. The dirt and rocks are reacting with the metal panels and causing premature deterioration of the metal. It is recommended that the work is done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
0643INT1 | INTERIOR FINISHES | 0643 | It is recommended that the interior walls and ceilings be painted at least once in the next two to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
2325ADA1 | ADA SIGNAGE | 2325 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #1 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
2325EXT1 | EXTERIOR/ INTERIOR FINISHES | 2325 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #1 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0945EXT1 | EXTERIOR FINISHES | 0945 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0943EXT1 | EXTERIOR FINISHES | 0943 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations and removing the dirt and rocks around the perimeter of the building. The dirt and rocks are reacting with the metal panels and causing premature deterioration of the metal. It is recommended that the work is done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
0642INT1 | INTERIOR FINISHES | 0642 | It is recommended that the interior walls and ceilings be painted at least once in the next three to four years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA RESIDENCE | 9953 | Wildlife |  |  | Kirch WMA | 1964 | 1900 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19000
2328ADA1 | ADA SIGNAGE | 2328 | ADA regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | CXT RESTROOM #4 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450
0945EXT2 | EXTERIOR SIDING REPLACEMENT | 0945 | The corrugated metal panels covering the building are original and should be scheduled for replacement. Many of the panels are damaged from general wear and tear. This project would provide for the removal and the disposal of the existing panels and the replacement with new pre-painted metal panels. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5100
2329ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2329 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #5 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2328ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2328 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #4 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2326ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2326 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #2 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0945ENV1 | SPILL CONTAINMENT | 0945 | The Equipment Shed does not have a method for containing spills or leakage from drums. This project would add secondary containment pallets for all containers in the building and install placards on the building exterior. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 6500
3677EXT1 | EXTERIOR FINISHES | 3677 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 16500
0943SFT1 | SAFETY CABINETS | 0943 | The building contains many different herbicides, pesticides and other hazardous products located on open shelves and on the floor. This does not meet OSHA standards or IFC for hazardous materials containment. This project would provide for two self-closing hazardous storage containers in the building and install placards on the building’s exterior in accordance with OSHA 1910.106 (d) and IFC Chapter 57 Section 5704.3.2.1.3. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 10000
2327ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2327 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | CXT RESTROOM #3 - CAMPGROUND | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 120 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
3677INT1 | INTERIOR FINISHES | 3677 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 16500
3677SIT1 | REMOVE SPRINKLERED LAWN WITHIN 3' OF BUILDING | 3677 | The house has considerable damage to the siding from lawn sprinklers wetting the siding. This project would create drip irrigated planters within three feet of the house and relocate sprinklers so they do not wet the house. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6600
3677ENV1 | PEST CONTROL | 3677 | There are numerous rodent droppings in the crawl space throughout this building. Due to the potential risk of disease, this project provides for treatment and clean up of the rodent droppings by a licensed pest control business. | RESIDENCE #2 | 9953 | Wildlife |  |  | Kirch WMA | 2013 | 1650 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 1000
9953ADA1 | BOAT DOCK AND RAMP REPLACEMENT | 9953 | The boat docks and concrete ramps are approaching the end of their expected life and should be scheduled for replacement due to extreme climatic conditions and use. The concrete ramps are cracking and spalling. It is important for the concrete to be in good shape to insure proper traction for tow vehicles and to prevent accidents. This project would provide for the purchase and installation of 3 new ADA compliant boat docks and concrete ramps. Removal and disposal of the existing concrete ramps and docks are included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 450000
0943SFT2 | EXPLOSION PROOF INTERIOR LED LIGHTING | 0943 | The existing lighting fixtures are the incandescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with longer life cycles and will be explosion proof. 4' LEDs in class 1 explosion proof fixtures are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
2332ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2332 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BLM RESTROOM #3 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0943ENV1 | HAZARDOUS MATERIALS STORAGE UPGRADE | 0943 | The Chemical Storage Shed contains hazardous materials (i.e. herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | CHEMICAL STORAGE SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 240 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2331ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2331 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BLM RESTROOM #2 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
2330ADA2 | ADA ACCESSIBLE PATH OF TRAVEL | 2330 | The ADA provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the restroom are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the existing sidewalk. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. 750 square feet of concrete was used for this estimate. | BLM RESTROOM #1 | 9953 | Wildlife |  |  | Kirch WMA | 2000 | 70 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
9953SIT8 | HAZARDOUS COMMUNICATION PROGRAM | 9953 | Due to the storage of hazardous materials, this site shall comply with IFC 2012 Chapter 4 Emergency Planning and Preparedness, and have a written Hazardous Materials Management Plan, including but not limited to, Section 5003 Safety Data Sheets, Section 406 Employee Training and Response Procedures and Section 407 Hazard Communication. Chapter 50 Section 5001 will provide additional assistance in devising and implementing a hazardous communication program. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0642EXT5 | EXTERIOR FINISHES | 0642 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming, painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | KIRCH WMA RESIDENCE | 9953 | Wildlife |  |  | Kirch WMA | 1964 | 1900 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 19000
0645ENV1 | HAZARDOUS MATERIALS STORAGE | 0645 | The Oil Storage Building contains hazardous materials (i.e. gas, batteries, herbicides and pesticides). Per IFC 2012 Hazardous Materials, and in accordance with NFPA; where hazardous materials are stored, dispensed or used, Section 5003 states the proper use and application is to have mechanical exhaust and ventilation, and hazard identification signs shall be installed. Refer to Section 5004 and 5005 for the proper use and setup. It is important to comply with all applicable codes. This project would provide for all requirements in IFC 2012, to include Section 105 permits and inspections through the State Fire Marshal’s Office and the State Public Works Division. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 30000
0643ADA2 | ADA SIGNAGE & STRIPING | 0643 | The ADA provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards for Accessible Design were used as references for this project. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 3500
0643SFT3 | SMOKE AND CARBON MONOXIDE ALARM INSTALLATION | 0643 | Section 907.2.11 of the 2012 IBC and 2012 IFC explains the requirements for smoke alarms in dwelling units including installing and maintaining smoke alarms in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. IFC 2012 Section 908.7 carbon monoxide alarms group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with single-station carbon monoxide alarm. The carbon monoxide alarm shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. State Fire Marshal NAC 477.915 (3) requires that smoke detectors and carbon monoxide alarms be connected to the wiring of the building with a battery backup. This project would provide funding for the purchase and installation of a smoke alarm and combo smoke alarm and carbon monoxide alarm in accordance with these codes. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2500
0643EXT3 | CONCRETE APRON INSTALLATION | 0643 | The building has two vehicle garage doors that don’t have exterior concrete aprons. This project would provide for the installation of two new 4" thick concrete slab-on-grade aprons at the vehicle garage doors. Removal and disposal of the existing concrete is included in this estimate. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 2400
0643EXT2 | ROOF REPLACEMENT | 0643 | The standing seam metal roof on this building was in poor condition at the time of the survey and had active leaks. It is recommended that this building be re-roofed in the next 1-2 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 15000
9953SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 9953 | There is a set of stairs on the west side of the office which are lacking handrails. This project would provide for the installation of a 1-1/2 inch tube steel handrail to be installed on each side of the stairs. Chapter 10 of the 2012 IBC was used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 5000
0643ELE2 | ELECTRICAL AND COMMUNICATIONS UPGRADE | 0643 | This building was constructed before the high demand for electrical services were needed for computers, communications systems and other electrical devices. As time has progressed, the buildings electrical demand and communications system has changed. The electrical system is utilized to its current maximum potential and the communications system is outdated. The electrical panels, switches and receptacles are at their limit. It is recommended to upgrade the entire electrical system and communications system to meet the evolving needs of the building. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31250
0643ELE1 | GFCI DUPLEX OUTLET REPLACEMENT | 0643 | There are several outlets in the restroom, kitchen and garage that are not GFCI protected. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of GFCI duplex outlets. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0643ENR1 | LIGHTING UPGRADE | 0643 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
0643SFT4 | SITE BOLLARDS | 0643 | The building has a propane tank that provides fuel for the heaters. The propane tank does not have adequate bollard coverage. Per IFC 2012 Section 312 Vehicle Impact Protection, there needs to be steel posts installed, not less than 4 inches in diameter and filled with concrete. The spacing shall not be more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for eight new bollards to be located around the other bollards. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 8000
0945EXT3 | ROOF REPLACEMENT | 0945 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | EQUIPMENT SHED | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 1200 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0642INT2 | INTERIOR REMODEL AND FIRE SUPPRESSION | 0642 | The interior fixtures and finishes are in general disrepair and the building is due for a complete remodel. This project would provide for the removal and replacement of the flooring, doors and frames, cabinetry, trim and baseboards and any other interior finishes and fixtures in need of replacement. When a remodel is conducted per 2012 IBC, NAC 477.915 (2) states, R occupancy, be scheduled for installation of an automatic fire suppression system during the next remodeling of or addition to the building. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | KIRCH WMA RESIDENCE | 9953 | Wildlife |  |  | Kirch WMA | 1964 | 1900 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 123500
0643SFT1 | SEISMIC GAS SHUT-OFF VALVE INSTALLATION | 0643 | This project would provide for the installation of a seismic gas shut-off valve on the main gas service piping just prior to entering the building. This estimate is based on the manufacturer Pacific Seismic Products or approved equal, equipped with the optional Model MS remote monitoring switch (to be interfaced with the direct digital control system and/or with an audible alarm). The gas piping immediately adjacent to the seismic gas valve shall be secured to the building utilizing unistrut channel bracing. | SHOP/ BUNKHOUSE/ OFFICE | 9953 | Wildlife |  |  | Kirch WMA | 1969 | 1250 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 4000
0644ELE3 | GFCI OUTLETS | 0644 | The existing receptacles in the Kirch WMA Pump House and outside are standard duplex receptacles. The 2011 (NEC) National Electrical Code 210.8 requires these locations to have Ground Fault Circuit Interrupter (GFCI) protection. This project would provide for removing the standard receptacles and installing GFCI receptacles. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 800
0644ELE2 | LIGHTING UPGRADE | 0644 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 800
0644EXT2 | ROOF REPLACEMENT | 0644 | The asphalt roll roofing was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new single-ply roofing system. This will allow the roof to qualify for the statewide roofing warranty and preventative maintenance agreement programs. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 1200
0644SFT1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0644 | There is an electrical panel in the building which does not have the proper floor clearance. The 2012 IFC Section 605.3 states, a working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches, the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space. This project would provide funds to relocate the shelf and other items currently blocking the working space. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
0644ELE1 | WIRING CLEANUP | 0644 | The wiring in the Kirch WMA Pump House is disorganized and not in proper electrical boxes. This creates a safety issue during repairs or upgrades. This project would provide for organization, proper labeling and for the wiring to be placed in electrical boxes per NEC 2011. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0644INT2 | INTERIOR FINISHES | 0644 | It is recommended to paint the interior walls and ceilings at least once in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and adequately prepared to receive the coating. An epoxy-based paint should be utilized in wet areas for durability. | KIRCH WMA PUMP HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1992 | 100 | 2016-06-08 | Four to Ten Years | Long-Term Needs | 3 | 1000
0645ENV2 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 0645 | At the time of the survey, there were oil drums stored in the Oil Storage Building as well as propane tanks, gas cans and aerosol cans stored in the same area. This does not meet OSHA standards for proper storage containment. The oil drums should be stored on OSHA approved drum spill pallets in order to protect the environment from spills or leaks. The project will provide for two OSHA approved drum spill pallets capable of storing two drums each and purchasing an OSHA approved storage cabinet for miscellaneous items such as the gas cans. According to OSHA 1910.106 (d), a proper storage container shall be provided for flammable or combustible liquids in drums or other containers (including flammable aerosols) not exceeding 60 gallons individual capacity and those portable tanks not exceeding 660 gallons individual capacity. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 15000
0645SFT2 | BATTERY STORAGE | 0645 | Section 608 of the 2012 IFC explains the requirements for stationary storage of battery systems. This project will provide funding for the proper way to store, charge and/or use batteries indoors. IFC Section 608 states batteries shall have safety caps, spill control and neutralization, mechanical ventilation and/or cabinet ventilation, supervision over the mechanical ventilation, building or cabinet signage, seismically braced, and a smoke alarm. This project would provide funding for the requirement of Section 608 of the 2012 IFC. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 25000
0645SFT1 | EXPLOSION PROOF INTERIOR LED LIGHTING | 0645 | The existing lighting fixtures are the incandescent type, and are not energy efficient or explosion proof. This project will upgrade fixtures to higher efficiency units with longer life cycles and will be explosion proof. 4' LEDs in class 1 explosion proof fixtures are suggested. Occupancy sensors will be installed for additional savings. Electrical wiring upgrades have not been included in this estimate. | OIL STORAGE BUILDING | 9953 | Wildlife |  |  | Kirch WMA | 1960 | 150 | 2016-06-08 | Immediate to Two Years | Currently Critical | 1 | 2000
9953SIT6 | FENCE REPLACEMENT | 9953 | This site is home to some endangered species. The habitat is tightly managed to protect them. Feral horses and stray cattle must be kept out. The perimeter fencing for the wildlife management area is a juniper pole fence, which is aging. The fence posts are losing their integrity and failing. This project recommends replacing the fence with steel posts and wildlife stranded wire. The estimate is based on approximately 50 miles of fencing. This project or a portion thereof was previously recommended in the FCA report dated 05/24/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300000
9953SIT5 | IRRIGATION SYSTEM REPLACEMENT | 9953 | The campground is served by a well, which provides water for campers and the irrigation. A drip irrigation system was installed at the campground to provide water for trees and shrubs, but problems with water quality and other issues adversely affected the effectiveness of the system. This project recommends removing the existing system and replacing it with a new drip irrigation system including backflow prevention, filters, and self-cleaning bubblers and valves. Following installation, trees and shrubs should be reintroduced to the campground area. This project or a portion thereof was previously recommended in the FCA report dated 05/24/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9953SIT2 | ACCESS BRIDGE REPLACEMENT | 9953 | The Tule access bridge crosses a ditch at the site, providing access to the opposite side of the site for recreation. The structure is older, in poor condition, and could become a safety issue. This project recommends the installation of a concrete box culvert and walkway to replace the bridge. The new installation will last longer and be less susceptible to damage by water flows. This project or a portion thereof was previously recommended in the FCA report dated 05/24/2002 and 09/29/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/08/2016. | KIRCH WMA SITE | 9953 | Wildlife |  |  | Kirch WMA |  |  | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
2337EXT1 | HISTORIC BUILDING MAINTENANCE | 2337 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOG RANCH BUILDING #2 | 9953 | Wildlife |  |  | Kirch WMA | 1920 | 700 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0944EXT1 | HISTORIC BUILDING MAINTENANCE | 0944 | The wood structure is over 87 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SLAUGHTER HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1930 | 700 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
2336EXT1 | HISTORIC BUILDING MAINTENANCE | 2336 | The wood structure is over 75 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LOG RANCH BUILDING #1 | 9953 | Wildlife |  |  | Kirch WMA | 1920 | 460 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6900
0941EXT1 | HISTORICAL BUILDING MAINTENANCE | 0941 | The wood structure is over 87 years old and there are numerous areas where the wood is splitting, warping and deteriorating. This is also an exhibit for the park and requires maintenance. This project would provide for sealing the wood and repairing the roof as needed. This project should be coordinated with the Nevada State Historical Preservation Office for possible restrictions or requirements, which are not included in this estimate. It is recommended that the work be done in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD RANCH SCHOOL HOUSE | 9953 | Wildlife |  |  | Kirch WMA | 1930 | 650 | 2016-06-08 | Two to Four Years | Necessary - Not Yet Critical | 2 | 665
0903INT2 | RESTROOM REMODEL | 0903 | One of the two restrooms in the residence is original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restroom. The removal and disposal of the existing fixtures and finishes is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
0647ENR3 | EXTERIOR EIFS INSTALLATION | 0647 | The Maintenance Shop is an uninsulated concrete masonry unit structure. This project would provide for the installation of an exterior insulation and finish system which would reduce energy consumption resulting in energy cost savings. This project is recommended to be done in conjunction with the HVAC and lighting upgrade projects. An acrylic based finish is recommended due to the climate and extreme temperature fluctuations. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14400
0647INT1 | INTERIOR FINISHES | 0647 | The interior finishes are in fair condition. It is recommended that the interior CMU walls be sealed at least once in the next two to four years. Prior to sealing, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0647EXT2 | ROOF/ STRUCTURE REPLACEMENT | 0647 | The roof framing and the rolled asphalt roofing on this building were in poor condition at the time of the survey. The framing is rotted and failing particularly noticeable at the main ridge beam which is cracked. It is recommended that the entire roof structure be replaced including structural supports and a new composition roofing system including the underlayment. This estimate includes removal and disposal of the old framing and roofing system. Engineering of the roof structure will be required and a $5,000 allowance is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 101841
0647ENR1 | WINDOW REPLACEMENT | 0647 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 3 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 4500
0647ENR2 | LIGHTING UPGRADE | 0647 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0903ENR1 | WINDOW REPLACEMENT | 0903 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 21 units and includes replacing the wood trim around each unit. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 31500
0903SFT1 | EXTERIOR STAIR REPLACEMENT | 0903 | The exterior concrete stairs near the garage do not comply with 2012 IBC Chapter 10. The treads and risers are not uniform in size and the stairway is missing handrails. This project would provide for the installation of a compliant stairway including handrails. Removal and disposal of the existing stairs is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 9000
0903SFT2 | INTERIOR DOOR REPLACEMENT | 0903 | The door to the stairway leading to the basement swings out over the stairs. This is a safety hazard and does not comply with 2012 IBC Chapter 10. This project would provide for reversing the swing on the door. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 1000
0903SFT3 | INTERIOR STAIR HANDRAIL REPLACEMENT | 0903 | The handrails for the stairway to the basement are older, not safe and do not meet code. The gripping surfaces are incorrect and they are installed on only one side of the stairs. This project recommends the installation of handrails on both sides of the stairs, proper returns and supports in accordance with the 2012 IBC Chapter 10, Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 12000
0903ENR2 | LIGHTING UPGRADE | 0903 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade the fixtures to higher efficiency units with a longer life cycle. Compact fluorescent lamps are suggested. Electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9600
0903SFT4 | SMOKE ALARM INSTALLATION | 0903 | IRC 2012 Section R314 and R315.3 explains the requirements for smoke alarms in dwelling units. This includes: installing and maintaining smoke alarms in each sleeping room; having a carbon monoxide and smoke detector on the ceiling or wall outside of each sleeping area; in the immediate vicinity of bedrooms when an alteration, repair or addition requiring a permit occurs. IRC 2012, requires that smoke detectors and carbon monoxide alarms be UL rated. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the wiring in a building and include a battery for emergency backup power. This project would provide funding for the purchase and installation of smoke alarms and carbon monoxide alarms in accordance with IRC and NAC laws. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 2000
0903INT3 | CONCRETE REPAIRS | 0903 | The concrete floor and walls in the basement are damaged from water infiltration and heaving. There are cracks and stains that should be repaired and cleaned. It is recommended that the concrete be cleaned and repaired in order to extend its useful life. This project would provide for cleaning the concrete, filling in the cracks and applying a coat of sealant. It is recommended that this project be completed in the next 2-3 years. This project should be implemented after the Drainage Improvements project to ensure that future damage does not occur. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
0647HVA1 | HVAC INSTALLATION | 0647 | The building has no central cooling or heating system and is uncomfortably warm in the summer and cold in the winter. It is recommended to install a 3 ton fuel fired packaged HVAC unit complete with ducting, diffusers as required and connection to the existing fuel tank. This project should be coordinated with the exterior EIFS system installation project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
0648EXT1 | EXTERIOR FINISHES | 0648 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CHICKEN COOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 168 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1680
3028ADA1 | ADA SIGNAGE & STRIPING | 3028 | The ADA provides for accessibility to sites and services for people with physical limitations. The concrete parking area and passenger loading area are missing proper signage and striping to comply with ADA requirements. This project would provide for striping, signage and any other necessary upgrades to the parking space. NRS 338.180, IBC - 2012, ICC/ANSI A117.1 - 2009 and Americans with ADAAG - 2010 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CXT COMFORT STATION #2 - NORTH | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 112 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 3500
0903EXT1 | EXTERIOR FINISHES | 0903 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0904EXT1 | EXTERIOR FINISHES | 0904 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are cleaning and sealing the concrete and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | GRANARY | 9954 | Wildlife |  |  | Key Pittman WMA |  | 177 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1770
0904EXT2 | ROOF REPLACEMENT | 0904 | The roof framing and the corrugated metal roofing on this building were in poor condition at the time of the survey. The framing is rotted and many wood members are splitting. It is recommended that the framing and roofing be replaced in the next 2-3 years. This estimate includes removal and disposal of the old framing and roofing system. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | GRANARY | 9954 | Wildlife |  |  | Key Pittman WMA |  | 177 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2655
2942EXT1 | EXTERIOR/ INTERIOR FINISHES | 2942 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CXT COMFORT STATION #1 - SOUTH | 9954 | Wildlife |  |  | Key Pittman WMA | 2007 | 56 | 2017-04-06 | Four to Ten Years | Long-Term Needs | 3 | 1120
3029EXT1 | EXTERIOR FINISHES | 3029 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3029SFT1 | SAFETY CABINETS | 3029 | The storage building contains many different paints, stains, pesticides and other hazardous products on open shelves and on the floor. This does not meet OSHA standards for hazardous materials containment. This project would provide two hazardous storage containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Immediate to Two Years | Currently Critical | 1 | 5000
0903HVA1 | HVAC EQUIPMENT REPLACEMENT | 0903 | The HVAC system is original to the building and should be scheduled for replacement. It is not energy efficient and has reached the end of its expected and useful life. The R-22 refrigerant in the cooling system is no longer EPA complaint and its production is mandated to be phased out completely by January 1, 2020. This project would provide for installation of a new HVAC system and cleaning of the existing duct work and grilles. This project includes the removal and disposal of the existing HVAC system and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
3028EXT1 | EXTERIOR/ INTERIOR FINISHES | 3028 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/22/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/13/2016. | CXT COMFORT STATION #2 - NORTH | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 112 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2240
0647SFT1 | EXTERIOR LANDING INSTALLATION | 0647 | There is an out-swinging exterior door from the building which swings out over a step and does not have a landing that complies with IBC 2012. IBC Section 1008 requires a landing to be not more than 1/2" below the threshold. This project would provide for the installation of a compliant landing for the door. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
0903ENV1 | PEST CONTROL | 0903 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0647ENV1 | PEST CONTROL | 0647 | There are numerous rodent droppings throughout this building. Due to the potential risk of disease, this project provides for treatment and cleanup of the rodent droppings by a licensed pest control business. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0647EXT3 | OVERHEAD DOOR REPLACEMENT | 0647 | There are two overhead coiling doors which are damaged and do not function properly. Exposure and wind have caused the doors to bend, crack and lose their finish. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the manually operated overhead coiling doors and replacement with new manually operated overhead coiling doors. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0647SIT1 | TREE AND SHRUB PRUNING/ REMOVAL | 0647 | There are several trees that are in need of removal to prevent damage to the Maintenance Shop. This project would provide for the trimming and/ or removal of the trees along the Maintenance Shop building and removal of the trees along the fence line. | MAINTENANCE SHOP | 9954 | Wildlife |  |  | Key Pittman WMA |  | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
0904SFT1 | EXTERIOR LANDING INSTALLATION | 0904 | Section 1008.1 of the 2012 IBC describes the requirements for doors including floor elevations and landings. The floor or landing shall be at the same elevation on each side of the door, the exterior landing shall not exceed a 2-percent slope and shall have a length measured in the direction of travel of not less than 44 inches. The landing at the door on the building does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | GRANARY | 9954 | Wildlife |  |  | Key Pittman WMA |  | 177 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3029ENR1 | LIGHTING UPGRADE | 3029 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. 5,000K LED lamps, without the ballasts, are suggested, and new tombstones (if needed). Occupancy sensors will be installed in low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 350
3029ELE1 | GFCI OUTLETS | 3029 | The existing receptacle is a standard duplex receptacle. The 2011 NEC 210.8 requires this location shall be GFCI protected. This project would provide for removing the standard receptacle and installing a GFCI receptacle. | WMA STORAGE BUILDING | 9954 | Wildlife |  |  | Key Pittman WMA | 0 | 300 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 400
0903PLM1 | WATER HEATER REPLACEMENT | 0903 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SUPERVISOR'S RESIDENCE | 9954 | Wildlife |  |  | Key Pittman WMA | 1959 | 1200 | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
9954ELE1 | WIRING CLEANUP | 9954 | The wiring at the electrical panel feeding the wellhead is disorganized, not in conduit, and does not have exterior grade cover plates or boxes. This creates a safety issue due to the moist environment. This project would provide for wiring organization and placement into electrical boxes, conduit to be added and for the proper labeling per NEC 2011. | KEY PITTMAN WMA SITE | 9954 | Wildlife |  |  | Key Pittman WMA | 0 |  | 2017-04-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
0302EXT1 | EXTERIOR ENERGY RETROFIT | 0302 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | SAND SPRINGS STATION #5(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0305EXT1 | EXTERIOR ENERGY RETROFIT | 0305 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | BUCKLAND STATION #4(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1965 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49000
0303EXT2 | REPLACE ROOF | 0303 | The roof on this building was in poor condition at the time of the survey. Recent storms damaged the roof, there are missing shingles, and active leaks are reported by the occupants. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed in the next year to be consistent with the roofing program and the end of the warranty period. Additional monies are included to replace some fascia and missing attic vent screens. | B&G CLUB/HISP SERVICES #10(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 15000
0303EXT1 | EXTERIOR FINISHES | 0303 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | B&G CLUB/HISP SERVICES #10(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 8000
0300EXT1 | EXTERIOR ENERGY RETROFIT | 0300 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with an exterior mounted, removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | RUBY STATION #2(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
9955SIT5 | REMOVE PLANTERS | 9955 | Several buildings at the site have planters that are elevated a few feet up onto the exterior wall. This practice promotes water infiltration through the side of the building and has been known to cause mold growth along the exterior walls of buildings. There is evidence of recurring water damage on the interior wall finishes in several locations. This project recommends that the planters be removed as soon as possible. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 5000
9955PLM1 | INSTALL WATER SHUT-OFF VALVES TO EACH BUILDING | 9955 | The site has a central water shut-off. In the event that plumbing work needs to be done that requires the water to be turned off, most of the buildings on the site are without water. The Uniform Plumbing Code (UPC) states in Section 605.2, "...water piping supplying more than one building on any one premises shall be equipped with a separate full way valve to each building, so arranged that the water supply can be turned on or off to any individual or separate building..." It is recommended that a shut-off valve be installed on the remainder of the buildings that have water service to them. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 30000
9955SIT1 | INSTALL EXTERIOR SITE LIGHTING | 9955 | This project recommends installing general security lighting fixtures around the parking areas and paved portions of the site. Cost includes light fixtures, wiring, trenching and installation, based on a 20 foot pole. Work should be performed prior to or concurrent with parking lot replacement. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 30000
9955SIT3 | SIDEWALK REPLACEMENT | 9955 | The existing sidewalks serving buildings on this site have deteriorated and are failing. In some areas cracks wider than four inches have been identified, and there is substantial settling in a number of locations. This project addresses removal and replacement of existing sidewalks as needed. The sidewalks should include flared curb cuts for site accessibility. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 140000
9955ADA1 | ADA PARKING RE-STRIPING | 9955 | The accessible parking area striping is fading, and is becoming difficult to identify. The area does not have the proper signage identifying the parking space as accessible. CABO/ANSI A117.1 - 1992 Section 4.6.2 states, "...accessible parking spaces shall be identified by a sign showing the international symbol of accessibility..." The lot will be re-striped and accessible routes of travel identified. This project covers up to 4 spaces. Signage is included. ADA parking is required at the front parking lot, serving the Boys and Girls Club, Volunteers of America and Hispanic Services, and the rear parking lot, serving Child and Family Services offices. These costs were developed from the RS Means ADA Compliance Pricing Guide. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 4000
0295ENR1 | LIGHTING UPGRADE | 0295 | The building lighting fixtures are older T-12 fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Sensors will be installed in restrooms and other low occupancy areas for additional savings. | BOYS & GIRLS CLUB GYM #12(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0302EXT2 | REPLACE ROOF | 0302 | The existing roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed consistent with the roofing program and the end of the warranty period. | SAND SPRINGS STATION #5(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
9955SIT2 | REPLACE ASPHALT PAVING | 9955 | The asphalt at the site is failing, with significant alligatoring and cracks observed. The macadam has deteriorated to the point that it is no longer viable. This project covers the removal and replacement of existing blacktop for parking and site access, and additional parking at the main parking areas. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 300000
0297EXT1 | EXTERIOR FINISHES | 0297 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | REHAB BUILDING #3(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8500
0304LGT1 | LONG-TERM NEEDS | 0304 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | MTN. SPRINGS STATION #1(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1963 | 2425 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 24000
0301LGT1 | LONG-TERM NEEDS | 0301 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0301ELE1 | MINOR ELECTRICAL UPGRADE | 0301 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0301EXT2 | REPLACE ROOF | 0301 | The existing roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. It is recommended that this building be re-roofed consistent with the roofing program and the end of the warranty period. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 14000
0307EXT1 | EXTERIOR FINISHES | 0307 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will not be needed if the asbestos containing siding is abated and replaced. | GARAGE #13(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2000 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
2313EXT91 | EXTERIOR FINISHES | 2313 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | QUONSET #14(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 500 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9955LGT1 | LONG-TERM NEEDS | 9955 | Projects in this category address possible long term needs of the site. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. This project accounts for possible system repair or replacement, and cyclical maintenance, including the parking lots, sidewalks, fences, and other site systems. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 100000
0295PLM1 | REPLACE WATER HEATERS | 0295 | The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear. It is recommended that new on-demand appliances be installed for efficient use of energy. | BOYS & GIRLS CLUB GYM #12(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 2000
0304EXT1 | EXTERIOR ENERGY RETROFIT | 0304 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | MTN. SPRINGS STATION #1(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1963 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 49000
0307LGT1 | LONG-TERM NEEDS | 0307 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | GARAGE #13(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2000 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 10000
0301EXT1 | EXTERIOR ENERGY RETROFIT | 0301 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with a removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | VOA FOSTER CARE HOUSING #6(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0299LGT1 | LONG-TERM NEEDS | 0299 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | FRIDAY STATION #11(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0299EXT1 | EXTERIOR ENERGY RETROFIT | 0299 | The building is constructed of concrete masonry units (CMU) with no insulation. The windows are original to the building, and of single pane construction. Buildings of this type are not energy efficient. This project recommends adding an exterior insulating finish system (EIFS) over the CMU, augmenting the windows with an exterior mounted, removable storm-type window system, and replacing the exterior doors. This work will make the building more energy efficient. If the EIFS system is not installed, the building will require exterior finishes, caulking around windows and doors, and similar improvements. This work should be performed following surface preparation and repair or replacement of fascias and overhangs. Costs would run approximately $5.00 per square foot. | FRIDAY STATION #11(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 56000
0299ELE1 | MINOR ELECTRICAL UPGRADE | 0299 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | FRIDAY STATION #11(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
9955PLM2 | BACKFLOW ASSEMBLY, VAULT, AND POWER | 9955 | State Health law now mandates backflow prevention on domestic water lines and fire sprinkler or standpipe lines. This project makes allowance for installation of a 6" reduced pressure backflow prevention assembly, required fittings, an above ground vault, and allowance for 200 feet of 1" conduit to provide power for the required heat source inside the vault. This installation will serve the site. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 26000
0295EXT2 | REROOF BUILDING | 0295 | The roof is showing signs of wear and deterioration, and is reaching the end of its useful life. This report recommends that the roof be replaced. | BOYS & GIRLS CLUB GYM #12(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 29000
0298LGT1 | LONG-TERM NEEDS | 0298 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | ICE HOUSE #7(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1950 | 1700 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 17000
0297EXT2 | REPLACE ROOF | 0297 | The existing roof on this building was in poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. This roof appears to be at least that old. It is recommended that this building be re-roofed consistent with the roofing program and the end of the warranty period. | REHAB BUILDING #3(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0304ELE1 | MINOR ELECTRICAL UPGRADE | 0304 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | MTN. SPRINGS STATION #1(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1963 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
9955SIT7 | SITE DRAINAGE ISSUES | 9955 | A number of the buildings have moisture damage due to improper drainage. The offices have problems with irrigation runoff, rain and snow melt collecting in the courtyards or draining into the crawl spaces under the buildings. The courtyard concrete patios are cracked and buckling, which adds to these problems. This project recommends gutters be installed, courtyard patios demolished and re-poured, and the grade re-worked to promote drainage away from the buildings. Additional work will be required to transport the drainage to a storm drain or other system to minimize localized flooding. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 150000
0294HVA1 | REPLACE HVAC SYSTEM | 0294 | The building has an older HVAC system, which appears to be original to the building. The boiler is not operational, and has been disconnected, and this project recommends replacing the system. Most of the building rely on windows cooling units, which is not recommended under current energy guidelines. New hot water heaters and ducting will be needed. | BOYS & GIRLS CLUB #9(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 137000
0305ELE1 | MINOR ELECTRICAL UPGRADE | 0305 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | BUCKLAND STATION #4(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1965 | 2425 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0302ELE1 | MINOR ELECTRICAL UPGRADE | 0302 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | SAND SPRINGS STATION #5(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
0300ELE1 | MINOR ELECTRICAL UPGRADE | 0300 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | RUBY STATION #2(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
9955SIT4 | TRIM OR REMOVE TREES ADJOINING BUILDINGS | 9955 | Several of the buildings have trees which are growing up against the structures. The trees move in windy conditions, rubbing the roofs, which can cause premature failure of system and voiding roof warranties. The root systems are causing shifting and heaving of foundations and sidewalks, creating unsafe conditions. There are also several large trees that are in need of trimming. This lack of maintenance could become a safety issue. There were numerous branches on the ground at the time of survey and damage to a fence had occurred due to a falling tree. This project recommends that these issues be addressed, before additional damage is done. Carson City is responsible for site landscaping and maintenance, and there may be some cost sharing or savings working with city staff to address this issue. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 25000
0305LGT1 | LONG-TERM NEEDS | 0305 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | BUCKLAND STATION #4(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1965 | 2425 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 24000
0302LGT1 | LONG-TERM NEEDS | 0302 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | SAND SPRINGS STATION #5(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0300LGT1 | LONG-TERM NEEDS | 0300 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | RUBY STATION #2(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2760 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 28000
0294LGT1 | LONG-TERM NEEDS | 0294 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | BOYS & GIRLS CLUB #9(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 23000
0294ENR1 | LIGHTING UPGRADE | 0294 | The building lighting fixtures are older T-12 fluorescent types and not energy efficient. This project will upgrade lighting fixtures to T-8 lamps with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. Sensors will be installed in restrooms and other low occupancy areas for additional savings. | BOYS & GIRLS CLUB #9(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0295LGT1 | LONG-TERM NEEDS | 0295 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | BOYS & GIRLS CLUB GYM #12(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 15000
0294EXT1 | EXTERIOR FINISHES | 0294 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. This project will not be needed if the asbestos containing siding is abated and replaced. | BOYS & GIRLS CLUB #9(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0297LGT1 | LONG-TERM NEEDS | 0297 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | REHAB BUILDING #3(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 25000
0297SFT1 | INSTALL EMERGENCY EGRESS LIGHTING | 0297 | There are older emergency egress lighting in this building. These units have a finite lifespan, and this project recommends the installation of new egress lights along the main exit routes when reoccupying the building.. | REHAB BUILDING #3(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1975 | 2400 | 2003-01-10 | Immediate to Two Years | Currently Critical | 1 | 4000
0303LGT1 | LONG-TERM NEEDS | 0303 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for scheduled replacement of flooring, water heaters, HVAC, and the like. | B&G CLUB/HISP SERVICES #10(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 23000
0303ELE1 | MINOR ELECTRICAL UPGRADE | 0303 | This building was constructed as a residence and lacks the electrical capacity needed in a modern office. This project will provide for additional outlets and electrical capacity, as well as some expansion capability. Additional funds are included to replace and augment exterior lighting on and around the building. | B&G CLUB/HISP SERVICES #10(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 2269 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0295EXT1 | EXTERIOR FINISHES | 0295 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. | BOYS & GIRLS CLUB GYM #12(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1898 | 2925 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10000
2313LGT1 | LONG-TERM NEEDS | 2313 | Projects in this category address possible long term needs of the facility. This does not represent a cost for all future maintenance but is a budgetary number for future Capital Improvement projects related to maintenance. The cyclical treatment of the building exterior and interior is very important to help maintain the finish, weather proofing, integrity and appearance of the building. This treatment does not include the roofing material itself but it should include everything that has to do with water proofing the building envelope including painting or staining, sealing, repair, and caulking where applicable; for example, around all windows, flashing, fixtures, sills, etc. This also includes interior applied finishes such as paint, grout, caulking, etc. Special attention should be paid to areas that are exposed to moisture. This project also accounts for possible system replacements. | QUONSET #14(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City | 1960 | 500 | 2003-01-10 | Four to Ten Years | Long-Term Needs | 3 | 1000
0294ELE1 | ELECTRICAL UPGRADE | 0294 | This building was constructed before the high demand for new types of electrical devices were needed. As time progressed, the building's electrical demand has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building. | BOYS & GIRLS CLUB #9(VACANT) | 9955 | Admin | PubWorks | B&G | Carson City |  | 4578 | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
9955SIT6 | REPLACE SANITARY SEWER | 9955 | The sanitary sewer lines are original to the site and showing evidence of partial collapse and failure. The vitreous clay piping has cracked, hubs have separated, and tree roots have infiltrated in a number of locations, contributing to problems. This project recommends the entire system be replaced. Additional monies are included to replace the building laterals. Costs were developed from a similar project at the Stewart Facility, and is based on an 8" main and 4" or 6" laterals. | NORTHERN NEVADA CHILDREN'S HOME SITE | 9955 | Admin | PubWorks | B&G | Carson City | 0 |  | 2003-01-10 | Two to Four Years | Necessary - Not Yet Critical | 2 | 550000
9956SIT4 | LOADING DOCK / APRON REPLACEMENT - PAINT SHOP | 9956 | The concrete loading dock and concrete aprons at the overhead doors are in poor shape and failing. This project would provide for the installation of a new concrete loading dock and aprons. Removal and disposal of the existing concrete is included in this estimate. A total of 1,050 square feet was used to generate this estimate. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 10500
2315INT1 | INTERIOR FINISHES | 2315 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 6600
0239HVA2 | INSTALL HVAC SYSTEM | 0239 | The offices and restroom do not currently have any HVAC systems as required by the Mechanical Code and 2006 IBC. This project would provide for a new gas fired furnace, an air cooled condensing unit and all required ductwork and utility connections for a complete system in these areas. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
0239SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0239 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 35000
0239EXT3 | EXTERIOR DOOR REPLACEMENT | 0239 | The existing exterior metal doors and frames are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of the south double door assembly and the north single door assembly with new metal doors, frames and ADA accessible hardware and thresholds. Removal and disposal of the existing doors is included in this estimate. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0239ADA1 | ADA RESTROOM UPGRADE | 0239 | The unisex restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 15000
0239EXT2 | ROOF REPLACEMENT | 0239 | The existing roof consists of corrugated transite and single-ply with the corrugated roofing covering about three-fourths of the building. The roofing material has reached the end of its expected life. It is recommended that this building be re-roofed in the next two to three years with a standing seam metal roofing system in place of the corrugated transite as well as a new single-ply membrane roofing system on the low slope roof area. This estimate includes removal and disposal of the old roofing and an increased square footage cost for asbestos abatement. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
0239INT1 | INTERIOR FINISHES | 0239 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next four to five years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 25000
0391SFT3 | SEISMIC RETROFIT | 0391 | This building is an unreinforced sandstone masonry structure which requires seismic strengthening to meet current building and life safety codes. An initial study was done under CIP 07-M46 which provided detailed recommendations for a seismic retrofit. The planning and design will be requested under CIP 09-P05 and the construction cost will be requested for the 2011 CIP. The estimate is for the construction costs only. This project should coincide with a complete remodel of the interior of the building. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 390000
2315EXT2 | WINDOW REPLACEMENT | 2315 | The windows are original, single pane construction in wood frames. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9956ENV1 | INSTALL DOMESTIC WATER BACKFLOW PREVENTION | 9956 | There is a two inch domestic water line located in the southwest corner of the parking lot which feeds the B & G office buildings. It does not have any backflow prevention. This project would provide for a two inch double check backflow assembly device to be installed at this location. A below grade installation including a vault with a traffic rated lid is also included in this project. The existing shut-off or isolation valve would remain and a new isolation valve should be installed just outside of the building where the water service is located.. This is also included in the estimate. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13000
2315EXT1 | EXTERIOR FINISHES | 2315 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 22000
0391ADA3 | ADA SIGNAGE | 0391 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 900
0239ELE1 | PROVIDE CLEARANCE AT ELECTRICAL PANELS | 0239 | There are electrical panels in the building which do not have proper clear floor space around them. The 2006 IFC section 605.3 states that, "A working space of not less than 30 inches in width, 36 inches in depth and 78 inches in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches , the working space shall not be less than the width of the equipment. No storage of any materials shall be located within the designated working space." This project would provide funds to relocate the tables, microwaves and other items currently blocking the working space. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 250
0391SFT8 | STORAGE AREA GUARDRAIL / HANDRAIL INSTALLATION | 0391 | The upper level storage area contains numerous levels with a mix of stairs and handrails / guardrails that do not meet the intent of the building code. This project would provide for new stairs, handrails and guardrails to be installed. The 2006 IBC Chapter 10 was used for reference. Removal and disposal of the existing stairs and guardrails is included in this estimate. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 7500
2312EXT2 | ROOF REPLACEMENT | 2312 | The asphalt composition shingle roof on this building was in fair condition at the time of the survey. It is recommended that this building be re-roofed in the next four years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing system. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 36000
2315EXT4 | EXTERIOR DOOR REPLACEMENT | 2315 | The existing exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of two door assemblies with new metal doors, frames, paint and hardware. Removal and disposal of the existing doors is included in this estimate. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
2312ADA1 | ADA RESTROOM UPGRADE | 2312 | The unisex restroom does not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one ADA Unisex restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 15000
2312INT1 | INTERIOR FINISHES | 2312 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2312HVA1 | HVAC UPGRADE | 2312 | The small office area has only an electric baseboard heater which is in poor condition and no cooling system. It is recommended to install upgraded heating equipment and an evaporative cooler in this occupied area to ensure a comfortable work environment. This project would provide for the purchase and installation of a natural gas fired heater and a wall mounted evaporative cooler including all required connections to existing utilities. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2312EXT1 | EXTERIOR FINISHES | 2312 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 24000
0391SFT7 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0391 | The building is a B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 109200
0391SFT6 | EXITING STUDY | 0391 | The building has undergone several interior remodels and expansions including adding flooring and partitions to the second floor. Without comprehensive planning during these remodels, the exiting requirements have not been addressed and the building is now potentially a life safety hazard. This project recommends that a licensed architect or other professional perform an exiting study to assess the current state of the exiting plan based on current and / or future use. Future projects may result from the completed report and are not included in this estimate. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 2500
2315SFT2 | FIRE ALARM SYSTEM INSTALLATION | 2315 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will be in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 15400
2315SFT1 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 2315 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 1500
2312EXT3 | OVERHEAD DOOR REPLACEMENT | 2312 | There is an 8'x8' overhead coiling door on the North side of the building which is damaged and does not function properly. It is original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the overhead coiling door and replacement with a new manually operated overhead coiling door. Removal and disposal of the existing door is included in this estimate. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
2312SFT1 | FIRE ALARM SYSTEM INSTALLATION | 2312 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will be in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 16800
2315EXT3 | ROOF REPLACEMENT | 2315 | The single-ply roof on this building was reported in fair condition at the time of the survey. This existing single-ply roofing system was installed in 1998. The statewide roofing program estimates the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. This building should be re-roofed in the next five to six years, consistent with the roofing program guidelines and the warranty period. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 33000
0391EXT4 | WINDOW REPLACEMENT | 0391 | The existing window systems in the building are of original wood frames and single pane glazing. Many of the window openings have been modified to accommodate air conditioning units. These units are not energy efficient. This project would provide for the removal of the existing window units and replacement with new energy efficient glazing that would match the historical nature of the existing windows. This building is on the State Historical Register and approval of this project may be required by the Nevada State Historical Preservation Office. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
0391EXT3 | EXTERIOR FINISHES | 0391 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including sealing the stone, painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 78000
0391INT1 | INTERIOR FINISHES | 0391 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 39000
0391ENR1 | LIGHTING UPGRADE | 0391 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 23400
0239ENR1 | LIGHTING UPGRADE | 0239 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
9956ADA1 | ADA ACCESSIBLE PARKING INSTALLATION - PARKING LOT | 9956 | The ADA accessible parking stalls in the south parking lot do not meet slope requirements due to root damaged asphalt. This project would provide for the removal of the existing asphalt and installation of 5 new ADA compliant parking and loading zones. One shall be a van accessible space. Signage is included in this estimate. 900 square feet of paving was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 15000
9956ADA2 | SIDEWALK / CURB REPLACEMENT - PARKING LOT | 9956 | The concrete sidewalks and curbs surrounding the parking lot are in poor condition. There are damaged curbs, spalling concrete and non-conforming ADA curb cuts at street crossings. This project would provide for the removal and replacement of the concrete sidewalks and curbing around the parking lot. Four ADA compliant curb cuts, 3,000 square feet of concrete sidewalk and 275 lineal feet of concrete curbing was used to generate this estimate. The sidewalk along Stewart Street was not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 40250
0239EXT1 | EXTERIOR FINISHES | 0239 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 50000
9956SIT1 | REPLACE ASPHALT PAVING - B & G BUILDINGS | 9956 | The asphalt around the side and rear of the B&G buildings is failing, with significant alligatoring and cracks observed. The paving has deteriorated to the point that it is no longer viable. This project covers the removal and replacement of all existing asphalt paving around and between the B & G buildings. This project should be done concurrently with the sidewalk replacement project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 45000
0391ADA1 | ACCESSIBLE WATER FOUNTAIN | 0391 | This building contains a water fountain. The 2006 IBC Section 1109.5 states where a water fountain is provided, at least half should be accessible. This project would provide funding for the purchase and replacement of a new accessible fixed high / low ADA accessible drinking fountain. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 4000
0391PLM1 | REPLACE PLUMBING / WASTE SYSTEM | 0391 | The plumbing and waste system is older and in poor condition. Parts of the system appear to be original to the building and have continued to deteriorate. This project recommends replacing the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Four to Ten Years | Long-Term Needs | 3 | 75000
0391SFT5 | UPGRADE EXIT SIGNS AND EGRESS LIGHTING | 0391 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. There are signs which indicate egress which do not comply with current code and should be removed. Per the 2006 IBC, egress is not permitted through the garage or down the back stairs from the storage area. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 19500
9956SIT2 | CRACK FILL AND SEAL ASPHALT PAVING - PARKING LOT | 9956 | The parking lot south of the B & G buildings is in fair condition. There are numerous cracks that are in need of filling. This project would provide for crack fill and sealing of the parking lot including striping. This project should be done concurrently with the ADA parking and sidewalk replacement project. It is recommended that this project be done on a cyclical basis every three to five years to maintain the integrity of the pavement. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22500
0391ELE1 | MAJOR ELECTRICAL UPGRADE | 0391 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. There are electrical boxes missing safety covers in the attic. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 195000
0391HVA1 | REPLACE HVAC EQUIPMENT | 0391 | The HVAC system consists of two hot water boilers, a few isolated evaporative coolers and window mounted air conditioning units. There is no central cooling system although the radiant heating from the boilers is sufficient. The boilers were replaced in 2001. This project would provide for installation of a central cooling system including duct work and grills throughout the building. This project includes removal and disposal of the existing cooling units and all required connections to utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 156000
0239HVA1 | INSTALL EVAPORATIVE COOLERS | 0239 | The building has no central cooling system and is uncomfortably warm in the summer. It is recommended to install three evaporative coolers in the building to ensure a comfortable work environment in the shop areas. This project would provide for the purchase and installation of three evaporative coolers including all required connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | B & G PAINT SHOP | 9956 | Admin | PubWorks | B&G | Carson City | 1948 | 5000 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
0391ADA4 | REPLACE STAIR HANDRAILS | 0391 | The stair handrails are older and do not meet code for safety or accessibility. The gripping surfaces are incorrect and they are not continuous from the top to bottom landings. This project recommends the installation of handrails on both sides of the stairs, with proper returns and supports. Removal and disposal of the existing railing is included. 2006 IBC Chapter 10, Section 1012, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 20000
9956SEC1 | INSTALL EXTERIOR SITE LIGHTING IN PARKING LOT | 9956 | This project would provide for the installation of general security lighting fixtures around the parking lot. Cost includes light fixtures, wiring, trenching and installation, based on a 20 foot pole. This project should be done prior to any pavement projects. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS AND GROUNDS OFFICE SITE | 9956 | Admin | PubWorks | B&G | Carson City | 0 |  | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 66000
0391SFT4 | FIRE ALARM SYSTEM UPGRADE | 0391 | This building is partially equipped with a fire alarm system that no longer complies with current requirements and does not monitor the second floor offices. It is recommended that the system be replaced to current requirements to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2006 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 39000
2312ENR1 | LIGHTING UPGRADE | 2312 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to T-8 lamps with electronic ballasts to current standards, resulting in increased efficiency and reduced costs associated with illumination. Any electrical wiring upgrades are not included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS GARAGE | 9956 | Admin | PubWorks | B&G | Carson City | 1990 | 2400 | 2008-11-25 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7200
2315ENV1 | DUST COLLECTION SYSTEM, WOOD SHOP | 2315 | The building has a woodshop which does not have a complete dust collection system. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. This project recommends installing a new dust collection system. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | B & G OFFICE GARAGE ADDITION | 9956 | Admin | PubWorks | B&G | Carson City | 1960 | 2200 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 15000
0391ADA2 | ADA ACCESSIBLE COUNTER | 0391 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This building contains a counter which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 02/24/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 11/25/2008. | BUILDINGS & GROUNDS OFFICE | 9956 | Admin | PubWorks | B&G | Carson City | 1900 | 7800 | 2008-11-25 | Immediate to Two Years | Currently Critical | 1 | 3000
0895HVA1 | HEATER REPLACEMENT | 0895 | The existing heating system consists of a ceiling mounted heater and does not have cooling equipment. The heater is inefficient and was installed in 2004. The heater should be replaced within 8-10 years with a 80% AFUE or higher unit. This project would replace the existing heater. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 3500
1655SIT1 | SITE BOLLARDS | 1655 | The Headquarters building has seven sectional overhead doors. These areas are in need of bollards to protect the building. This project would provide funding for 15 eight inch diameter bollards to be located on each side of the garage sectional overhead doors. This project or a portion thereof was previously recommended in the FCA report dated and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 9750
0895EXT1 | EXTERIOR FINISHES | 0895 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6400
1655HVA2 | HEAT PUMP REPLACEMENT | 1655 | There is one roof top heat pump (Goodman) system that was installed in 1995. It is not energy efficient and has reached the end of its useful life. This project would provide for installation of the heat pump system and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing heat pump system and all required connections to utilities. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 12000
0895EXT2 | EXTERIOR DOOR REPLACEMENT | 0895 | The exterior metal vestibule door is damaged from age and general wear and tear and has reached the end of its expected life. This project would provide for the replacement of the door assembly with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1655HVA3 | HVAC EQUIPMENT REPLACEMENT | 1655 | There are several HVAC packaged units and swamp coolers on the roof that were installed in 2004. This project would provide for installation of the new HVAC packaged units, swamp coolers and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC equipment and all required connections to utilities. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 308250
2966EXT1 | EXTERIOR FINISHES | 2966 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 4-5 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | PUMP HOUSE | 9957 | CNR | Forestry |  | Washoe Valley | 2008 | 150 | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 1500
0895INT1 | INTERIOR FINISHES | 0895 | The interior walls are insulated and sheet rocked in the front half of the building only. The sheet rock in the office room is severely damaged and should be removed, replaced and painted. It is recommended that these interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1655ENV1 | SPILL CONTAINMENT | 1655 | The vehicle garage does not have a method for containing spills or leakage from oil drums and other containers. This does not meet OSHA standards for hazardous materials containment. This project would add secondary containment pallets for all containers in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 6500
1655SFT2 | GENERATOR MODIFICATIONS | 1655 | The emergency generator is not currently connected to the overhead garage doors in the fire response garage. The doors should be connected to the generator so that the emergency vehicles can be deployed at any time. It is not unlikely that a power outage would coincide with other types of emergencies where the vehicles would be needed. This project recommends connecting the overhead doors to the emergency generator and includes purchase and installation of wiring and electrical hardware. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 6000
1655PLM1 | WATER HEATER REPLACEMENT | 1655 | The average life span of a water heater is eight to ten years. The 40 gallon electric water heater in the generator room was installed in 2004. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 1-2 years. It is recommended that a new gas-fired water heater be installed for more efficient use of energy. This estimate includes: 100 feet of gas pipe, fittings, couplers, and labor for installation. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 3000
1655STR1 | STRUCTURAL REPAIRS | 1655 | A storage area has been constructed in the apparatus room, accessed via stairs in the garage. There is no record of a CIP project for this work or of any structural evaluations having been conducted. This project recommends adding structural members to the existing framing to ensure proper load bearing capacity. This will require a structural design from a licensed engineer, inspections and permitting which are not included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 15000
1655EXT2 | EXTERIOR LIGHTING UPGRADE | 1655 | The exterior wall-mounted light fixtures appear to be original to the building. They are damaged from age and general wear and tear. This project would provide for the purchase and installation of six energy efficient light fixtures. Removal and disposal of the existing fixtures is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1655ADA1 | ADA DOOR HARDWARE REPLACEMENT | 1655 | The 2010 ADA Standards for Accessible Design states that handles, pulls, latches, locks and other operable parts on doors and gates shall be operable with one hand and shall not require tight grasping, pinching, or twisting of the wrist. The force to activate operable parts shall be 5 pounds maximum. It is recommended that proper lever hardware be installed on all of the interior and exterior doors in this building to meet these requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and sections 309.4 and 404.2.7 of the 2010 ADA Standards For Accessible Design were used as a reference for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 20000
1655INT1 | INTERIOR FINISHES | 1655 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115300
1655EXT1 | EXTERIOR FINISHES | 1655 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115300
2348INT1 | INTERIOR FINISHES | 2348 | The interior finishes are in fair condition. It is recommended that the interior walls be painted at least once in the next two to three years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
1655SFT5 | MEZZANINE STAIR HANDRAIL REPLACEMENT | 1655 | The stair handrails and guardrails leading up to the mezzanine in the apparatus room do not meet code for safety. This project recommends the installation of handrails on both sides of the stairs and guardrails at the top landing in accordance with the 2012 IBC Section 1012 and Section 1013. Removal and disposal of the existing rails is included in the estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 3600
2348EXT1 | EXTERIOR FINISHES | 2348 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the painting, sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3200
1655SFT4 | STORAGE REMOVAL | 1655 | The storage areas in the parts room and the apparatus room mezzanine have items stored too close to the fire sprinkler heads. The 2012 IFC Section 315.3.1 states that, "Storage shall be maintained a minimum of 18 inches below sprinkler head deflectors in sprinklered areas of buildings." This project would provide for the removal of all items in conflict with this code requirement to insure that the fire suppression system operates correctly. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 500
2339EXT1 | EXTERIOR FINISHES | 2339 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding for the maintenance of the exterior of the building. Included in the cost is the painting, sealing and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ WELDING SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 1250 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12500
1655ADA5 | ADA SHOWER UPGRADE | 1655 | The shower in the office area is not accessible. If a shower is provided, then at least one accessible shower stall shall be provided. This project would provide for one ADA compliant shower stall to be installed to provide shower facilities for the disabled. Included in this estimate is removal of the existing shower stall and installation of an ADA compliant shower stall complete with accessible plumbing fixtures, seat, etc. International Building Code (IBC) - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 7500
1655SFT3 | STAIR HANDRAIL REPLACEMENT | 1655 | There are three sets of stair handrails in the building that are older and do not meet code for safety. The rails do not extend at the top and bottom of the stairs in accordance with the 2012 International Building Code (IBC) Section 1012.6. This project applies to the stairs between the offices and the shop, the stairs in the vehicle garage and the exterior stairs off of the Ready Room. Each of these flights of stairs has 4 risers. This project recommends the installation of handrails on both sides of the stairs at each of these locations in accordance with the 2012 International Building Code (IBC) Section 1012. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 3000
1655INT2 | SHEET VINYL FLOORING REPLACEMENT | 1655 | The sheet vinyl flooring in the shop restroom is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the flooring and installation of new sheet vinyl with a 6" cove base. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1350
2347EXT1 | EXTERIOR FINISHES | 2347 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost are sealing and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ RADIO EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1990 | 50 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
2348PLM1 | FLOOR DRAIN REPAIR | 2348 | The floor drain in the building is clogged and water has pooled around it. The standing water will prematurely deteriorate the building components as well as create a slipping hazard. This project would provide for a licensed contractor to clear the drain and provide any necessary repairs to prevent future problems. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 2000
0895EXT3 | WINDOW REPLACEMENT | 0895 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 2 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
9957SIT8 | SLURRY SEAL ASPHALT PAVING | 9957 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas and the maintenance yard. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 50,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 62500
9957SIT4 | SITE BOLLARDS | 9957 | There are two above ground fuel tanks on the site, one for diesel and one for unleaded gasoline. The unleaded gasoline tank does not have adequate protection from vehicles. Per International Fire Code 2012 Section 312 Vehicle Impact Protection, steel posts need to be installed, not less than 4 inches in diameter and filled with concrete. The spacing shall be not more than 4 feet between posts on center and located not less than 3 feet from each gas tank. This project would provide funding for two new bollards to be located in front of the unleaded gasoline tank. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
9957SIT5 | INSTALL WHEEL STOPS | 9957 | The Headquarters building has four parking spaces next to the building. These spaces are missing wheel stops which could cause damage to the building. This project would provide for the purchase and installation of four 72"x6"x4" rubber composite wheel stops. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1655ELE2 | ELECTRICAL UPGRADE | 1655 | This building was constructed before the high demand for electrical services were needed for computers and other electrical devices. As time has progressed, the buildings electrical demand and system has changed. It is utilized to its current maximum potential. The electrical panels and receptacles are at their limit. It is recommended the entire system be upgraded to meet the evolving needs of the building including three-phase power. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 308250
2348ENR1 | LIGHTING UPGRADE | 2348 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade T-12 lamps to T-8 lamps with electronic ballasts and upgrade the HID (high intensity discharge) lamps to current standards, resulting in increased efficiency and reduced costs associated with illumination. An occupancy sensor will be installed in the Garden Equipment Storage room for additional savings. Any electrical wiring upgrades are not included in this estimate. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 480
2339ENR0 | INSULATE BUILDING | 2339 | The building is not insulated and is not energy efficient. Due to this, the heater continuously runs. This project would provide for the installation of blanket insulation with impermeable vinyl interior surface batt insulation in the walls (R19) and ceilings (R38) to help moderate temperature fluctuations. | HQ WELDING SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 1250 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
2348ELE5 | ELECTRICAL UPGRADE | 2348 | This building was constructed before the high demand for electrical services were needed. As time has progressed, the building’s electrical demand and system has changed. The electrical panel has been altered and added to improperly. There are open circuits missing cover plates and wires attached to the panel incorrectly. The electrical panels and receptacles do not comply with NEC 2011. It is recommended to have the entire system upgraded to meet the current standards including three-phase power. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 16000
2348EXT0 | EXTERIOR DOOR REPLACEMENT | 2348 | The existing exterior metal door and frame appear to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement and installation of a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | HQ GARDEN EQUIPMENT STORAGE | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 320 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9957SFT8 | MOTORIZED GATE INSTALLATION | 9957 | The site has a perimeter fence that has a sliding vehicle access gate. It is manually operated, has no track system and is difficult to open and close. Several employees have sustained injuries operating the gate. This project recommends the gate be upgraded to a motorized track system that can handle heavy equipment traffic. The gates will be required to meet UL Standard 325, per NRS 405.270. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 45000
9957ENV3 | 4" BACKFLOW ASSEMBLY, VAULT, AND POWER | 9957 | State Health Law (NAC 445A.67185) and the Uniform Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers as appropriate to the hazard and in appropriate locations near the potential source of contamination. Costs include an above ground vault, and allowance for 200 feet of 1" conduit to provide power for freeze protection. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 35000
9957SIT2 | EXTERIOR SITE LIGHTING INSTALLATION | 9957 | The site has minimal lighting in the parking lot and between the buildings which is a security and safety concern. This project would provide funding for the purchase and installation of five 20'-0" high light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This estimate includes removal and disposal of the three existing pole lights in the parking lot. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Four to Ten Years | Long-Term Needs | 3 | 60000
0895INT2 | INTERIOR DOOR REPLACEMENT | 0895 | The interior doors in this building are hollow core units and are damaged from general wear and tear. This project would provide for the installation of new solid core interior doors including frames, lever action door handles, hardware and paint. Removal and disposal of the existing doors is included in this cost estimate. A total of 3 interior doors was used in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | HQ PAINT SHOP | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 3200 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9957SIT7 | SIDEWALK AND LANDING INSTALLATIONS | 9957 | A number of buildings at the site do not have proper landings at exit doors as required by the 2012 IBC 1008.1.5. This project addresses new sidewalks and landings as needed including the rear door from the parts room in the Headquarters building and the entrance to the HQ Welding Shop. This estimate is for 2,000 square feet of 4" thick concrete. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1655ADA4 | ADA ACCESSIBLE COUNTER | 1655 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. This building contains a counter which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. International Building Code (IBC) - 2012, ICC/ANSI A117.1 - 2009 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2009 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 4000
9957ELE1 | BUILDING DISCONNECTS | 9957 | Power for the smaller buildings around the HQ building is pulled off the main panel in the HQ apparatus garage. There is no way to shut off power to the individual buildings, or shut off power for the HQ without de-energizing all of the buildings. This project will provide six separate building disconnects as well as disconnects in the HQ building, for the garage and shop. The 2011 NEC 250.32 (D) was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 03/04/2003 and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | NDF WESTERN AREA HEADQUARTERS SITE | 9957 | CNR | Forestry |  | Washoe Valley | 0 |  | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 24000
1655ADA3 | POWER DOOR ACTUATOR REPAIRS | 1655 | The building has an existing ADA entry with a power assisted door opener. The opener is currently not operational and should be scheduled for replacement. This project recommends replacing the ADA actuator and includes removal and disposal of the existing equipment. This project or a portion thereof was previously recommended in the FCA report dated and 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 1500
1655ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 1655 | This building contains a water fountain that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 4000
1655EXT4 | OVERHEAD DOOR REPLACEMENT | 1655 | There are two 12'x14' overhead coiling doors in the repair shop which are damaged and do not function properly. They are original to the building and should be scheduled for replacement. This project would provide for the removal and disposal of the power-operated overhead coiling doors and replacement with new power-operated doors. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
1655EXT3 | ROOF REPLACEMENT | 1655 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 15 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 2004. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172950
1655ELE1 | EXTERIOR OUTLET REPLACEMENT | 1655 | The building has an exterior electrical outlet that does not meet code. The outlet is not a GFCI type outlet which is required according to the 2011 NEC. This project would provide for the purchase and installation of one GFCI duplex outlet. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 400
1655SFT1 | FIRE ALARM ANNUNCIATOR PANEL REPLACEMENT | 1655 | There is a fire alarm annunciator panel mounted on the exterior of the building near the main entrance. The panel is not rated for exterior applications and was not operating during the survey of 2009. It was most likely damaged from exposure and should be scheduled for replacement. This project recommends replacing the panel with an exterior rated panel and includes connections to the fire alarm system and any other utilities. This project or a portion thereof was previously recommended in the FCA report dated 01/27/2009. It has been amended accordingly to reflect conditions observed during the most recent survey date of 12/16/2015. | WESTERN AREA HEADQUARTERS | 9957 | CNR | Forestry |  | Washoe Valley | 1980 | 12330 | 2015-12-16 | Immediate to Two Years | Currently Critical | 1 | 6500
1467INT3 | KITCHEN CABINET REPLACEMENT | 1467 | The kitchen cabinets are original to the building and have reached the end of their expected life. This project recommends the replacement of the existing kitchen counters, cabinets and associated hardware with mid range, high quality components. ADA compliant casework is recommended for this facility. Appliances are not included in this estimate. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 15000
1467EXT2 | ROOF REPAIRS | 1467 | During the survey of 4/30/2008, there were areas of the composition shingle roof that were missing and / or damaged from a wind event. This project would provide for the repair of the damaged shingles. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 1200
1468EXT2 | ROOF REPAIRS | 1468 | During the survey of 4/30/2008, there were areas of the composition shingle roof that were missing and / or damaged from a wind event. This project would provide for the repair of the damaged shingles. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 1200
1466PLM4 | WATER HEATER REPLACEMENT | 1466 | The average life span of a water heater is eight to ten years. The existing 93 gallon natural gas water heater in the building was installed in 1993. It has reached the end of its expected life and is not energy efficient. This project would provide for the removal and disposal of the old water heater and installation of a new 100 gallon water heater. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2200
1466HVA2 | HVAC UPGRADE | 1466 | The HVAC system is largely original to the building and is due for a major upgrade. This equipment has reached the end of its serviceable and expected life span, and should be scheduled for replacement within the next two to three years. This project would provide for replacement of the two Weil-McLain boilers, the water treatment system and several other parts of the HVAC system including a broken gate valve and the boiler exhaust system. Cleaning of the existing ductwork, grills and diffusers, and balancing is included in the project. The estimate includes all utility connections as well as removal and disposal of the existing equipment. This work should be performed concurrently with the "HVAC Controls Upgrade" project. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200000
1466ENR2 | EXTERIOR LIGHTING UPGRADE | 1466 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, give off inadequate lighting and are not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new high intensity, energy efficient light fixtures, including connections to the existing electrical system. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1466ADA3 | ADA RESTROOM UPGRADE | 1466 | The Men's and Women's designated ADA restrooms do not meet the Americans with Disabilities Act (ADA) regulations. A retrofit is necessary to comply with 2006 IBC Chapter 11, ICC/ANSI A117.1-1998 Sections 603 - 604 and the Americans with Disabilities Act Accessibility Guidelines (ADAAG). Given the current configuration of the restrooms, the work will include the installation of a new toilet, sink, grab bars, faucets, mirrors, dispensers and hardware. Some minor design work will be required and may impact the final cost estimate. This estimate is for one Men's and one Women's restroom facility. The removal and disposal of the old restroom fixtures is included in this estimate. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 64000
1466SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 1466 | The building is a B occupancy per the 2003 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 240940
1466INT1 | INTERIOR FINISHES | 1466 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 86050
1467PLM2 | WATER HEATER REPLACEMENT | 1467 | The average life span of a water heater is eight to ten years. The two existing 80 gallon natural gas water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of two new 80 gallon water heaters. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1468EXT3 | WINDOW REPLACEMENT | 1468 | The windows are original, dual pane construction in a metal frame. These older windows have broken seals, become fogged up and discolored due to moisture infiltrating the glass. This project recommends replacing the windows with dual pane, high efficiency units. This estimate is for the replacement of 12 units. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 18000
9958ADA2 | ADA SIDEWALK UPGRADES | 9958 | The concrete sidewalks throughout the campus are in need of replacement or modification. There are many areas that do not meet ADA guidelines and 2006 IBC Chapter 10, Section 1010 requirements for ramps including exceeding minimum slope requirements or missing rails and curbs at ramps. There are also many sections of concrete that have cracks due to settling or are spalling considerably. This project would provide for the removal and replacement of the concrete sidewalks. 5,000 SF of 4" thick concrete sidewalk was used for this estimate. A professional design should be commissioned for this project in order to determine the most cost effective construction. The design will incorporate current ADA requirements to insure 100% compliance on all accessible routes-of-travel. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 75000
9958SIT4 | EROSION CONTROL | 9958 | On the north side of the Administration/ Classroom Building, the dirt bank between the building and McCarran Blvd is eroding considerably. The runoff from McCarran Blvd is exacerbating an already poorly designed drainage area. The dirt bank has slowly crept closer to the building and has left little space for water to drain around the building. This is now causing damage to the building from flooding and has also flooded the play yard next to the building. There have been several minor improvements accomplished to control the situation, but it is apparent that a major improvement must happen in order to protect the building from permanent damage. This project recommends installing a retaining wall between the building and the street in order to provide proper drainage and erosion control. The estimate is based on a 500 foot long, 8'-0" high reinforced concrete masonry unit retaining wall. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 100000
1466INT2 | CARPET REPLACEMENT | 1466 | The carpet in the addition is showing signs of extreme wear and some areas were not installed correctly. It is recommended that the carpet be replaced with heavy duty commercial grade carpet in the next two to three years. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 34200
1468ENR2 | EXTERIOR LIGHTING UPGRADE | 1468 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, give off inadequate lighting and are not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new high intensity, energy efficient light fixtures, including connections to the existing electrical system. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1467EXT3 | WINDOW REPLACEMENT | 1467 | The windows are original, dual pane construction in a metal frame. These older windows have become fogged up and discolored due to moisture infiltrating the glass. This project recommends replacing the windows with dual pane, high efficiency units. This estimate is for the replacement of 12 units. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 12000
1468PLM2 | WATER HEATER REPLACEMENT | 1468 | The average life span of a water heater is eight to ten years. The two existing 80 gallon natural gas water heaters in the building have reached the end of their expected life and are not energy efficient. This project would provide for the removal and disposal of the old water heaters and installation of two new 80 gallon water heaters. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3700
1468INT3 | KITCHEN CABINET REPLACEMENT | 1468 | The kitchen cabinets are original to the building and have reached the end of their expected life. This project recommends the replacement of the existing kitchen counters, cabinets and associated hardware with mid range, high quality components. ADA compliant casework is recommended for this facility. Appliances are not included in this estimate. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Four to Ten Years | Long-Term Needs | 3 | 15000
1467INT2 | INTERIOR FINISHES | 1467 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1467ENR2 | EXTERIOR LIGHTING UPGRADE | 1467 | The building has perimeter lighting on the exterior of the building, but the light fixtures are old, give off inadequate lighting and are not energy efficient. This project would provide for the replacement of the exterior lighting fixtures with new high intensity, energy efficient light fixtures, including connections to the existing electrical system. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1468INT2 | INTERIOR FINISHES | 1468 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next two to three years and every 5 to 7 years thereafter to maintain the integrity of the interior of the building. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 20000
1467HVA1 | HVAC SYSTEM REPLACEMENT | 1467 | The HVAC system consists of two furnaces and two air cooled condensers. This equipment is original to the building and has reached the end of its expected life. This project recommends replacing the equipment in the next 2 to 3 years. The estimate includes removal and disposal of the existing equipment. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22000
1466PLM1 | REPLACE EXISTING TOILET FIXTURES | 1466 | The existing restrooms date to the construction date of the building. The toilet is an older tank-flush model. Due to variations in the water pressure and the age of the facility, this project recommends the replacement of the existing fixture with a new, pressure-assisted, low-gallonage model. This project should coincide with the ADA restroom remodel project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
9958ADA1 | ADA PARKING | 9958 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The existing ADA parking stalls throughout the campus do not entirely meet the requirements of the code. This project provides funding to bring the existing ADA parking areas up to code including updated signage, re-striping, regrading and any other necessary upgrades. IBC - 2006, ICC/ANSI A117.1 - 2003 and Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 2003 were referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 50000
1466SFT5 | EXIT SIGN UPGRADES | 1466 | The exit signs are older and appear to be original to the building. Additional signs are required to identify the paths of exit. These signs should be self-illuminating, or LED signs with internal battery back-up. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 10000
1466PLM2 | MISCELLANEOUS PLUMBING | 1466 | This building received an addition in 1996, and is served by a four pipe hydronic system. Some of the piping for the addition blocks the pans on the fan coil units in the existing building, which prevents maintenance and repairs. The piping affects several fan coils; two have failed and cannot be reached to be replaced. This project provides funding to re-route the piping system to allow access to the affected units, and to replace the failed fan coils. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1466EXT1 | EXTERIOR FINISHES | 1466 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. Elastomeric paint is recommended for the stucco portion of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172100
1468HVA1 | HVAC SYSTEM REPLACEMENT | 1468 | The HVAC system consists of two gas fired furnaces and two air cooled condensers. One furnace and one condenser are original to the building and have reached the end of their expected life. This project recommends replacing one furnace and one condenser in the next 2 to 3 years. The estimate includes removal and disposal of the existing equipment. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 11000
1467EXT1 | EXTERIOR FINISHES | 1467 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. Elastomeric paint is recommended for the stucco portion of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1468EXT1 | EXTERIOR FINISHES | 1468 | It is important to maintain the finish, weather resistance and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. Elastomeric paint is recommended for the stucco portion of the building. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1467PLM1 | REPLACE EXISTING TOILET FIXTURES | 1467 | The existing restrooms date to the construction date of the building. The toilet is an older tank-flush model. Due to variations in the water pressure and the age of the facility, this project recommends the replacement of the existing fixture with a new, pressure-assisted, low-gallonage model. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT A | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1468PLM1 | REPLACE EXISTING TOILET FIXTURES | 1468 | The existing restrooms date to the construction date of the building. The toilet is an older tank-flush model. Due to variations in the water pressure and the age of the facility, this project recommends the replacement of the existing fixture with a new, pressure-assisted, low-gallonage model. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | BEHAVIORAL SERVICES HOUSING UNIT B | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 4000 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
9958SEC4 | INSTALL EXTERIOR SITE LIGHTING | 9958 | The site has minimal site lighting in the parking lots and between the buildings which is a security and safety concern. This project would provide funding for purchase and installation of six 20'-0" high light poles including 30" diameter raised concrete bases, electrical trenching, conduit, wiring and connections to existing utilities. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55224
9958SIT3 | SLURRY SEAL ASPHALT PAVING | 9958 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 70,000 square feet of asphalt area was used to generate this estimate. It is recommended that the site drainage project be completed prior to this project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 42000
9958SIT1 | SITE DRAINAGE ISSUES | 9958 | The site has recurring problems with water pooling at the lower grassy area between the housing units. Some of this may be attributable to drainage problems at the site. Other problems may be a result from site irrigation. This project recommends installing a dry or French drain to minimize flooding and to carry off accumulations. This project includes trenching, installation of gravel in the trench, a 4 inch perforated pipe, more gravel, a non-woven fabric to prevent soil intrusion into the gravel and pipe, backfilling the trench, tamping to finish grade and removal of spoils or surplus soil. This project is recommended to coincide with the retaining wall project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | CHILDREN'S BEHAVIORAL SERVICES SITE | 9958 | HHS | DCFS | NNCAS | Reno | 1977 |  | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 35000
1466ADA1 | POWER DOOR OPENER AND HARDWARE | 1466 | The main entrances to this building are dual leaf, commercial grade aluminum and glass door assemblies. The hardware and configuration of the doors does not fully meet ADA requirements. This project recommends the installation of a power-assisted door opener for the main entrance and side entrance and includes the installation, related wiring and hardware. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 10000
1466ADA2 | SIGNAGE FOR ADA COMPLIANCE | 1466 | Americans with Disabilities Act (ADA) regulations pertaining to building access, route of travel and restrooms has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. This project would provide funding for purchase and installation of ADA signage including directional signage from parking to accessible building entrances, route of travel inside the building and restrooms. Americans with Disabilities Act Accessibility Guidelines (ADAAG) - 1998 was referenced for this project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 4000
1466HVA1 | HVAC CONTROLS UPGRADE | 1466 | The HVAC system controls are older and not efficient. There have been ongoing problems with the zone control valves, and a number have had to be replaced. The second floor is reported as too warm, and the main floor too cold. This project recommends the installation of an Energy Management System (EMS) for the entire site. This system will monitor and control the heating, ventilation, air conditioning and lighting equipment in the building through a central computer system. Electronic sensors will be installed on each piece of equipment which will feed information into the computer system. The maintenance staff can then control and monitor the equipment remotely which will significantly lower energy costs. Along with electricity, gas and water meters, this system will provide detailed reports on energy consumption allowing the maintenance staff to analyze and customize the energy used by the facility. This work should be performed concurrently with the "HVAC Upgrade" project. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Two to Four Years | Necessary - Not Yet Critical | 2 | 129075
1466SFT4 | INSTALL EMERGENCY EGRESS LIGHTING | 1466 | There are older emergency egress lighting in this building. These units have a finite lifespan, and this project recommends their replacement with new egress lights, and providing additional lights on the main exit routes and in individual rooms as needed. This project or a portion thereof was previously recommended in the FCA report dated 04/23/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/30/2008. | ADMINISTRATION/CLASSROOM BUILDING | 9958 | HHS | DCFS | NNCAS | Reno | 1977 | 17210 | 2017-10-24 | Immediate to Two Years | Currently Critical | 1 | 9000
2578EXT1 | EXTERIOR FINISHES | 2578 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the concrete masonry units and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5000
2578ENR1 | LIGHTING UPGRADE | 2578 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
2369INT1 | INTERIOR FINISHES | 2369 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS7 CENTER COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2370EXT1 | EXTERIOR FINISHES | 2370 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 BEACH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
3049EXT1 | EXTERIOR/ INTERIOR FINISHES | 3049 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | EQUESTRIAN CAMPGROUND SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2010 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
2578ADA1 | ADA RESTROOM UPGRADES | 2578 | The designated accessible restroom does not entirely meet the Americans with Disabilities Act (ADA) requirements. The flush handle is on the wrong side of the toilet and there is no vertical grab bar. There may be other minor variances from the code as well. When the upgrade is designed a full inspection should be made to identify all necessary upgrades. This project would provide funding for upgrades to bring the restroom into full compliance with the ADA. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2500
2373ELE1 | SOLAR PANEL REPLACEMENT | 2373 | The power to the building is provided by a photovoltaic system. The solar panels have been broken by vandals and should be scheduled for replacement. This project provides for the purchase and installation of two roof-mounted solar panels. | SS11 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
2373EXT1 | EXTERIOR/ INTERIOR FINISHES | 2373 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS11 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
2372EXT1 | EXTERIOR/ INTERIOR FINISHES | 2372 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS9 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2371EXT1 | EXTERIOR/ INTERIOR FINISHES | 2371 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 BEACH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2370PLM1 | WATER HEATER REPLACEMENT | 2370 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS7 BEACH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
2370INT1 | INTERIOR FINISHES | 2370 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS7 BEACH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2578INT1 | INTERIOR FINISHES | 2578 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS RANGER STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 1000 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3057EXT2 | ROOF REPLACEMENT | 3057 | The corrugated metal roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a standing seam metal roofing system. This estimate includes removal and disposal of the old roofing. | LD GARAGE #5 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
3053PLM1 | PLUMBING / WASTE LINE REPLACEMENT | 3053 | The plumbing and waste system is older and in poor condition. Most of the system appears to be original to the building and should be scheduled for replacement. This project recommends replacing all of the water and sewer lines in the building. This estimate includes removal and disposal of the existing system as required. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 21000
3053INT2 | KITCHEN FLOORING REPLACEMENT | 3053 | The sheet vinyl flooring in the kitchen was installed poorly and should be scheduled for replacement. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 4" base. 150 square feet was used to generate this estimate. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1050
3054EXT1 | EXTERIOR FINISHES | 3054 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | WATER TREATMENT PLANT | 9959 | CNR | Parks |  | Lahontan SRA | 2000 | 400 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1200
3055EXT1 | EXTERIOR FINISHES | 3055 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | METAL STORAGE BUILDING | 9959 | CNR | Parks |  | Lahontan SRA | 2009 | 240 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 720
3056EXT1 | EXTERIOR FINISHES | 3056 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
3048INT1 | INTERIOR FINISHES | 3048 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS DAY USE COMFORT STATION SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3057EXT1 | EXTERIOR FINISHES | 3057 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #5 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
3053EXT3 | ROOF REPLACEMENT | 3053 | The asphalt composition shingle roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 4-5 years with a new 50 year asphalt composition roofing shingles and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 14000
3058EXT1 | EXTERIOR FINISHES | 3058 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 1256 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
3059EXT1 | EXTERIOR FINISHES | 3059 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 1256 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 7500
3060EXT1 | EXTERIOR FINISHES | 3060 | It is important to maintain the finish, weather resistance and appearance of the water tank. This project would provide for the painting of the water tank and caulking of the joints to maintain it in a good, weather tight condition. It is recommended that this project be implemented in the next 4 to 5 years and is recommended on a cyclical basis based on environmental conditions. | WATER TANK #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 1256 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 7500
9959SIT4 | ASPHALT PAVING INSTALLATION | 9959 | The maintenance yard and parking lot next to the Regional Headquarters building is not paved. This project would provide 100,000 square feet of asphalt cement paving for this area. The estimate includes grading, 6" base, compaction and installation of 4" thick asphalt cement paving. | LAHONTAN STATE RECREATION AREA | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 300000
1320INT1 | INTERIOR FINISHES | 1320 | The interior finishes are in fair condition. It is recommended that the Fiberglass Reinforced Panels are power washed and re-caulked and the ceramic tiles are repaired and sealed as needed. This project should be done at least once in the next 2-3 years and scheduled on a cyclical basis to maintain the integrity of the structure. | OVERLOOK CXT COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2006 | 204 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1020
2369EXT1 | EXTERIOR FINISHES | 2369 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 CENTER COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
3056EXT2 | ROOF REPLACEMENT | 3056 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | LD GARAGE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4000
3053EXT1 | EXTERIOR FINISHES | 3053 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
3048EXT1 | EXTERIOR FINISHES | 3048 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. This project or a portion thereof was previously recommended in the FCA report dated 09/23/2010. It has been amended accordingly to reflect conditions observed during the most recent survey date of 04/05/2017. | SS DAY USE COMFORT STATION SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 720
3047INT1 | INTERIOR FINISHES | 3047 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3047INT2 | RESTROOM FIXTURE REPLACEMENT | 3047 | The fixtures in two of the restroom stalls have been pieced out for repairs to other restrooms. These two stalls are closed to the public and should be upgraded in order to bring them back into a functioning condition. This project would provide for the purchase and installation of the fixtures including the water closets, urinals, lavatories, faucets, and all dispensers. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5000
3047PLM1 | WATER HEATER REPLACEMENT | 3047 | There is a 15 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3048PLM1 | WATER HEATER REPLACEMENT | 3048 | There is a 15 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS DAY USE COMFORT STATION SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
3050EXT1 | EXTERIOR FINISHES | 3050 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for painting of the Ramada and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | RIVER CAMP RAMADA | 9959 | CNR | Parks |  | Lahontan SRA | 2008 | 144 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 288
3053SFT4 | SMOKE DETECTOR INSTALLATION | 3053 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
3052EXT1 | EXTERIOR FINISHES | 3052 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS MECHANICAL BUILDING SOUTH | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 480 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2400
3053SFT3 | STOVE OIL TANK RELOCATION | 3053 | There is an above ground stove oil storage tank located on the side of the building. According to Table 3504.2.1 of the 2006 International Fire Code, flammable gases must be stored at least 5 feet away from a building of non-rated construction. This project would provide for relocating the stove oil storage tank to comply with the code. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
3053INT1 | INTERIOR FINISHES | 3053 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
3053ENR1 | WINDOW REPLACEMENT | 3053 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
3053ENR2 | EVAPORATIVE COOLER REPLACEMENT | 3053 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3053ENR3 | FURNACE REPLACEMENT | 3053 | The building is heated by an oil fired furnace. It is original to the building, not energy efficient and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
3053SFT2 | EXTERIOR STAIR / HANDRAIL REPLACEMENT | 3053 | The exterior concrete stairs at the entry door are due for replacement. They are cracked and crumbling and have reached the end of their useful life. The new landing and stairs should comply with the current adopted building code. Section R311.4.3 of the 2006 IBC describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. This project would provide for removal of the existing stairs and installation of a compliant landing, handrails and stairs for the entrance. | LD RESIDENCE #4 | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 1400 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 3500
3047EXT1 | EXTERIOR FINISHES | 3047 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS DAY USE COMFORT STATION NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
3051EXT1 | EXTERIOR FINISHES | 3051 | It is important to maintain the finish, weather resistance and appearance of the structure. This project would provide for staining the wood on the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH SHORE MARINA KIOSK | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 192 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1920
0544EXT1 | EXTERIOR FINISHES | 0544 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD7 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1200
1322EXT1 | EXTERIOR FINISHES | 1322 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2300
0496ADA1 | RESTROOM REMODEL | 0496 | The building has six separate restroom stalls, but no shower stalls. The maintenance staff indicated the need to remodel two of the stalls to provide showers. This project would provide for a complete remodel of two of the stalls to provide shower facilities, one of which shall comply with ADA accessible guidelines. The removal and disposal of the existing fixtures and finishes is included in this estimate. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 16000
0497EXT1 | EXTERIOR/ INTERIOR FINISHES | 0497 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD2 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
0499EXT4 | EXTERIOR FINISHES | 0499 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5280
0499INT2 | INTERIOR FINISHES | 0499 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 5-6 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5280
0499ENR2 | LIGHTING UPGRADE | 0499 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact flourescent lamps) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0499ENR1 | EVAPORATIVE COOLER REPLACEMENT | 0499 | An evaporative cooler is installed on the roof of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to the existing ductwork and utilities in the gable end of the residence.. The estimate includes removal and disposal of the old roof mounted evaporative cooler and any required patching of the roof. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3500
0540EXT1 | EXTERIOR/ INTERIOR FINISHES | 0540 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD3 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2040
0496ENR1 | LIGHTING UPGRADE | 0496 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in each room for additional savings. Any electrical wiring upgrades are not included in this estimate. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0543EXT1 | EXTERIOR/ INTERIOR FINISHES | 0543 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD6 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
0496SFT1 | GFCI DUPLEX OUTLET REPLACEMENT | 0496 | There are six outlets in the restrooms throughout the building which are not GFCI. These outlets should be changed to GFCI type outlets per the NEC. This project would provide for the purchase and installation of six GFCI duplex outlets. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 300
0544INT1 | INTERIOR FINISHES | 0544 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD7 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0589EXT1 | EXTERIOR/ INTERIOR FINISHES | 0589 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD9 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
0592EXT1 | EXTERIOR FINISHES | 0592 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD10 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1200
0592INT1 | INTERIOR FINISHES | 0592 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD10 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1200
0592EXT2 | EXTERIOR DOOR REPLACEMENT | 0592 | The exterior metal doors are damaged from age and general wear and tear and have reached the end of their expected life. This project would provide for the replacement of three door assemblies with new metal doors, frames and hardware. Removal and disposal of the existing doors is included in this estimate. | LD10 CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 240 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0599EXT1 | EXTERIOR/ INTERIOR FINISHES | 0599 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD11 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2005 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1320EXT1 | EXTERIOR FINISHES | 1320 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OVERLOOK CXT COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 2006 | 204 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1020
1321EXT1 | EXTERIOR/ INTERIOR FINISHES | 1321 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLACKBIRD POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1280
1321ELE1 | SOLAR PANEL REPLACEMENT | 1321 | The power to the building is provided by a photovoltaic system. The solar panels have been broken by vandals and should be scheduled for replacement. This project provides for the purchase and installation of two roof-mounted solar panels. | BLACKBIRD POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
0542EXT1 | EXTERIOR/ INTERIOR FINISHES | 0542 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD5 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1997 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2040
0493SFT3 | EXIT SIGN AND EGRESS LIGHTING UPGRADE | 0493 | The emergency egress lighting is insufficient and the exit signs do not meet current standards. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2006 Chapter 10 was referenced for this project. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1500
9959ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9959 | The parking areas at the LD1 Comfort Station, North Boat Launch and SS Boat Launch have pole lights that are difficult to maintain and not energy efficient. This project would provide for the replacement of the existing lights with solar powered LED exterior light fixtures. The existing light heads can be replaced with the new LED lights, but additional lighting should be provided as well including 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. The estimate is based on replacement and / or installation of 20 light fixtures. | LAHONTAN STATE RECREATION AREA | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 150000
9959SIT2 | CARPORT STRUCTURE INSTALLATION | 9959 | There are approximately 10 state vehicles parked in the parking lot next to the Regional Headquarters building at any given time. The vehicles include boats and work trucks that deteriorate rapidly due to exposure to the elements. This project would provide materials and labor to construct a steel carport capable of protecting 10 vehicles to be built in the parking lot. | LAHONTAN STATE RECREATION AREA | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 75000
0493EXT1 | EXTERIOR FINISHES | 0493 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 13650
0493INT1 | INTERIOR FINISHES | 0493 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22750
0493ENR1 | WINDOW REPLACEMENT | 0493 | The windows in the front office are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
0493INT2 | FLOORING REPLACEMENT | 0493 | The carpet and sheet vinyl in the front office section of the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 4-5 years. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 7000
0493ADA2 | ADA ACCESSIBLE COUNTER | 0493 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The front office has a service counter for the public to approach which does not meet current codes. Section 7.2 of the Americans with Disabilities Act Accessible Guidelines (ADAAG) states that the counter must have a portion which is at least 36" in length with a maximum height of 36" above the finish floor. This project will provide an accessible counter space in accordance with this requirement. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1500
0493ENR2 | LIGHTING UPGRADE | 0493 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6825
0496PLM1 | WATER HEATER REPLACEMENT | 0496 | There is a 20 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
0493SFT2 | FIRE ALARM SYSTEM INSTALLATION | 0493 | This building is lacking a fire detection and alarm system. It is recommended that a fire detection and alarm system be installed. When completed, the new system will provide visual, as well as audible notification, in accordance with ADA requirements located in ICC/ANSI A117.1- 2006 Section 7 and the 2006 International Fire Code. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 13650
1322INT1 | INTERIOR FINISHES | 1322 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2300
0493ENR3 | HEATER INSTALLATION | 0493 | Two of the garage bays have broken or missing heating equipment and they are uncomfortably cold in the winter. It is recommended to install new heating equipment in these occupied areas to ensure a comfortable work environment. This project would provide for the purchase and installation of two propane fired heaters including all required connections to existing utilities. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7000
0494EXT1 | EXTERIOR FINISHES | 0494 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting the wood, cleaning and sealing the masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD WELL HOUSE(VACANT) | 9959 | CNR | Parks |  | Lahontan SRA | 1960 | 64 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 200
0494EXT2 | ROOF REPLACEMENT | 0494 | The wood shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | OLD WELL HOUSE(VACANT) | 9959 | CNR | Parks |  | Lahontan SRA | 1960 | 64 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 300
0494EXT3 | EXTERIOR DOOR REPLACEMENT | 0494 | The existing exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | OLD WELL HOUSE(VACANT) | 9959 | CNR | Parks |  | Lahontan SRA | 1960 | 64 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
0495EXT1 | EXTERIOR FINISHES | 0495 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | OLD DISTRICT HEADQUARTERS | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 860 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4300
0495EXT2 | ROOF REPLACEMENT | 0495 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | OLD DISTRICT HEADQUARTERS | 9959 | CNR | Parks |  | Lahontan SRA | 1930 | 860 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8600
0498EXT1 | EXTERIOR FINISHES | 0498 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding and sealing the wood and caulking of the flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
0496INT1 | INTERIOR FINISHES | 0496 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0496EXT1 | EXTERIOR FINISHES | 0496 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD1 DAY USE COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
0493SFT1 | FIRE SUPPRESSION SYSTEM INSTALLATION | 0493 | The building is a partial B occupancy per the 2006 IBC. Pursuant to the Nevada State Fire Marshal Regulation, NAC 477.915 (c) states, that every building owned or occupied by the state which is designated as a B occupancy, or has a floor area greater than 12,000 square feet on any floor or 24,000 square feet on all floors or is an R-1 occupancy, must have sprinklers installed when the building is remodeled or an addition is proposed. This project would provide funding for the installation of a fire sprinkler system and backflow prevention in the event the building is remodeled or an addition is undertaken. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 31850
2363EXT1 | EXTERIOR/ INTERIOR FINISHES | 2363 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS3 NORTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1987 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
0493ADA3 | ADA SIGNAGE | 0493 | Americans with Disabilities Act (ADA) regulations pertaining to building access has established building signage criteria for permanent spaces in buildings. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage in this facility does not comply with this criteria. It is recommended that applicable signage be installed where required. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | REGIONAL HEADQUARTERS/MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 4550 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1347INT1 | FLOOR REPAIRS | 1347 | The painted concrete floor in the building is damaged and should be scheduled for repairs. This project would provide for stripping the concrete, filling the cracks and applying a new coat of paint in the next 2-3 years. | SS MECHANICAL BUILDING NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 480 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 960
1350ENR1 | WINDOW REPLACEMENT | 1350 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 9 units. Removal and disposal of the existing windows is included in this estimate. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6750
1350EXT2 | EXTERIOR DOOR REPLACEMENT | 1350 | The exterior wood door at the entry appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
1350SFT2 | EXTERIOR LANDING / HANDRAIL INSTALLATION | 1350 | Section R311.4.3 of the 2006 IBC Residential Building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minimum dimension of 36 inches measured in the direction of travel. The front entry landing does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. Also included are handrails to be installed at the steps as required by Chapter 10 of the 2006 IBC. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1200
1350EXT3 | ROOF REPLACEMENT | 1350 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 9000
1351EXT1 | EXTERIOR FINISHES | 1351 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is the caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be caulked and sealed in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 1200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 3600
1351INT1 | INTERIOR FINISHES | 1351 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings in the office and restroom area be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS MAINTENANCE SHOP | 9959 | CNR | Parks |  | Lahontan SRA | 1980 | 1200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1346EXT2 | ROOF REPLACEMENT | 1346 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SS GARAGE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2362EXT1 | EXTERIOR/ INTERIOR FINISHES | 2362 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | CATFISH CUT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1345EXT2 | ROOF REPLACEMENT | 1345 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SS GARAGE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
2364EXT1 | EXTERIOR/ INTERIOR FINISHES | 2364 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS3 SOUTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1987 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2365EXT1 | EXTERIOR FINISHES | 2365 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS3 COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
2365INT1 | INTERIOR FINISHES | 2365 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS3 COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2365PLM1 | WATER HEATER REPLACEMENT | 2365 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS3 COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
2366EXT1 | EXTERIOR/ INTERIOR FINISHES | 2366 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS5 NORTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2006 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
2367EXT1 | EXTERIOR/ INTERIOR FINISHES | 2367 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS5 SOUTH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1998 | 208 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2080
2368EXT1 | EXTERIOR FINISHES | 2368 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS7 SOUTH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 4500
2368INT1 | INTERIOR FINISHES | 2368 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS7 SOUTH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
2368PLM1 | WATER HEATER REPLACEMENT | 2368 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS7 SOUTH COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
2361EXT1 | EXTERIOR/ INTERIOR FINISHES | 2361 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS12 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2007 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1330ENR1 | FURNACE REPLACEMENT | 1330 | The building is heated by a propane-fired furnace. It is original to the building, not energy efficient and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1322ENR1 | LIGHTING UPGRADE | 1322 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts or compact flourescent light bulbs are suggested. Occupancy sensors will be installed in restrooms, conference rooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1322ADA1 | ADA UPGRADES | 1322 | The existing Americans with Disabilities Act (ADA) designated route of travel to the restroom does not meet current accessibility requirements. Included in this project is installing edge protection on the ramp leading up to the restroom and adding ADA signage. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | NORTH SHORE MARINA CLIVUS RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1984 | 460 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2000
1324EXT1 | EXTERIOR/ INTERIOR FINISHES | 1324 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DRUM POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1324ADA1 | ADA PARKING SIGN | 1324 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage for the parking space does not comply with this criteria. This project would provide funding for purchase and installation of an ADA parking sign which was missing from the ADA parking space at the time of the survey. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | DRUM POINT SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1326EXT1 | EXTERIOR FINISHES | 1326 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD STORAGE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 120 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 600
1327EXT1 | EXTERIOR FINISHES | 1327 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is cleaning and sealing the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD GARAGE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1328EXT1 | EXTERIOR FINISHES | 1328 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 3-4 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1328INT1 | INTERIOR FINISHES | 1328 | The interior finishes are in fair condition. It is recommended that the painted gypsum board interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1347EXT1 | EXTERIOR FINISHES | 1347 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS MECHANICAL BUILDING NORTH | 9959 | CNR | Parks |  | Lahontan SRA | 1978 | 480 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2400
1328ENR2 | LIGHTING UPGRADE | 1328 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
2369PLM1 | WATER HEATER REPLACEMENT | 2369 | There is a 20 gallon propane-fired water heater in the closet. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 5-6 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SS7 CENTER COMFORT STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 900 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1250
1330PLM1 | WATER HEATER REPLACEMENT | 1330 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
0499SFT2 | EXTERIOR LANDING / HANDRAIL INSTALLATION | 0499 | Section R311.4.3 of the 2006 IBC Residential building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The front entry landing does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door and handrails at the steps as required by Chapter 10 of the 2006 IBC. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2500
1331SFT2 | EXTERIOR LANDING / HANDRAIL INSTALLATION | 1331 | Section R311.4.3 of the 2006 IBC Residential Building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The exterior landing at the entry door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door and installation of handrails as required by Chapter 10 of the 2006 IBC. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 2500
1343ENR2 | LIGHTING UPGRADE | 1343 | The existing lighting fixtures are the older fluorescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. F28 T-8 lamps with electronic ballasts are suggested. Occupancy sensors will be installed in the restroom and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1343ENR3 | EVAPORATIVE COOLER REPLACEMENT | 1343 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1344EXT1 | EXTERIOR FINISHES | 1344 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS GARAGE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
1345EXT1 | EXTERIOR FINISHES | 1345 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS GARAGE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
1346EXT1 | EXTERIOR FINISHES | 1346 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS GARAGE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1000
1344EXT2 | ROOF REPLACEMENT | 1344 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing. | SS GARAGE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 200 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1328ENR1 | WINDOW REPLACEMENT | 1328 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | SS ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1986 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
1330EXT2 | EXTERIOR FINISHES | 1330 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 7-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 5280
1350ENR2 | EVAPORATIVE COOLER REPLACEMENT | 1350 | An evaporative cooler is installed on the roof of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1350INT2 | KITCHEN REMODEL | 1350 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1350INT1 | FLOORING REPLACEMENT | 1350 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 4" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6300
9959SIT1 | SLURRY SEAL ASPHALT PAVING | 9959 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads and parking areas at the LD1 Day Use Comfort Station, Overlook Comfort Station, Silver Springs Boat Launch and the Silver Springs Ranger Residence. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 200,000 square feet of asphalt area was used to generate this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LAHONTAN STATE RECREATION AREA | 9959 | CNR | Parks |  | Lahontan SRA | 0 |  | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 100000
1331INT2 | FLOORING REPLACEMENT | 1331 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6230
0499INT1 | FLOORING REPLACEMENT | 0499 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #1 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4900
1330INT1 | FLOORING REPLACEMENT | 1330 | The sheet vinyl and carpet in the building are damaged and reaching the end of their useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of new 12x12 VCT with a 6" base and heavy duty commercial grade carpet in the next 2-3 years. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5600
1330SFT2 | EXTERIOR LANDING INSTALLATION | 1330 | Section R311.4.3 of the 2006 IBC Residential Building Code describes the requirements for landings at exterior doors. The landing shall not be more than 7 3/4 inches below the top of the threshold and shall have a minumum dimension of 36 inches measured in the direction of travel. The front entry door does not comply with this code and poses a safety hazard. This project would provide for the installation of a compliant landing for the door. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1331ENR3 | EVAPORATIVE COOLER REPLACEMENT | 1331 | An evaporative cooler is installed on the side of this building and is severely scaled and has reached the end of it's useful and expected life. This project would provide for a new evaporative cooler to be installed including all required connections to utilities. The estimate includes removal and disposal of the old cooler. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1331INT1 | INTERIOR FINISHES | 1331 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4450
1331ENR1 | WINDOW REPLACEMENT | 1331 | The windows are older, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 8 units. Removal and disposal of the existing windows is included in this estimate. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6000
1331ENR2 | FURNACE REPLACEMENT | 1331 | The building is heated by a propane-fired furnace. It is original to the building, not energy efficient and is reaching the end of its useful life. This project provides for disposal of the existing unit and replacement with a new propane-fired unit including connections to utilities. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1336INT2 | KITCHEN REMODEL | 1336 | The kitchen is in fair to poor condition. The cabinets and equipment are showing signs of general wear and tear and are approaching the end of their expected life. This project recommends the replacement of the existing kitchen cabinets, counters, fixtures and equipment with mid range, high quality components. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1336ENR1 | WINDOW REPLACEMENT | 1336 | The windows are original, single pane construction in a metal frame. These older windows are drafty, not energy efficient and at least one is broken. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 6 units. Removal and disposal of the existing windows is included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1336EXT2 | ROOF REPLACEMENT | 1336 | The asphalt composition shingle roof on this building was in poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new 50 year asphalt composition roofing shingle and new underlayments. This estimate includes removal and disposal of the old roofing and underlayments. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 5880
1336INT1 | INTERIOR FINISHES | 1336 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2940
1336EXT1 | EXTERIOR FINISHES | 1336 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost is sanding, priming and painting and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted in the next 7-8 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2940
1331EXT5 | ROOF REPAIRS | 1331 | The roof design is inadequate and is contributing to the premature deterioration of the building. There are leaks on the west side of the roof between the two gable ends where the cricket is not sufficient. The cricket needs to be rebuilt to create a steeper slope. This will ensure that rain and snow does not accumulate on the roof and cause leaks. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1500
1331PLM1 | WATER HEATER REPLACEMENT | 1331 | There is a 50 gallon propane-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 6-7 years. It is recommended that a new propane-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1500
1331EXT2 | EXTERIOR DOOR REPLACEMENT | 1331 | The front exterior wood door appears to be original to the building. It is damaged from age and general wear and tear. This project would provide for the replacement of the wood door with a new metal door, frame and hardware. Removal and disposal of the existing door and painting of the new door is included in this estimate. | LD RESIDENCE #3 | 9959 | CNR | Parks |  | Lahontan SRA | 1923 | 890 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 750
1330ENR2 | WINDOW REPLACEMENT | 1330 | The windows are original, dual pane construction in a metal frame. These older windows are drafty and not energy efficient. The windows leak and some were damaged during high winds in 2002. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 10 units. Removal and disposal of the existing windows is included in this estimate. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | LD RESIDENCE #2 | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 1056 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7500
1336ENR2 | LIGHTING UPGRADE | 1336 | The existing lighting fixtures are the older incandescent type, and are not energy efficient. This project will upgrade fixtures to higher efficiency units with a longer life cycle. CFL (compact flourescent lamps) are suggested. Occupancy sensors will be installed in restrooms and other low occupancy areas for additional savings. Any electrical wiring upgrades are not included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 588
1336PLM1 | WATER HEATER REPLACEMENT | 1336 | There is a 50 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1336INT3 | SHOWER AND RESTROOM REMODEL | 1336 | The restrooms and shower rooms are original to the building and in overall poor condition. The finishes, fixtures, cabinets, toilets, showers and exhaust fans are showing signs of wear and deterioration. This project would provide for a complete remodel of the restrooms and shower rooms. The removal and disposal of the existing fixtures and finishes is included in this estimate. | SEASONAL EMPLOYEES BASE CAMP | 9959 | CNR | Parks |  | Lahontan SRA | 1976 | 588 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 25000
1337EXT1 | EXTERIOR/ INTERIOR FINISHES | 1337 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | VIRGINIA BEACH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2000 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1350SFT1 | SMOKE DETECTOR INSTALLATION | 1350 | The 2006 IBC and 2006 IFC, section 907.2.10.1.2 requires smoke detectors in dwelling units be installed in each sleeping room and on the ceiling or wall outside of each separate sleeping area in the immediate vicinity of bedrooms. State Fire Marshal NAC 477.915 (3) requires that smoke detectors be connected to the building wiring with a battery backup. This project would provide funding for the purchase and installation of smoke detectors. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1338EXT1 | EXTERIOR FINISHES | 1338 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, staining the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS2 COMFORT STATION - BOAT LAUNCH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 400 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2000
1342ELE1 | SOLAR PANEL REPLACEMENT | 1342 | The power to the building is provided by a photovoltaic system. The solar panels have been broken by vandals and should be scheduled for replacement. This project provides for the purchase and installation of two roof-mounted solar panels. | SS10 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 204 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1338INT1 | INTERIOR FINISHES | 1338 | The interior finishes are in fair condition. It is recommended that the Fiberglass Reinforced Panels are power washed and re-caulked and the ceramic tiles are repaired and sealed as needed. This project should be done at least once in the next 2-3 years and scheduled on a cyclical basis to maintain the integrity of the structure. | SS2 COMFORT STATION - BOAT LAUNCH | 9959 | CNR | Parks |  | Lahontan SRA | 1974 | 400 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1337ADA1 | ADA SIGNAGE | 1337 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The criteria includes: sign mounting heights and locations; character heights and proportions; raised and Braille characters/pictograms; and sign contrast and finish. The signage for the parking space does not comply with this criteria. This project would provide funding for purchase and installation of an ADA parking sign which was missing from the ADA parking space at the time of the survey. NRS 338.180, IBC - 2006, ICC/ANSI A117.1 - 2003 and the most current version of the Americans with Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | VIRGINIA BEACH SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2000 | 128 | 2019-06-19 | Immediate to Two Years | Currently Critical | 1 | 1000
1350INT3 | INTERIOR FINISHES | 1350 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. This project or a portion thereof was previously recommended in the FCA report dated 06/02/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 07/15/2010. | SS RANGER RESIDENCE | 9959 | CNR | Parks |  | Lahontan SRA | 1981 | 900 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4500
1340EXT1 | EXTERIOR/ INTERIOR FINISHES | 1340 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS6 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1998 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
1343INT1 | INTERIOR FINISHES | 1343 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1342EXT1 | EXTERIOR/ INTERIOR FINISHES | 1342 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS10 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 2040
1343EXT1 | EXTERIOR FINISHES | 1343 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building excluding the roof. Included in the cost are cleaning and sealing the brick masonry, sanding, priming and painting the wood and caulking of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1500
1339EXT1 | EXTERIOR/ INTERIOR FINISHES | 1339 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS4 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 1998 | 204 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1020
1343ENR1 | WINDOW REPLACEMENT | 1343 | The windows are original, single pane construction in a metal frame. These older windows are drafty and not energy efficient. This project recommends replacing the windows with dual pane, higher efficiency units. This estimate is for the replacement of 5 units. Removal and disposal of the existing windows is included in this estimate. | LD ENTRANCE STATION | 9959 | CNR | Parks |  | Lahontan SRA | 1979 | 300 | 2019-06-19 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3750
1341EXT1 | EXTERIOR/ INTERIOR FINISHES | 1341 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the interior and exterior of the building. Included in the cost are cleaning and sealing the precast concrete and caulking of the windows, flashing, fixtures and all other penetrations. An epoxy paint is recommended on the interior precast concrete. It is recommended that the building be sealed and caulked in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | SS8 SST RESTROOM | 9959 | CNR | Parks |  | Lahontan SRA | 2003 | 128 | 2019-06-19 | Four to Ten Years | Long-Term Needs | 3 | 1280
9961SEC1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9961 | There is no site lighting in the park which is a security and safety concern. This project would provide for the installation of 5 solar powered LED exterior light fixtures, 20 foot tall poles and 30" diameter raised concrete bases. This installation will eliminate the need for trenching and electrical connections. This project or a portion thereof was previously recommended in the FCA report dated 05/14/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 06/06/2012. | DAYTON STATE PARK | 9961 | CNR | Parks |  | Dayton | 0 |  | 2012-06-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 32500
9961ADA5 | ACCESSIBLE ENTRANCE RAMP | 9961 | The Comfort Station is lacking an accessible path of travel to the entrance of the building. It appears that the slope exceeds 5% and a new configuration is recommended including handrails. This building is required to have an accessible entrance per the Americans with Disabilities Act (ADA) regulations. This project would provide for an ADA accessible route / ramp from the accessible parking space to access the building including handrails and signage. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DAYTON STATE PARK | 9961 | CNR | Parks |  | Dayton | 0 |  | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 35000
9961ADA6 | DUAL LEVEL DRINKING FOUNTAIN INSTALLATION | 9961 | This park has an outdoor water fountain near the Ramada parking area that is not ADA compliant. The 2012 IBC Section 1109.5 states where drinking fountains are provided on an exterior site, on a floor or within a secured area, no fewer than two drinking fountains shall be provided. One shall comply with the requirements for people who use a wheelchair and one shall comply with the requirements for standing persons. This project would provide funding for the purchase and installation of two drinking fountains to meet the ADA requirements. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DAYTON STATE PARK | 9961 | CNR | Parks |  | Dayton | 0 |  | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 4000
1228ADA1 | ADA UPGRADES | 1228 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. The Ramada requires several upgrades to comply with ADA requirements. There are elevation changes in the concrete flooring that exceed accessible limits, the grill and sink are not accessible and there are no accessible picnic tables. This project would provide for grinding the concrete, replacing the grill and sink, providing at least two accessible picnic tables and any other necessary upgrades to comply with ADA regulations. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DAY USE AREA RAMADA | 9961 | CNR | Parks |  | Dayton | 1979 | 2508 | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 10000
9961ADA7 | ADA PARKING IMPROVEMENTS | 9961 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. A concrete parking area, passenger loading area and path of travel to the Office are necessary to comply with ADA accessibility requirements. This project would provide for a concrete van accessible ADA parking and loading space and concrete walkway to the Office entrance. This will require regrading, placement of P.C. concrete, signage, striping and any other necessary upgrades. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. It is recommended that this project coincide with the paving project. | DAYTON STATE PARK | 9961 | CNR | Parks |  | Dayton | 0 |  | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 2500
1030SFT2 | EXIT SIGN & EGRESS LIGHTING | 1030 | The shop has no exit lighting and emergency egress lighting. This project would provide for the purchase and installation of self-illuminated or LED style exit signs with battery-backed internal systems as well as emergency egress lighting to provide illumination along the egress route. IBC - 2012 Chapter 10 was referenced for this project. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 1500
1228EXT1 | EXTERIOR FINISHES | 1228 | It is important to maintain the finish, weather resistance, and appearance of the structure. This project would provide for staining or painting of the structure and it is recommended that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DAY USE AREA RAMADA | 9961 | CNR | Parks |  | Dayton | 1979 | 2508 | 2012-06-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2200
9961ADA4 | CAMPGROUND ADA UPGRADES | 9961 | According to proposed US Access Board regulations, a campground with 1-25 camping spaces should have at least 1 accessible space. The campground currently does not have an accessible space out of 10 spaces. Other regulations include a 20'-0" wide drive aisle for RV/ tent trailer sites and accessible amenities on an accessible route including the grill, picnic table, fire ring and water & electric utilities. This project provides for upgrading one existing campsites to an accessible campsite. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | DAYTON STATE PARK | 9961 | CNR | Parks |  | Dayton | 0 |  | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 17500
1030INT1 | INTERIOR FINISHES / FRP INSTALLATION | 1030 | The interior of the shop is stained plywood on the roof and ceiling. This project would provide for the cyclical staining or painting of the interior plywood walls and ceiling. This project also includes installing an FRP wall surround in the restroom. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2012-06-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1030ENR1 | LIGHTING UPGRADE | 1030 | The existing building lighting fixtures, T-12's are older incandescent type and are not energy efficient. This project will upgrade lighting fixtures to T-5's, with electronic ballasts, resulting in increased efficiency and reduced costs associated with illumination. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 1200
1030EXT1 | EXTERIOR FINISHES | 1030 | It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope, other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that this project be implemented in the next 2 to 3 years and is recommended on a cyclical basis based on environmental conditions. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2012-06-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2400
1062INT1 | INTERIOR FINISHES | 1062 | The interior of the shop is painted plywood on the roof and ceiling. This project would provide for the cyclical painting of the interior plywood walls and ceiling. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2012-06-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1062SFT1 | FIRE ALARM INSTALLATION | 1062 | This building is not equipped with an automatic fire detection and alarm system. It is recommended that a new system be installed to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 2500
1062ADA1 | ADA IMPROVEMENTS | 1062 | The Office is not ADA accessible. This project would provide for ADA accessibility upgrades including but not limited to a concrete parking and loading space, route of travel to the office, a new concrete walkway / landing at the front entrance and a new threshold for the existing door. Signage is also included in this estimate. he 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. 500 square feet of new PC concrete was used for this estimate. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 5000
1062EXT1 | EXTERIOR FINISHES | 1062 | It is important to maintain the finish, weather resistance, and appearance of the building. This project recommends work to protect the exterior building envelope other than the roof, including painting, staining, or other applied finishes, and caulking around windows, flashing, fixtures, and other penetrations to maintain the building in good, weather tight condition. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | DAYTON STATE PARK OFFICE | 9961 | CNR | Parks |  | Dayton | 1979 | 200 | 2012-06-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1227ADA1 | ADA IMPROVEMENTS | 1227 | The existing restroom are not 100 % ADA compliant. This project would provide for the required modifications to the restrooms including restroom fixture relocation to provide for clearances and mounting heights of fixtures and equipment and signage. The exterior concrete landing at the door appears to exceed a 2% slope also. This project also includes the removal and replacement of the exterior concrete to provide for a code compliant landing. This proposal is for one restroom which would become a unisex ADA restroom. This project should coincide with the ADA accessible ramp / route of travel project. The 2012 IBC, ICC/ANSI A117.1 - 2009, NRS 338.180 and the most current version of the ADA Standards For Accessible Design were used as a reference for this project. | COMFORT STATION | 9961 | CNR | Parks |  | Dayton | 1979 | 360 | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 15000
1227EXT1 | EXTERIOR & INTERIOR FINISHES | 1227 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding for the painting the wood portions of the building and repairing any cracks and sealing the stone masonry as well as caulking the window frames, doors and other penetrations excluding the roof. This project includes the exterior and interior finishes. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | COMFORT STATION | 9961 | CNR | Parks |  | Dayton | 1979 | 360 | 2012-06-06 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3600
9961SIT3 | ASPHALT PAVING INSTALLATION | 9961 | The yard around the Shop and Office, the campground loop road and the individual campsite parking areas are not currently paved. This project would provide asphalt cement paving for the yard, a 10' wide access road around the campground loop and 10' wide parking spaces at each campsite. The estimate includes grading, compaction and installation of 4" thick asphalt cement. | DAYTON STATE PARK | 9961 | CNR | Parks |  | Dayton | 0 |  | 2012-06-06 | Four to Ten Years | Long-Term Needs | 3 | 137500
1030SFT1 | FIRE ALARM INSTALLATION | 1030 | This building is not equipped with an automatic fire detection and alarm system. It is recommended that a new system be installed to ensure the safety of the occupants. Also, according to NAC 477.917 "If the value of individual or cumulative additions, alterations and repairs to a building or structure in any 12-month period exceeds 50 percent of the value of the building or structure at the commencement of the 12-month period, the building or structure must conform to the requirements for a new building or structure". When completed, the new system will provide visual, as well as audible notification, in accordance with the 2012 IBC Chapter 9, Section 907 and the State Fire Marshal's requirements. | DAYTON STATE PARK SHOP | 9961 | CNR | Parks |  | Dayton | 1999 | 480 | 2012-06-06 | Immediate to Two Years | Currently Critical | 1 | 3360
1704INT1 | INTERIOR FINISHES | 1704 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
1703INT1 | INTERIOR FINISHES | 1703 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 7575
1702INT1 | INTERIOR FINISHES | 1702 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6375
1701INT1 | INTERIOR FINISHES | 1701 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 18500
1699INT1 | INTERIOR FINISHES | 1699 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
1700INT1 | INTERIOR FINISHES | 1700 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 37000
1706INT1 | INTERIOR FINISHES | 1706 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
9962SEC2 | VIDEO SECURITY SYSTEM UPGRADE | 9962 | The site video security system is outdated and should be scheduled for replacement. The cameras have been removed or do not function on several of the buildings and there are blind spots in the coverage that should be addressed. This project addresses replacement of the cameras and controls at the site with all digital equipment as well as sufficient storage capacity. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | LOVELOCK CORRECTIONAL CENTER | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500000
1707INT1 | INTERIOR FINISHES | 1707 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
1704EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1704 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1707ENR2 | EXTERIOR WALL INSULATION | 1707 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
1705SFT1 | EXIT SIGN INSTALLATION | 1705 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1704SFT2 | EXIT SIGN INSTALLATION | 1704 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1707INT2 | VCT FLOORING REPLACEMENT | 1707 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1706INT2 | VCT FLOORING REPLACEMENT | 1706 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1705INT2 | VCT FLOORING REPLACEMENT | 1705 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1706ENR2 | EXTERIOR WALL INSULATION | 1706 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
1705ENR2 | EXTERIOR WALL INSULATION | 1705 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8750
1704INT2 | VCT FLOORING REPLACEMENT | 1704 | The VCT (vinyl composite tile) flooring on the Intermediate Platform and the Observation Platform is damaged and reaching the end of its useful life. It is recommended that the VCT flooring be replaced. This project would provide for removal and disposal of the VCT and installation of new 12x12 VCT with a 6" base. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4050
1704ENR2 | EXTERIOR WALL INSULATION | 1704 | This building has no insulation in the exterior walls of the stairwell area. The temperature extremes make it impossible to properly condition the guard station above creating an uncomfortable work environment. This project will install batt insulation in the walls to help moderate temperature fluctuations. It may be possible to use a foamed-in system to fill the cavities where applicable; costs are similar to the batt insulation provided for in this project. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4200
1707EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1707 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1706SFT1 | EXIT SIGN INSTALLATION | 1706 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1705EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1705 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1706PLM1 | WATER HEATER REPLACEMENT | 1706 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1704SFT1 | EXTERIOR STAIR HANDRAIL INSTALLATION | 1704 | The concrete exterior stairs near the entry gate are lacking a handrail as required in the 2006 IBC Chapter 10, Section 1012. This project would provide for a tubular steel framed handrail to be installed at the two steps along the walkway. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 1500
1703ADA1 | ADA RESTROOM UPGRADES | 1703 | The Americans with Disabilities Act (ADA) provides for accessibility to sites and services for people with physical limitations. There are several minor adjustments that must be made to the restrooms in order to comply with the ADA. These include new signs, mounting the signs on the wall adjacent to the doors instead of on the doors and altering the locations and orientations of some of the restroom fixtures. The 2006 IBC, ICC/ANSI A117.1 - 2003 and the most current version of the Americans With Disabilities Act Accessible Guidelines (ADAAG) were used as a reference for this project. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 2500
1706EXT3 | SLIDING GLASS DOOR REPLACEMENT | 1706 | The sliding glass door has reached the end of its expected life. It is damaged from age and general wear and tear and is missing the screen door. This project would provide for the replacement of the sliding glass door assembly with a new door, frame and hardware. Removal and disposal of the existing door is included in this estimate. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1705SEC2 | SPOTLIGHT REPAIRS | 1705 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1702PLM1 | WATER HEATER REPLACEMENT | 1702 | There is a 30 gallon natural gas-fired water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1902PLM1 | WATER SOFTENER SYSTEM INSTALLATION | 1902 | There is no water softening/ treatment systems in the building to serve the mechanical equipment. Water that has not been treated causes wear and tear on the domestic water supply lines, plumbing fixtures and HVAC equipment. This project would provide for the purchase and installation of water softener system including all required connections to plumbing and electrical systems. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 15000
1700INT2 | RESTROOM FLOOR REPLACEMENT | 1700 | The epoxy floor covering in the restroom is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1000
1705INT1 | INTERIOR FINISHES | 1705 | The interior finishes are in fair condition. It is recommended that the interior walls and ceilings of the observation platform be painted at least once in the next 2-4 years. Prior to painting, all surfaces should be repaired and prepped. An epoxy-based paint should be utilized in wet areas for durability. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2010
1902INT2 | SHOWER FLOOR REPLACEMENT | 1902 | The epoxy floor covering in the two shower areas is damaged and reaching the end of its useful life. It is recommended that the flooring be replaced. This project would provide for removal and disposal of the existing flooring and installation of a new poured epoxy flooring in the next 2-3 years. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1902PLM2 | WATER HEATER REPLACEMENT | 1902 | There are two 100 gallon natural gas-fired water heaters in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, these units are showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that two new natural gas-fired water heaters be installed. Removal and disposal of the existing equipment is included in this estimate. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 8000
1704PLM1 | WATER HEATER REPLACEMENT | 1704 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1706SEC2 | SPOTLIGHT REPAIRS | 1706 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1707SFT1 | EXIT SIGN INSTALLATION | 1707 | The building does not have any exit signs. This project would provide for the purchase and installation of a self-illuminated or LED style exit sign with battery-backed internal system at the entry/ exit door. IBC - 2006 Chapter 10 was referenced for this project. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 500
1704SEC2 | SPOTLIGHT REPAIRS | 1704 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
1707PLM1 | WATER HEATER REPLACEMENT | 1707 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1705PLM1 | WATER HEATER REPLACEMENT | 1705 | There is an 8 gallon electric water heater in the building. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new electric water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 500
1707ENR3 | HVAC EQUIPMENT UPGRADE | 1707 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1706ENR3 | HVAC EQUIPMENT UPGRADE | 1706 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1705ENR3 | HVAC EQUIPMENT UPGRADE | 1705 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1704ENR3 | HVAC EQUIPMENT UPGRADE | 1704 | The wall mounted air conditioner/ heater is not energy efficient and has reached the end of its expected and useful life. There is also a window mounted evaporative cooler that is no longer operational. This project would provide for the purchase and installation of a new wall mounted air conditioner/ heater. The cost includes removal and disposal of the existing HVAC units and all required connections to utilities. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 3000
1707SEC2 | SPOTLIGHT REPAIRS | 1707 | The electrical cords on the spotlights are frayed and will eventually cause the lights to malfunction. It is important to replace the cords to prevent a short as well as to protect the staff from electrical shock. This project would provide for replacing the cords in the next 2-3 years. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1500
9962PLM3 | BACKFLOW PREVENTION | 9962 | State Health Law (NAC 445A.67185) and the Plumbing Code (UPC Section 603) require backflow prevention on water service connections to ensure that there are no unprotected connections between the supplies of water, systems for the pumping, storage and treatment of water, and distribution system of the public water system and any source of pollution or contamination pursuant to which any unsafe water or other degrading material can be discharged or drawn into the public water system as a result of back siphonage or backpressure. This project allows for the installation of double check valves or reduced pressure principle backflow preventers on the main connection to city water. Costs include an above ground vault and allowance for 200 feet of 1" conduit to provide power for freeze protection. | LOVELOCK CORRECTIONAL CENTER | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
1701INT2 | JANITORS CLOSET REPAIRS | 1701 | The mop sink in the Janitors Closet is mounted adjacent to gypsum board and is showing signs of water damage. This project would provide fiberglass reinforced panels (FRP) to be installed on the walls adjacent to the mop sink. The FRP shall extend two feet beyond the edge of the sink and a minimum of 54" above the floor finish. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 1400
1902INT1 | INTERIOR FINISHES | 1902 | The interior finishes are in fair condition. This project would provide funding to maintain the interior of the building. Included in the cost is painting the walls and ceilings, sealing the exposed masonry, repairing cracks in the masonry and replacing grout and caulk as needed. An epoxy-based paint should be utilized in wet areas for durability. It is recommended that the interior of the building be painted, sealed and repaired in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 115000
9962SIT3 | SLURRY SEAL ASPHALT PAVING | 9962 | It is important to maintain the asphalt concrete paving on the site. This project would provide for minor crack filling and slurry sealing of the paving site wide including access roads, parking areas, the maintenance yard, and the basketball court at Building #8. Striping is included in this estimate. This project should be scheduled on a 5 year cyclical basis to maintain the integrity of the paving and prevent premature failure. 350,000 square feet of asphalt area was used to generate this estimate. | LOVELOCK CORRECTIONAL CENTER | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 262500
9962ENR1 | EXTERIOR SOLAR SITE LIGHTING INSTALLATION | 9962 | The pole lights for the parking lot and entry access road were installed in 1993 and are due for an upgrade. The existing lamps are not energy efficient and require excessive labor time to replace. This project would provide for replacing the lamp heads with solar powered LED exterior light fixtures. This installation will eliminate electricity costs and the longer lifetime of the LED lamps will lower labor time for replacements. The estimate is based on the removal and replacement of 13 light fixtures. | LOVELOCK CORRECTIONAL CENTER | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 84500
9962ELE1 | HIGH MAST LAMP REPLACEMENT | 9962 | There are 13 high mast security light poles throughout the facility that have 10 security lamps each. A lot of these lamps were burned out at the time of the survey and should be scheduled for replacement. This project provides for the purchase and installation of 130 security lamps for the high mast light poles. The cost includes removal and disposal of the existing lamps. | LOVELOCK CORRECTIONAL CENTER | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 65000
1699PLM1 | WATER HEATER REPLACEMENT | 1699 | There is a 50 gallon natural gas-fired water heater in the basement. The average life span of a water heater is eight to ten years. With the passage of time and constant use, this unit is showing signs of wear and should be scheduled for replacement in the next 2-3 years. It is recommended that a new natural gas-fired water heater be installed. Removal and disposal of the existing equipment is included in this estimate. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2000
1700HVA2 | CHEMICAL FREE WATER FILTER | 1700 | The cooling tower was installed without a proper filtering system. The original design called for a Dolphin system, but funding was insufficient. The maintenance staff suggested that a Dolphin or similar chemical free system would be ideal. This project would provide for removal and disposal of the existing sock filter and installation of a chemical free filtering system. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 50000
1699ENV1 | DUST COLLECTION SYSTEM INSTALLATIONS | 1699 | The building has a carpentry shop and a welding shop which do not have complete dust collection systems. There is a fan and motor in the carpentry shop, but no ducting to the tables or equipment. In order to reduce the possibility of damage or injury, each piece of equipment should have complete collection capability. It is assumed that the existing equipment in the carpentry shop does not work or will need to be replaced in the near future. This project recommends installing a complete new dust collection system in each shop. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 40000
1700ENV1 | PROVIDE HAZARDOUS MATERIALS CONTAINMENT | 1700 | There are many different paints, stains, oils and other hazardous or flammable products on open shelves throughout the building. This does not meet OSHA standards for hazardous materials containment. This project would provide 5 hazardous materials storage cabinets in the building and install placards on the building exterior in accordance with OSHA 1910.106 (d). | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Immediate to Two Years | Currently Critical | 1 | 25000
1701EXT1 | ROOF REPLACEMENT | 1701 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 08-TRUSTEE DORMITORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 3700 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 55500
9962ENR2 | AIR HANDLER REPLACEMENT | 9962 | The HVAC roof top units throughout the site were installed in 1993 and 1997. They are not energy efficient and are reaching the end of their expected life. This project would provide for installation of new HVAC packaged units and cleaning of the existing duct work and grilles. This project includes removal and disposal of the existing HVAC units and all required connections to utilities. There are approximately 56 units at the site. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | LOVELOCK CORRECTIONAL CENTER | 9962 | Correct | LCC |  | Lovelock | 0 |  | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 6800000
1707EXT1 | ROOF REPLACEMENT | 1707 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1706EXT1 | ROOF REPLACEMENT | 1706 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 3 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1705EXT1 | ROOF REPLACEMENT | 1705 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1704EXT1 | ROOF REPLACEMENT | 1704 | The standing seam metal roof on this building was in fair to poor condition at the time of the survey. It is recommended that this building be re-roofed in the next 2-3 years with a new single-ply roofing system which will be installed directly over the existing metal roof. This will allow the roof to qualify for the statewide roofing program warranty and preventative maintenance agreement. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 1 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800
1902EXT1 | ROOF REPLACEMENT | 1902 | The roof on this building was in fair to poor condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1997. It is recommended that this building be re-roofed in the next 2-4 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | HOUSING UNIT 6 | 9962 | Correct | LCC |  | Lovelock | 1997 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 172500
1702EXT1 | ROOF REPLACEMENT | 1702 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 09-ARMORY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1275 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 19125
1699EXT1 | ROOF REPLACEMENT | 1699 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 06-WAREHOUSE/MAINTENANCE | 9962 | Correct | LCC |  | Lovelock | 1993 | 23000 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 345000
1703EXT1 | ROOF REPLACEMENT | 1703 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 10-ENTRY | 9962 | Correct | LCC |  | Lovelock | 1993 | 1515 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 22725
1700EXT1 | ROOF REPLACEMENT | 1700 | The roof on this building was in fair condition at the time of the survey. The statewide roofing program has set the useful life of an average roof at 20 years. The roof warranty expires at the end of the same time frame. The temperature fluctuations throughout the year, consistent wind which blows sand and dirt on to the roof membrane, and constant exposure to the sun are contributing factors to wear and deterioration. The current roofing system was installed in 1993. It is recommended that this building be re-roofed in the next 2-3 years to be consistent with the roofing program and the end of the warranty period. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 103500
1700HVA1 | BOILER REPLACEMENT | 1700 | There are three hot water boilers in the plant that service a majority of the HVAC needs throughout the facility. The system is designed to utilize two boilers at full capacity with the third being a reserve or back-up unit. This project recommends replacing the reserve boiler, or Boiler #3. It has had continuous problems with the fire tubes and tube sheets due to stress cracks and is due for replacement. The estimate includes removal and disposal of the existing equipment and connections to all utilities. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | BLDG. 07-CENTRAL PLANT | 9962 | Correct | LCC |  | Lovelock | 1993 | 7400 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 250000
3042EXT1 | EXTERIOR FINISHES | 3042 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is sanding, priming, painting, and caulking of the flashing, fixtures, and all other penetrations. It is recommended that the building be painted in the next 5-7 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | STORAGE BUILDING | 9962 | Correct | LCC |  | Lovelock | 2007 | 676 | 2010-03-09 | Four to Ten Years | Long-Term Needs | 3 | 3380
3040EXT1 | EXTERIOR FINISHES | 3040 | It is important to maintain the finish, weather resistance, and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is the caulking and sealing of the flashing, fixtures, and all other penetrations. It is recommended that the building be caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | FIRE PUMP HOUSE | 9962 | Correct | LCC |  | Lovelock | 1993 | 192 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 576
1707SEC1 | ACTIVATE ELECTRONIC LOCK SYSTEM | 1707 | The tower controls included an electronic control for the door lock at grade. The system was never made operational and requires tower staff to physically transfer a key from the tower to personnel below. This system is time consuming and rough on the keys and locks. This project recommends running conduit and power to activate the system, permitting tower personnel to remotely actuate the door locks. This project or a portion thereof was previously recommended in the FCA report dated 7/10/2003. It has been amended accordingly to reflect conditions observed during the most recent survey date of 3/9/2010. | TOWER 4 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 2500
1705EXT2 | EXTERIOR FINISHES | 1705 | It is important to maintain the finish, weather resistance and appearance of the building. This project would provide funding to protect the exterior of the building. Included in the cost is painting of the handrails and guardrails and caulking and sealing of the windows, flashing, fixtures and all other penetrations. It is recommended that the building be painted, caulked and sealed in the next 2-3 years and that this project be scheduled on a cyclical basis to maintain the integrity of the structure. | TOWER 2 | 9962 | Correct | LCC |  | Lovelock | 1993 | 402 | 2010-03-09 | Two to Four Years | Necessary - Not Yet Critical | 2 | 4800